## Prototype Model
Prototype Name | I | II | III | IV | IV |  |  | VIII
Prototype Description | Small Office Building | Medium Office Building | Large Office Building | Stand-alone Retail | Stand-alone Retail DuctLoss Baseline | Strip Mall-PSZ System | Strip Mall-PTAC System | Strip Mall- Fan Coil System
Vintage | New Construction | New Construction | New Construction | New Construction | Same as Stand-alone Retail | New Construction | New Construction | New Construction
Location | CZ-6/15/16 | CZ-6/15/16 | CZ-1/7/6/15/16 | CZ-1/6/7/15/16 |  | CZ-6/15/16 | CZ-6/15/16 | CZ-6/15/16
Fuel Type | gas, electricity | gas, electricity | gas, electricity | gas, electricity |  | gas, electricity | Same as Strip Mall- PSZ System | Same as Strip Mall- PSZ System
Total Floor Area (sq feet) | 5500 (90.8 ft x 60.5ft) | 53600 (163.8 ft x 109.2 ft) | 498,600 (240 ft x 160 ft) | 24695 (178 ft x 139 ft) |  | 22,500 ft² (300 ft x 75 ft)
Building shape
Aspect Ratio | 1.5 | 1.5 | 1.5 | 1.28 |  | 4
Number of Floors | 1 | 3 | 12 (plus basement) | 1 |  | 1
Window Fraction (Window-to-Wall Ratio) | 24.4% for South and 19.8% for the other three orientations (Window Dimensions: 6.0 ft x 5.0 ft punch windows for all façades) | 33% (Window Dimensions: 163.8 ft x 4.29 ft on the long side of facade 109.2 ft x 4.29 ft on the short side of the façade) | 40% of above-grade gross walls 37.5% of gross walls (including the below-grade walls) | 7.1% (Window Dimensions: 82.136 ft x 5 ft, 9.843 ft x 8.563 ft and 82.136 ft x 5 on the street facing facade) |  | 10.5% (Window Dimensions: 24 windows, 7 ft x 5 ft each and 12 doors, 6 ft x 7 ft each, on the street facing façade with south WWR 26%)
Window Locations | evenly distributed along four façades | evenly distributed along four façades | evenly distributed along four façades | Windows only on the street facing façade (25.4% WWR) |  | Windows only on the street facing façade
Shading Geometry | none | none | none | none |  | none
Azimuth | non-directional | non-directional | non-directional | non-directional |  | non-directional
Thermal Zoning | Perimeter zone depth: 16.4 ft. Four perimeter zones, one core zone and an attic zone. Percentages of floor area: Perimeter 70%, Core 30% | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 40%, Core 60% | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 33%, Core 67% | Five thermal zones Refer StandAloneRetailArea for details |  | 10 thermal zones (from left to right): LGStore1 (Type 1), SMStore1 (Type 1), SMStore2 (Type 2), SMStore3 (Type 3), SMStore4 (Type 2), LGStore2 (Type 3), SMStore5 (Type 3), SMStore6 (Type 3), SMStore7 (Type 3), and SMStore8 (Type 3). Refer StripMallArea for details
Floor to floor height (feet) | 10 | 13 | 13 | 20 |  | 17
Floor to ceiling height (feet) | 10 | 9 (4 ft above-ceiling plenum) | 9 | 20 (Core retail, Front Entry) 15 (Point of Sale, Front Retail, Back Space) |  | 17
Glazing sill height (feet) | 3 (top of the window is 8 ft high with 5 ft high glass) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass) | 3 ft | 3.74 ft (top of the window is 8.73 ft high with 5 ft high glass) |  | 3.0 ft (top of the window is 8 ft high)
Exterior walls
Construction | Wood-Frame Walls | Metal Framed wall (Non Res) | Metal Framed wall (Non Res) | Metal Framed wall (Non Res) |  | Metal Framed wall (Non Res)
Construction Assembly Layers | Refer T24NRWallWood | Refer T24NRWallMetalFrame | Refer T24NRWallMetalFrame | Refer T24NRWallMetalFrame |  | Refer T24NRWallMetalFrame
Refer T24BasementWall
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Refer T24NRWallWood for respective CZ U value | Refer T24NRWallMetalFrame for respective CZ U value | Refer T24NRWallMetalFrame for respective CZ U value | Refer T24NRWallMetalFrame for respective CZ U value |  | Refer T24NRWallMetalFrame for respective CZ U value
Dimensions | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio
Tilts and orientations | Vertical | Vertical | Vertical | Vertical | Vertical
Roof
Construction | Attic Roof with wood joist | Metal Roof | Metal Roof | Metal Roof | Metal Roof. Note: For duct loss baseline, the insulation layer is modelled at the drop ceiling. See details below | Metal Roof
Construction Assembly Layers | Refer T24NRAtticRfWood | Refer T24NRRoofMetal | Refer T24NRRoofMetal | Refer T24NRRoofMetal | Refer T24NRRoofInsAboveDeck | Refer T24NRRoofMetal
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Refer T24NRAtticRfWood for respective CZ U value | Refer T24NRRoofMetal for respective CZ U value | Refer T24NRRoofMetal for respective CZ U value | Refer T24NRRoofMetal for respective CZ U value | Refer T24NRRoofInsAboveDeck | Refer T24NRRoofMetal for respective CZ U value
Dimensions | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio
Tilts and orientations | Hipped roof: 10.76 ft attic ridge height, 2 ft overhang-soffit | Horizontal | Horizontal | Horizontal | Horizontal | Horizontal
Window |  |  |  |  | Same as Stand-alone Retail
Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio | based on window fraction, location, glazing sill height, floor area and aspect ratio | based on window fraction, location, glazing sill height, floor area and aspect ratio | based on window fraction, location, glazing sill height, floor area and aspect ratio |  | based on window fraction, location, glazing sill height, floor area and aspect ratio
Glass-Type and frame | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. |  | Fixed vertical window with U-value and SHGC as specified.
U-factor (Btu / h * ft2 * °F) | 0.36 | 0.36 | 0.36 | 0.36 |  | 0.36
SHGC | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.25
Visible transmittance | 0.42 | 0.42 | 0.42 | 0.42 |  | 0.42
Operable area | 0 | 0 | 0 | 0 |  | 0
Skylight | NA | NA | NA |  |  | NA
Dimensions |  |  |  | Skylight to Roof Ratio- 1.3 % Core Retail, Refer Skylight Layout for details
Glass-Type and frame |  |  |  | Glass, curb mounted skylight with U-value and SHGC as specified.
U-factor (Btu / h * ft2 * °F) |  |  |  | 0.58
SHGC |  |  |  | 0.25
Visible transmittance |  |  |  | 0.49
Foundation
Foundation Type | Slab on grade floor (unheated) | Slab on grade floor (unheated) F-factor method used for modeling botom floor perimeter zone floors | Slab on grade floor (unheated) | Slab on grade floor (unheated) |  | Slab on grade floor (unheated)
Construction | 8'' NW concrete floor | 8'' NW concrete floor with carpet for Core zone in bottom floor | 8'' NW concrete floor | 8'' NW concrete floor with carpet |  | 8'' NW concrete floor
Construction Assembly Layers | T24Floor_with_carpet |  | T24BFloor_with_carpet | T24Floor_with_carpet |  | T24Floor_with_carpet
Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Refer T24Floor_with_carpet for respective CZ U value | F factor= 0.73 | Refer T24BFloor_with_carpet for detailed description | T24Floor_with_carpet |  | T24Floor_with_carpet
Thermal properties for basement walls | NA | NA | Refer T24Basement_wall for detailed description | NA |  | NA
Dimensions | Based on floor area and aspect ratio. | Based on floor area and aspect ratio. | Based on floor area and aspect ratio. | Based on floor area and aspect ratio. |  | Based on floor area and aspect ratio.
Interior Surfaces
Construction | 2x4 uninsulated Stud Wall | 2x4 uninsulated Stud Wall for Interior Walls, 100mm NW Concrete floor with carpet for interior floor slabs & Acoustic celing tile for Drop ceiling | 2x4 uninsulated Stud Wall for Interior Walls, 100mm NW Concrete floor with carpet for interior floor slabs & Acoustic celing tile for Drop ceiling | 2x4 uninsulated Stud Wall for Interior Walls & Acoustic celing tile for Drop ceiling | 2x4 uninsulated Stud Wall for Interior Walls & Acoustic celing tile for Drop ceiling. Note: For duct loss baseline the drop ceiling is modelled with a layer of insulation. See details below | 2x4 uninsulated Stud Wall for Interior Walls
Construction Assembly Layers | Int_wall | Int_wall Int_slab_floor Drop Ceiling | Int_wall Int_slab_floor Drop Ceiling | Int_wall Drop Ceiling | Int_wall Drop Ceiling2 | Int_wall
Dimensions | Based on floor area and floor to floor height | Based on floor area and floor to floor height | Based on floor area and floor to floor height | Based on floor area and floor to floor height | Based on floor area and floor to floor height | Based on floor area and floor to floor height
Internal Mass | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Peak: 0.2318 cfm/sf of exterior wall surface area for BackSpace Plenum, Point of Sale Plenum and Front Retail Plenum (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on)
HVAC System Type |  |  |  |  | Same as Stand-alone Retail
System Type | Packaged single zone air conditioning unit | Packaged VAV with hot-water reheat with one system per floor serving all zones in the floor | VAV with hot-water reheat with one system per floor serving all zones in the floor | Unit heater in Front_entry, Packaged single zone air conditioning unit for other zones. |  | Packaged single zone (One PSZ per zone) | Packaged Terminal Air Conditioner (One PTAC per zone) | 4 pipe fan coil system (One FPFC per zone with central boiler and chiller)
Heating type | Gas furnace inside the packaged air conditioning unit | Gas furnace inside the packaged air conditioning unit | Gas boiler | Gas furnace inside the packaged air conditioning unit for back_space, core_retail, point_of_sale, and front_retail. Standalone gas furnace for front_entry. |  | Gas furnace | Electric heating | Heating hot water
Cooling type | Packaged air conditioning unit | Packaged air conditioning unit | Water cooled Centrifugal chillers (2) | Packaged air conditioning unit for back_space, core_retail, point_of_sale, and front_retail. No cooling for front_entry. |  | Single speed DX cooling | Single speed DX cooling | Chilled water system
Distribution and terminal units | Single zone constant air volume distribution. | VAV terminal box with damper and hot-water reheating coil with Single maximum control logic. Zone control type: minimum supply air at 25% of the zone maximum air flow rate. | VAV terminal box with damper and hot-water reheating coil with Single maximum control logic. Zone control type: minimum supply air at 30% of the zone maximum air flow rate. | Constant air volume air distribution 3 single-zone roof top units serving thermal zones back_space, point_of_sale, and front_retail with Duct loss - 4% of design flow rate. Variable Air Volume distribution with damper and reheat coil in core_retail zone with Zone minimum supply air at 50% of zone maximum air flow rate. |  | Single zone Constant air volume distribution | Constant Air Volume distribution | 4 pipe fan coil unit
HVAC Sizing
Cooling | Autosized with sizing factor of 1.15 | Autosized with sizing factor of 1.15 | Autosized with sizing factor of 1.15 | Autosized with sizing factor of 1.15 |  | Autosized with sizing factor of 1.15 | Autosized with sizing factor of 1.15 | Autosized with sizing factor of 1.15
Heating | Autosized with sizing factor of 1.25 | Autosized with sizing factor of 1.25 | Autosized with sizing factor of 1.25 | Autosized with sizing factor of 1.25 |  | Autosized with sizing factor of 1.25 | Autosized with sizing factor of 1.25 | Autosized with sizing factor of 1.25
HVAC Efficiency
Cooling | EER-11 (COP- 3.8445) | EER-11-Bottom VAV, 10 -Mid and Top VAV (COP- 3.23 - Bottom VAV, 2.93 Mid and Top VAV) | COP-6.1 | EER-10/COP-3.02 for back_space, point_of_sale, and front_retail. No cooling for front_entry) EER-9.5/COP-2.78 for core_retail |  | COP-3.2/EER- 11 | COP-3.2/EER- 11 | Chiller COP-6.1
Heating | 80% | 80% | 80% | 80% |  | 80% | 80% | 80%
HVAC Control
Thermostat Setpoint | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating |  | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating
Thermostat Setback | 85°F Cooling/60°F Heating | 80°F Cooling/60°F Heating | 80°F Cooling/60°F Heating | 85°F Cooling/60°F Heating |  | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating
|  | Medium Office Building Schedule for Heating/Cooling setpoint Schedule | Large Office Building Schedule for Heating/Cooling setpoint Schedule | Stand-alone Retail Schedule for Heating/Cooling setpoint Schedule AssemblySchedule for Back Space, Front Entry Retail Schedule for Front Retail, Core Retail & Point of Sale |  | Strip mall Schedule for Heating/Cooling setpoint Schedule | Strip mall Schedule for Heating/Cooling setpoint Schedule | Strip mall Schedule for Heating/Cooling setpoint Schedule
Design Supply air temperature | Maximum 104F, Minimum 55F | Maximum 104F, Minimum 55F Reheat coil max reheat temp 122F | Maximum 104F, Minimum 55F Reheat coil max reheat temp 122F | Maximum 104F, Minimum 55F Reheat coil max reheat temp 122F |  | Maximum 122°F, Minimum 55°F | Maximum 122°F, Minimum 55°F | Maximum 122°F, Minimum 55°F
Supply air temperature reset | NA | SAT reset by Demand (5F max temperature reset) | SAT reset by Demand (5F max temperature reset) | SAT reset by Demand (5F max temperature reset) |  | NA | NA | NA
Chilled water supply temperatures | NA | NA | 44°F | NA |  | NA | NA | 44°F
Chilled water return temperatures | NA | NA | 64°F | NA |  | NA | NA
Chilled water supply temperature reset | NA | NA | None | NA |  | NA | NA | Reset (44°F-54°F ) based on outdoor air temperature
Condenser Type | NA | NA | Water-cooled, no reset | NA |  | NA | NA | Water cooled, no reset
Hot water supply temperatures | NA | 180°F | 180°F | NA |  | NA | NA | 180°F
Hot water supply temperature reset | NA | None | None | NA |  | NA | NA | Reset (150°F-180°F ) based on outdoor air temperature
Economizers | No economizer | Differential Dry bulb economizer (Integrated) | Differential Dry bulb economizer (Integrated) | Differential Dry bulb economizer (integrated) |  | Differential Dry bulb economizer (Integrated) | No economizer | No economizer
Ventilation | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | Point of Sale & Core and Front Retail -0.2 cfm/ft2; Backspace, Front Entry-0.15 cfm/ft2 |  | Max of 15 cfm/person or 0.20 cfm/ft2 | Max of 15 cfm/person or 0.20 cfm/ft2 | Max of 15 cfm/person or 0.20 cfm/ft2
Supply Fan
Fan type | CAV | Variable Volume | Constant Volume for Basement,Variable Volume for all others | Constant Volume for Front entry, VAV for Core Retail and OnOff for all other zones |  | OnOff | OnOff | OnOff
Fan schedules | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule AssemblySchedule for Back Space, Front Entry Retail Schedule for Front Retail, Core Retail & Point of Sale |  | Strip mall Schedule | Strip mall Schedule | Strip mall Schedule
Supply Fan Total Efficiency (%) | 55.56% | 60% Bottom VAV, 62% -Mid and Top VAV | 60% (for CAV fan) and 60.84% (for all VAV fans) | 60.% (VAV), 56.25% (all other fans) |  | 60% | 60% | 60%
Fan Motor Efficiency | 85.5% | 92.4% | 93% (for CAV) and 94% (for VAV fans) | 92.4% (VAV), 86.5% (all other fans) |  | 86.5% | 86.5% | 86.5%
Supply Fan Pressure Rise | 2.49910709 ftinH2O | 3 inH20 Bottom VAV, 3 inH20 -Mid and Top VAV | 4.1 inH20 (for CAV), 5.6 inH2O (for VAV) | 4.09in H2O (VAV), 2.5in H2O (all other fans) |  | 2.50 inH2O | 2.50 inH2O | 2.50 inH2O
Pump
Pump Type | NA | SHW: Variable Speed HW: Constant Speed variable flow | SHW: Variable Speed HW: Constant Speed variable flow, Cooling Tower:Constant Speed, CHW: Constant PrimaryVariable Secondary (constant flow to chillers with bypass, variable flow to coils) | NA |  | NA | NA | Variable speed pumps for condenser water, chilled water and heating hot water systems
Rated Pump Head | NA | SHW: 5.9 ft H20, HW: 63.5 ft H20 | SHW:63.4 ft H20, HW: 60 ft H20, Cooling Tower:54 ft H20, CHW Primary: 15 ft H20, CHW Secondary: 60 ft H20 | NA |  | NA | NA | HW- 63.5 ftH2O CHW- 30.0 ftH2O CW- 20.0 ftH2O
Pump Power |  | SHW: 30.57 W, HW: 555.4 W | SHW:284.1312843 W, HW: 2345.78724 | NA |  |  |  | HW-615 W
Pump Motor Power per Unit Flow |  | SHW: 19 W/gpm, HW: 19 W/gpm | SHW: 19 W/gpm, HW: 19 W/gpm | NA |  |  |  | Hw: 19 W/gpm
Pump Efficiency | NA | Motor efficiency- SHW:0.9, HW: 0.9 Total efficiency- SHW: 63%, HW:63% | Motor efficiency- SHW:0.9. HW: 0.9, Cooling Tower:0.87, CHW Primary, Secondary:0.9 | NA |  | NA | NA | Motor efficiency: 0.9
Cooling Tower
Cooling Tower Type | NA | NA | open cooling tower with two speed fan | NA |  | NA | NA | open cooling tower with two speed fan
Tower range | NA | NA | 10F (Design CW supply temp. 85F, CW return temp 95F) | NA |  | NA | NA | 10F (Design CW supply temp. 85F, CW return temp 95F)
Tower Approach | NA | NA | 7F (Tower leaving temp 85F and wet-bulb 78F) |  |  | NA | NA | 7F (Tower leaving temp 85F and wet-bulb 78F)
Design Flow rate |  | NA | 3 gpm/Nominal Capacity |  |  |  |  | 3 gpm/Nominal Capacity
Cooling Tower Efficiency | NA | NA | 40 gpm/hp (high speed) 300. 59 gpm/hp (low speed) | NA |  | NA | NA | 48.5 gpm/hp (high speed) 303 gpm/hp (low speed)
Service Water Heating
SWH type | Storage Tank | Storage Tank | Storage Tank | Tank |  | NA | Same as Strip Mall- PSZ System | Same as Strip Mall- PSZ System
Fuel type | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | NA
Thermal efficiency (%) | 80% | 80% | 80% | 78% |  | NA
Peak Use Flow rate (gpm) | 40 gal | 1.61 gpm | 14.95 gpm | 1.86 gpm |  | NA
Peak Use Flow rate Schedule |  | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | NA
Water temperature setpoint | 120°F | 120°F | 120°F | 135°F |  | NA
Water temperature setpoint Schedule |  | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | NA
Water Heater Max Capacity (Btuh) |  | 64355.46 Btuh | 598171.13 Btuh | 40000 Btuh |  | NA
Water consumption | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | NA
Lighting Load
Lighting power density (W/ft2) | 0.8 W/ft2 | 0.75 W/ft2 | 0.75 W/ft2 | Point of sale, Retail-1.2 W/ft2,, Lobby-1.5 W/ft2, Backspace-0.6 W/ft2 |  | 1.2 W/ft2
Schedule | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule AssemblySchedule for Back Space, Front Entry Rtail Schedule for Front Retail, Core Retail & Point of Sale |  | Strip mall Schedule
Daylighting Controls | NA | NA | Continuous control in Primary and Secondary daylit area in all above grade perimeter zones. Refer LargeOfficeDaylight for more details | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . Refer StandAloneDaylight for more details |  | NA
Plug load
Electric power density (W/ft2) | 1.34 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | Point of sale, Retail-1.0 W/ft2, Backspace-0.2 W/ft2 |  | 0.5 W/ft2
Schedule | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule AssemblySchedule for Back Space, Front Entry Rtail Schedule for Front Retail, Core Retail & Point of Sale |  | Strip mall Schedule
Occupancy
Average people | 100- ft2/person | 100 ft2/person | 100 ft2/person | Point of sale, Retail - 30 ft2/person, Back Space- 333 ft2/person, Front Entry - 100 ft2/person |  | 30 ft2/person
Schedule | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule AssemblySchedule for Back Space, Front Entry Rtail Schedule for Front Retail, Core Retail & Point of Sale |  | Strip mall Schedule
Elevator
Quantity | NA | NA | NA | NA |  | NA
Motor type
Peak Motor Power (W/elevator)
Heat Gain to Building
Peak Fan/lights Power (W/elevator)
Motor and fan/lights Schedules
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Results (hidden)
| TEST RESULTS |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  |  | 16
| Test Case |  | Annual TDV EUI |  | Annual TDV EUI- Electricity |  | Annual TDV EUI- Natural Gas |  | Annual Total End Use Site Energy EUI |  | Annual End Use Site Energy EUI | [17 empty] | Variation from Baseline |  |  |  |  | Reference Model Occupied Unmet Load Hrs | Applicant Model Occupied Unmet Load Hrs
|  |  | (kBtu/sqft) |  | (kwh/sqft) |  | (therm/sqft) |  | (kBtu/sqft) |  | Heating (kBtu/sqft) |  | Cooling (kBtu/sqft) |  | Interior Lighting (kBtu/sqft) |  | Interior Equipment (kBtu/sqft) |  | Exterior Lighting (kBtu/sqft) |  | Fans (kBtu/sqft) |  | Pumps (kBtu/sqft) |  | Refrigeration (kBtu/sqft) |  | Water Heating (kBtu/sqft) |  | TDV % variation |  | Total End Use Site Energy % Variation
|  |  | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Pass/Fail
3 |  | Medium Office CZ-15 Baseline | 294.5639 |  | 10.3283 |  | 0.15484 |  | 50.722 |  | 0.35207 |  | 14.9552 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1483 |  | 0.12814 |  | 0 |  | 15.1282 | [6 empty] | 677.25
4 | 1 | Envelope Test Medium OfficeCZ-15 Roof Insulation | 293.7428 |  | 10.3019 |  | 0.15472 |  | 50.6193 |  | 0.33952 |  | 14.8696 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1449 |  | 0.12708 |  | 0 |  | 15.1282 |  | 0.2788% |  | 0.2024% |  | PASS | 674.5
5 | 2 | Envelope Test Medium OfficeCZ-15 Wall Insulation | 293.4568 |  | 10.2961 |  | 0.15467 |  | 50.5944 |  | 0.33475 |  | 14.8596 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.137 |  | 0.12513 |  | 0 |  | 15.1282 |  | 0.3758% |  | 0.2516% |  | PASS | 676.75
6 | 3 | Envelope Test Medium OfficeCZ-15 Floor Slab Insulation | 295.5473 |  | 10.364 |  | 0.15471 |  | 50.8303 |  | 0.33899 |  | 15.0632 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1674 |  | 0.12266 |  | 0 |  | 15.1282 |  | -0.3338% |  | -0.2136% |  | PASS | 673.5
7 | 4 | Envelope Test Medium OfficeCZ-15 Infiltration | 295.0579 |  | 10.3399 |  | 0.15499 |  | 50.7763 |  | 0.36673 |  | 14.9888 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1511 |  | 0.13132 |  | 0 |  | 15.1282 |  | -0.1677% |  | -0.107% |  | PASS | 676
8 |  | Medium Office CZ-16 Baseline | 207.5921 |  | 6.8524 |  | 0.2365 |  | 47.0258 |  | 8.5162 |  | 3.307 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4761 |  | 0.58519 |  | 0 |  | 15.1282 | [6 empty] | 822.5
9 | 5 | Envelope Test Medium OfficeCZ-16 Roof Insulation | 206.9981 |  | 6.8445 |  | 0.23479 |  | 46.8277 |  | 8.3451 |  | 3.2893 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4728 |  | 0.57918 |  | 0 |  | 15.1282 |  | 0.2861% |  | 0.4213% |  | PASS | 822.25
10 | 6 | Envelope Test Medium OfficeCZ-16 Wall Insulation | 206.9608 |  | 6.8463 |  | 0.23417 |  | 46.7715 |  | 8.2827 |  | 3.2974 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4735 |  | 0.57635 |  | 0 |  | 15.1282 |  | 0.3041% |  | 0.5408% |  | PASS | 821
11 | 7 | Envelope Test Medium OfficeCZ-16 Floor Slab Insulation | 207.7464 |  | 6.8598 |  | 0.23577 |  | 46.9781 |  | 8.4432 |  | 3.3305 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4873 |  | 0.57582 |  | 0 |  | 15.1282 |  | -0.07433% |  | 0.1015% |  | PASS | 816.75
12 | 8 | Envelope Test Medium OfficeCZ-16 Infiltration | 208.1379 |  | 6.8567 |  | 0.23908 |  | 47.2984 |  | 8.7742 |  | 3.3052 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4772 |  | 0.60038 |  | 0 |  | 15.1282 |  | -0.2629% |  | -0.5795% |  | PASS | 817
13 |  | Medium Office CZ-6 Baseline | 209.3173 |  | 7.505 |  | 0.15807 |  | 41.4112 |  | 0.67479 |  | 6.1474 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2533 |  | 0.19441 |  | 0 |  | 15.1282 | [6 empty] | 245.75
14 | 9 | Envelope Test Medium OfficeCZ-6 Roof Insulation | 208.827 |  | 7.4944 |  | 0.15765 |  | 41.3331 |  | 0.6329 |  | 6.1148 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2522 |  | 0.19176 |  | 0 |  | 15.1282 |  | 0.2342% |  | 0.1886% |  | PASS | 246.75
15 | 10 | Envelope Test Medium OfficeCZ-6 Wall Insulation | 209.0477 |  | 7.5014 |  | 0.15761 |  | 41.3534 |  | 0.62919 |  | 6.1396 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2552 |  | 0.18787 |  | 0 |  | 15.1282 |  | 0.1288% |  | 0.1396% |  | PASS | 246.5
16 | 11 | Envelope Test Medium OfficeCZ-6 Floor Slab Insulation | 209.6939 |  | 7.5167 |  | 0.15792 |  | 41.4356 |  | 0.65959 |  | 6.1887 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.263 |  | 0.1831 |  | 0 |  | 15.1282 |  | -0.1799% |  | -0.0589% |  | PASS | 231.25
17 | 12 | Envelope Test Medium OfficeCZ-6 Infiltration | 209.3185 |  | 7.5029 |  | 0.15831 |  | 41.428 |  | 0.69883 |  | 6.1383 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2506 |  | 0.19866 |  | 0 |  | 15.1282 |  | -0.0005911% |  | -0.04055% |  | PASS | 250.75
18 |  | Small Office CZ-15 SolarReflectance-Low Slope Baseline | 224.9749 |  | 8.7755 |  | 0.037977 |  | 33.7399 |  | 0.82687 |  | 8.9009 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9466 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 146.33
19 | 13 | Envelope Test Small OfficeCZ-15 SolarReflectance-Low Slope | 223.4125 |  | 8.7204 |  | 0.038097 |  | 33.5642 |  | 0.83893 |  | 8.7511 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9104 |  | 0 |  | 0 |  | 2.9699 |  | 0.6945% |  | 0.5208% |  | PASS | 147.33
20 |  | Small Office CZ-16 SolarReflectance-Low Slope Baseline | 227.8293 |  | 8.8658 |  | 0.038321 |  | 34.0827 |  | 0.86133 |  | 9.1456 |  | 6.1447 |  | 12.9509 |  | 0 |  | 2.0086 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 152.67
21 | 14 | Envelope Test Small OfficeCZ-16 SolarReflectance-Low Slope | 225.5537 |  | 8.7856 |  | 0.038511 |  | 33.8277 |  | 0.88028 |  | 8.9268 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9535 |  | 0 |  | 0 |  | 2.9699 |  | 0.9988% |  | 0.748% |  | PASS | 146.83
22 |  | Small Office CZ-6 SolarReflectance-Low Slope Baseline | 185.13 |  | 7.3356 |  | 0.051434 |  | 30.1722 |  | 2.1723 |  | 4.534 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.3936 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 78.83
23 | 15 | Envelope Test Small OfficeCZ-6 SolarReflectance-Low Slope | 183.2247 |  | 7.269 |  | 0.051951 |  | 29.9965 |  | 2.2222 |  | 4.36 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.3419 |  | 0 |  | 0 |  | 2.9699 |  | 1.029% |  | 0.5824% |  | FAIL | 80.67
24 |  | Small Office CZ-15 SolarReflectance-Steep Slope Baseline | 189.5434 |  | 7.4684 |  | 0.052589 |  | 30.7407 |  | 2.286 |  | 4.8699 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.5108 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 82.16
25 | 16 | Envelope Test Small OfficeCZ-15 SolarReflectance-Steep Slope | 186.6769 |  | 7.3669 |  | 0.053329 |  | 30.4685 |  | 2.3618 |  | 4.6064 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.4298 |  | 0 |  | 0 |  | 2.9699 |  | 1.512% |  | 0.8854% |  | FAIL | 82.17
26 |  | Small Office CZ-16 SolarReflectance-Steep Slope Baseline | 181.6485 |  | 6.8787 |  | 0.10673 |  | 34.1412 |  | 7.7003 |  | 3.0405 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3385 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 163.16
27 | 17 | Envelope Test Small OfficeCZ-16 SolarReflectance-Steep Slope | 180.8061 |  | 6.8444 |  | 0.1078 |  | 34.1309 |  | 7.8071 |  | 2.9526 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3092 |  | 0 |  | 0 |  | 2.9699 |  | 0.4637% |  | 0.03027% |  | PASS | 160.5
28 |  | Small Office CZ-6 SolarReflectance-Steep Slope Baseline | 183.8604 |  | 6.9448 |  | 0.1075 |  | 34.4444 |  | 7.7778 |  | 3.2007 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.4057 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 161.34
29 | 18 | Envelope Test Small OfficeCZ-6 SolarReflectance-Steep Slope | 182.6063 |  | 6.8934 |  | 0.109 |  | 34.4186 |  | 7.9276 |  | 3.0698 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3609 |  | 0 |  | 0 |  | 2.9699 |  | 0.6821% |  | 0.07502% |  | PASS | 158.33
30 |  | Envelope Test Primary SchoolCZ-15 Light | 223.6777 |  | 8.725 |  | 0.03827 |  | 33.5969 |  | 0.85616 |  | 8.7631 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9121 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 148
31 | 19 | Envelope Test Primary SchoolCZ-15 Heavy | 223.2729 |  | 8.7179 |  | 0.038063 |  | 33.5521 |  | 0.83549 |  | 8.7338 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9156 |  | 0 |  | 0 |  | 2.9699 |  | 0.181% |  | 0.08101% |  | PASS | 150.67
32 |  | Envelope Test Primary SchoolCZ-16 Light | 181.2833 |  | 6.8631 |  | 0.10742 |  | 34.1567 |  | 7.7692 |  | 2.9991 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3264 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 160.17
33 | 20 | Envelope Test Primary SchoolCZ-16 Heavy | 180.9009 |  | 6.8545 |  | 0.10678 |  | 34.0637 |  | 7.7054 |  | 2.9819 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3161 |  | 0 |  | 0 |  | 2.9699 |  | 0.211% |  | 0.1251% |  | PASS | 159.34
34 |  | Envelope Test Primary SchoolCZ-6 Light | 184.4065 |  | 7.3104 |  | 0.052123 |  | 30.155 |  | 2.2412 |  | 4.4668 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.3764 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 79.84
35 | 21 | Envelope Test Primary SchoolCZ-6 Heavy | 183.8862 |  | 7.2993 |  | 0.051279 |  | 30.0327 |  | 2.1568 |  | 4.4376 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.3661 |  | 0 |  | 0 |  | 2.9699 |  | 0.2821% |  | 0.1519% |  | PASS | 79.34
36
37 |  | Medium Office CZ-15 Baseline | 294.5639 |  | 10.3283 |  | 0.15484 |  | 50.722 |  | 0.35207 |  | 14.9552 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1483 |  | 0.12814 |  | 0 |  | 15.1282 | [6 empty] | 677.25
38 | 22 | Envelope Glazing Test Medium OfficeCZ-15 Window U | 292.5652 |  | 10.2822 |  | 0.15409 |  | 50.4899 |  | 0.2773 |  | 14.812 |  | 5.059 |  | 12.9515 |  | 0 |  | 2.1493 |  | 0.11258 |  | 0 |  | 15.1282 |  | 0.6785% |  | 0.4575% |  | PASS | 684.75
39 | 23 | Envelope Glazing Test Medium OfficeCZ-15 Window SHGC | 288.5239 |  | 10.1094 |  | 0.15528 |  | 50.0184 |  | 0.39554 |  | 14.3202 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.0337 |  | 0.13061 |  | 0 |  | 15.1282 |  | 2.051% |  | 1.387% |  | FAIL | 636.25
40 | 24 | Envelope Glazing Test Medium OfficeCZ-15 Window U&SHGC | 286.4189 |  | 10.0607 |  | 0.15437 |  | 49.7614 |  | 0.30488 |  | 14.1682 |  | 5.059 |  | 12.9515 |  | 0 |  | 2.0339 |  | 0.11594 |  | 0 |  | 15.1282 |  | 2.765% |  | 1.894% |  | FAIL | 633.25
41 |  | Medium Office CZ-16 Baseline | 207.5921 |  | 6.8524 |  | 0.2365 |  | 47.0258 |  | 8.5162 |  | 3.307 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4761 |  | 0.58519 |  | 0 |  | 15.1282 | [6 empty] | 822.5
42 | 25 | Envelope Glazing Test Medium OfficeCZ-16 Window U | 206.3141 |  | 6.8619 |  | 0.22775 |  | 46.1828 |  | 7.6408 |  | 3.3457 |  | 5.0624 |  | 12.9515 |  | 0 |  | 1.4996 |  | 0.55479 |  | 0 |  | 15.1282 |  | 0.6156% |  | 1.793% |  | PASS | 813
43 | 26 | Envelope Glazing Test Medium OfficeCZ-16 Window SHGC | 204.8334 |  | 6.7642 |  | 0.23781 |  | 46.8551 |  | 8.6465 |  | 3.1028 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.3823 |  | 0.58218 |  | 0 |  | 15.1282 |  | 1.329% |  | 0.3631% |  | FAIL | 842.5
44 | 27 | Envelope Glazing Test Medium OfficeCZ-16 Window U&SHGC | 203.441 |  | 6.7717 |  | 0.22884 |  | 45.9843 |  | 7.7502 |  | 3.1396 |  | 5.0624 |  | 12.9515 |  | 0 |  | 1.4028 |  | 0.54984 |  | 0 |  | 15.1282 |  | 2% |  | 2.215% |  | FAIL | 815.5
45 |  | Medium Office CZ-6 Baseline | 209.3173 |  | 7.505 |  | 0.15807 |  | 41.4112 |  | 0.67479 |  | 6.1474 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2533 |  | 0.19441 |  | 0 |  | 15.1282 | [6 empty] | 245.75
46 | 28 | Envelope Glazing Test Medium OfficeCZ-6 Window U | 209.7913 |  | 7.5337 |  | 0.15686 |  | 41.3884 |  | 0.55408 |  | 6.2366 |  | 5.0624 |  | 12.9515 |  | 0 |  | 1.2835 |  | 0.17232 |  | 0 |  | 15.1282 |  | -0.2265% |  | 0.05506% |  | PASS | 231
47 | 29 | Envelope Glazing Test Medium OfficeCZ-6 Window SHGC | 205.8698 |  | 7.388 |  | 0.15848 |  | 41.0529 |  | 0.7158 |  | 5.8174 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.1785 |  | 0.19989 |  | 0 |  | 15.1282 |  | 1.647% |  | 0.8651% |  | FAIL | 269.5
48 | 30 | Envelope Glazing Test Medium OfficeCZ-6 Window U&SHGC | 206.2687 |  | 7.4151 |  | 0.15715 |  | 41.0124 |  | 0.58271 |  | 5.9047 |  | 5.0624 |  | 12.9515 |  | 0 |  | 1.2062 |  | 0.17692 |  | 0 |  | 15.1282 |  | 1.456% |  | 0.9628% |  | FAIL | 258.5
49 |  | Large Office CZ-7 Baseline | 209.1751 |  | 8.5106 |  | 0.051375 |  | 34.1755 |  | 0.51816 |  | 3.3156 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.5473 |  | 1.686 |  | 0 |  | 4.6184 | [6 empty] | 325.75
50 | 31 | Envelope Glazing Test Large OfficeCZ-7 WWR 20% | 206.2328 |  | 8.4296 |  | 0.050922 |  | 33.8539 |  | 0.47285 |  | 3.1662 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.5186 |  | 1.6002 |  | 0 |  | 4.6183 |  | 1.407% |  | 0.9409% |  | FAIL | 194
51 | 32 | Envelope Glazing Test Large OfficeCZ-7 WWR 60% | 211.547 |  | 8.577 |  | 0.051869 |  | 34.4516 |  | 0.56752 |  | 3.4414 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.576 |  | 1.7474 |  | 0 |  | 4.6184 |  | -1.134% |  | -0.8081% |  | FAIL | 477
52 | 33 | Envelope Glazing Test Large OfficeCZ-7 WWR 60% with South overhang | 209.8252 |  | 8.5192 |  | 0.051884 |  | 34.2558 |  | 0.56903 |  | 3.356 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.502 |  | 1.7155 |  | 0 |  | 4.6184 |  | -0.3108% |  | -0.2352% |  | PASS | 480.75
53 |  | Large Office CZ-1 Baseline | 180.2285 |  | 7.2061 |  | 0.099686 |  | 34.5543 |  | 5.3506 |  | 0.27201 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8179 |  | 0.28964 |  | 0 |  | 4.6184 | [6 empty] | 347
54 | 34 | Envelope Glazing Test Large OfficeCZ-1 WWR 20% | 179.3501 |  | 7.2122 |  | 0.095753 |  | 34.182 |  | 4.9573 |  | 0.26046 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8625 |  | 0.27777 |  | 0 |  | 4.6184 |  | 0.4874% |  | 1.077% |  | PASS | 280.75
55 | 35 | Envelope Glazing Test Large OfficeCZ-1 WWR 60% | 181.0399 |  | 7.2182 |  | 0.10192 |  | 34.8191 |  | 5.5742 |  | 0.2761 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8471 |  | 0.29753 |  | 0 |  | 4.6184 |  | -0.4502% |  | -0.7665% |  | PASS | 391
56
57 |  | Medium Office CZ-15 Baseline | 294.5639 |  | 10.3283 |  | 0.15484 |  | 50.722 |  | 0.35207 |  | 14.9552 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1483 |  | 0.12814 |  | 0 |  | 15.1282 | [6 empty] | 677.25
58 | 36 | Lighting Tests Medium OfficeCZ-15 low LPD | 285.803 |  | 9.9491 |  | 0.155 |  | 49.4433 |  | 0.36744 |  | 14.683 |  | 4.0468 |  | 12.9515 |  | 0 |  | 2.1384 |  | 0.12796 |  | 0 |  | 15.1282 |  | 2.974% |  | 2.521% |  | FAIL | 709.5
59 | 37 | Lighting Tests Medium OfficeCZ-15 high LPD | 303.4138 |  | 10.7097 |  | 0.15469 |  | 52.008 |  | 0.33687 |  | 15.232 |  | 6.0703 |  | 12.9515 |  | 0 |  | 2.1603 |  | 0.12902 |  | 0 |  | 15.1282 |  | -3.004% |  | -2.535% |  | FAIL | 646.5
60 |  | Medium Office CZ-16 Baseline | 207.5921 |  | 6.8524 |  | 0.2365 |  | 47.0258 |  | 8.5162 |  | 3.307 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4761 |  | 0.58519 |  | 0 |  | 15.1282 | [6 empty] | 822.5
61 | 38 | Lighting Tests Medium OfficeCZ-16 low LPD | 199.9267 |  | 6.5151 |  | 0.23732 |  | 45.9567 |  | 8.5982 |  | 3.2149 |  | 4.0495 |  | 12.9515 |  | 0 |  | 1.439 |  | 0.57564 |  | 0 |  | 15.1282 |  | 3.693% |  | 2.273% |  | FAIL | 845.75
62 | 39 | Lighting Tests Medium OfficeCZ-16 high LPD | 215.0636 |  | 7.1902 |  | 0.23453 |  | 47.9811 |  | 8.3186 |  | 3.3998 |  | 6.0742 |  | 12.9515 |  | 0 |  | 1.514 |  | 0.59473 |  | 0 |  | 15.1282 |  | -3.599% |  | -2.031% |  | FAIL | 806.25
63 |  | Medium Office CZ-6 Baseline | 209.3173 |  | 7.505 |  | 0.15807 |  | 41.4112 |  | 0.67479 |  | 6.1474 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2533 |  | 0.19441 |  | 0 |  | 15.1282 | [6 empty] | 245.75
64 | 40 | Lighting Tests Medium OfficeCZ-6 low LPD | 201.1365 |  | 7.1446 |  | 0.15837 |  | 40.2116 |  | 0.70519 |  | 5.9671 |  | 4.0495 |  | 12.9515 |  | 0 |  | 1.2172 |  | 0.19318 |  | 0 |  | 15.1282 |  | 3.908% |  | 2.897% |  | FAIL | 258.75
65 | 41 | Lighting Tests Medium OfficeCZ-6 high LPD | 217.58 |  | 7.8659 |  | 0.15777 |  | 42.6125 |  | 0.64492 |  | 6.3292 |  | 6.0742 |  | 12.9515 |  | 0 |  | 1.2897 |  | 0.19494 |  | 0 |  | 15.1282 |  | -3.947% |  | -2.901% |  | FAIL | 235
66
67 |  | Large Office CZ-7 Baseline | 209.1751 |  | 8.5106 |  | 0.051375 |  | 34.1755 |  | 0.51816 |  | 3.3156 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.5473 |  | 1.686 |  | 0 |  | 4.6184 | [6 empty] | 325.75
68 | 42 | Daylighting Tests Large OfficeCZ-7 Continuous Dimming | 201.666 |  | 8.1953 |  | 0.05177 |  | 33.1393 |  | 0.55762 |  | 3.2328 |  | 5.2785 |  | 15.0362 |  | 0 |  | 2.4954 |  | 1.6388 |  | 0 |  | 4.6184 |  | 3.59% |  | 3.032% |  | FAIL | 366.5
69 | 43 | Daylighting Tests Large OfficeCZ-7 Continuous Dimming and high VT | 201.7138 |  | 8.1941 |  | 0.05178 |  | 33.136 |  | 0.55861 |  | 3.2358 |  | 5.2722 |  | 15.0362 |  | 0 |  | 2.4945 |  | 1.6386 |  | 0 |  | 4.6184 |  | 3.567% |  | 3.042% |  | FAIL | 366.5
70 | 44 | Daylighting Tests Large OfficeCZ-7 Stepped Dimming | 198.9275 |  | 8.0748 |  | 0.051913 |  | 32.7425 |  | 0.57195 |  | 3.1994 |  | 4.9398 |  | 15.0362 |  | 0 |  | 2.4796 |  | 1.6186 |  | 0 |  | 4.6184 |  | 4.899% |  | 4.193% |  | FAIL | 383.75
71 | 45 | Daylighting Tests Large OfficeCZ-7 Stepped Dimming and high VT | 198.7724 |  | 8.0661 |  | 0.051941 |  | 32.7153 |  | 0.57473 |  | 3.1921 |  | 4.9209 |  | 15.0362 |  | 0 |  | 2.4766 |  | 1.6181 |  | 0 |  | 4.6184 |  | 4.973% |  | 4.273% |  | FAIL | 384.25
72 |  | Large Office CZ-7 WWR 20% Baseline | 206.2328 |  | 8.4296 |  | 0.050922 |  | 33.8539 |  | 0.47285 |  | 3.1662 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.5186 |  | 1.6002 |  | 0 |  | 4.6183 | [6 empty] | 194
73 | 46 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Continuous Dimming | 199.0772 |  | 8.1291 |  | 0.051192 |  | 32.8555 |  | 0.49983 |  | 3.0648 |  | 5.3345 |  | 15.0362 |  | 0 |  | 2.478 |  | 1.5549 |  | 0 |  | 4.6184 |  | 3.47% |  | 2.949% |  | FAIL | 215.5
74 | 47 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Continuous Dimming and high VT | 198.7609 |  | 8.1217 |  | 0.051224 |  | 32.8335 |  | 0.5031 |  | 3.0641 |  | 5.3137 |  | 15.0362 |  | 0 |  | 2.4752 |  | 1.5541 |  | 0 |  | 4.6184 |  | 3.623% |  | 3.014% |  | FAIL | 215.25
75 | 48 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Stepped Dimming | 197.1025 |  | 8.0496 |  | 0.051198 |  | 32.585 |  | 0.50044 |  | 3.0418 |  | 5.111 |  | 15.0362 |  | 0 |  | 2.4691 |  | 1.5414 |  | 0 |  | 4.6183 |  | 4.427% |  | 3.748% |  | FAIL | 225
76 | 49 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Stepped Dimming and high VT | 196.6667 |  | 8.0293 |  | 0.051252 |  | 32.521 |  | 0.50586 |  | 3.0429 |  | 5.0468 |  | 15.0362 |  | 0 |  | 2.4673 |  | 1.5373 |  | 0 |  | 4.6184 |  | 4.638% |  | 3.937% |  | FAIL | 225.25
77 |  | Large Office CZ-7 WWR 60% Baseline | 211.547 |  | 8.577 |  | 0.051869 |  | 34.4516 |  | 0.56752 |  | 3.4414 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.576 |  | 1.7474 |  | 0 |  | 4.6184 | [6 empty] | 477
78 | 50 | Daylighting Tests Large OfficeCZ-7WWR-60%,Continuous Dimming | 204.1573 |  | 8.2628 |  | 0.052228 |  | 33.4153 |  | 0.60342 |  | 3.3572 |  | 5.2811 |  | 15.0362 |  | 0 |  | 2.527 |  | 1.6997 |  | 0 |  | 4.6184 |  | 3.493% |  | 3.008% |  | FAIL | 522.5
79 | 51 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Continuous Dimming and high VT | 204.0337 |  | 8.2577 |  | 0.052237 |  | 33.3987 |  | 0.60433 |  | 3.3478 |  | 5.2742 |  | 15.0362 |  | 0 |  | 2.5259 |  | 1.6997 |  | 0 |  | 4.6184 |  | 3.552% |  | 3.056% |  | FAIL | 522.25
80 | 52 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Stepped Dimming | 201.2606 |  | 8.1389 |  | 0.052351 |  | 33.0048 |  | 0.61573 |  | 3.3061 |  | 4.9465 |  | 15.0362 |  | 0 |  | 2.5125 |  | 1.6804 |  | 0 |  | 4.6184 |  | 4.862% |  | 4.2% |  | FAIL | 536.25
81 | 53 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Stepped Dimming and high VT | 201.0881 |  | 8.1297 |  | 0.05238 |  | 32.9763 |  | 0.61866 |  | 3.2978 |  | 4.9263 |  | 15.0362 |  | 0 |  | 2.5097 |  | 1.6807 |  | 0 |  | 4.6184 |  | 4.944% |  | 4.282% |  | FAIL | 536.25
82 |  | Large Office CZ-1 Baseline | 180.2285 |  | 7.2061 |  | 0.099686 |  | 34.5543 |  | 5.3506 |  | 0.27201 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8179 |  | 0.28964 |  | 0 |  | 4.6184 | [6 empty] | 347
83 | 54 | Daylighting Tests Large OfficeCZ-1 Continuous Dimming | 174.4021 |  | 6.9223 |  | 0.10453 |  | 34.0703 |  | 5.8353 |  | 0.26158 |  | 5.2946 |  | 15.0362 |  | 0 |  | 2.7385 |  | 0.28108 |  | 0 |  | 4.6184 |  | 3.233% |  | 1.401% |  | FAIL | 354.75
84 | 55 | Daylighting Tests Large OfficeCZ-1 Continuous Dimming and high VT | 174.3376 |  | 6.9184 |  | 0.10462 |  | 34.0661 |  | 5.8443 |  | 0.26158 |  | 5.2835 |  | 15.0362 |  | 0 |  | 2.7363 |  | 0.2811 |  | 0 |  | 4.6184 |  | 3.269% |  | 1.413% |  | FAIL | 354.5
85 | 56 | Daylighting Tests Large OfficeCZ-1 Stepped Dimming | 172.3111 |  | 6.8257 |  | 0.10615 |  | 33.9026 |  | 5.9975 |  | 0.25778 |  | 4.9898 |  | 15.0362 |  | 0 |  | 2.7213 |  | 0.27711 |  | 0 |  | 4.6184 |  | 4.393% |  | 1.886% |  | FAIL | 359.25
86 | 57 | Daylighting Tests Large OfficeCZ-1 Stepped Dimming and high VT | 172.1336 |  | 6.814 |  | 0.10644 |  | 33.892 |  | 6.0267 |  | 0.25764 |  | 4.9585 |  | 15.0362 |  | 0 |  | 2.7131 |  | 0.27682 |  | 0 |  | 4.6184 |  | 4.492% |  | 1.917% |  | FAIL | 359.25
87 |  | Large Office CZ-1 WWR-20% Baseline | 179.3501 |  | 7.2122 |  | 0.095753 |  | 34.182 |  | 4.9573 |  | 0.26046 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8625 |  | 0.27777 |  | 0 |  | 4.6184 | [6 empty] | 280.75
88 | 58 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Continuous Dimming | 174.0325 |  | 6.9534 |  | 0.10063 |  | 33.7861 |  | 5.445 |  | 0.2534 |  | 5.3818 |  | 15.0362 |  | 0 |  | 2.7772 |  | 0.26969 |  | 0 |  | 4.6183 |  | 2.965% |  | 1.158% |  | FAIL | 295.25
89 | 59 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Continuous Dimming and high VT | 173.874 |  | 6.9427 |  | 0.10095 |  | 33.7825 |  | 5.4777 |  | 0.25325 |  | 5.3519 |  | 15.0362 |  | 0 |  | 2.771 |  | 0.26954 |  | 0 |  | 4.6184 |  | 3.053% |  | 1.169% |  | FAIL | 296
90 | 60 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Stepped Dimming | 172.6837 |  | 6.9004 |  | 0.10093 |  | 33.6354 |  | 5.4751 |  | 0.25044 |  | 5.2178 |  | 15.0362 |  | 0 |  | 2.7666 |  | 0.2665 |  | 0 |  | 4.6183 |  | 3.717% |  | 1.599% |  | FAIL | 302
91 | 61 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Stepped Dimming and high VT | 172.273 |  | 6.8753 |  | 0.10176 |  | 33.6327 |  | 5.5582 |  | 0.24985 |  | 5.1423 |  | 15.0362 |  | 0 |  | 2.7577 |  | 0.26572 |  | 0 |  | 4.6183 |  | 3.946% |  | 1.607% |  | FAIL | 301.75
92 |  | Large Office CZ-1 WWR-60% Baseline | 181.0399 |  | 7.2182 |  | 0.10192 |  | 34.8191 |  | 5.5742 |  | 0.2761 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8471 |  | 0.29753 |  | 0 |  | 4.6184 | [6 empty] | 391
93 | 62 | Daylighting Tests Large OfficeCZ-1WWR-60%,Continuous Dimming | 175.1306 |  | 6.9383 |  | 0.10588 |  | 34.2599 |  | 5.9701 |  | 0.26614 |  | 5.2989 |  | 15.0362 |  | 0 |  | 2.7779 |  | 0.28749 |  | 0 |  | 4.6184 |  | 3.264% |  | 1.606% |  | FAIL | 404.5
94 | 63 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Continuous Dimming and high VT | 175.0594 |  | 6.9339 |  | 0.10597 |  | 34.2538 |  | 5.979 |  | 0.2661 |  | 5.287 |  | 15.0362 |  | 0 |  | 2.7748 |  | 0.28747 |  | 0 |  | 4.6184 |  | 3.303% |  | 1.624% |  | FAIL | 404.75
95 | 64 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Stepped Dimming | 173.0459 |  | 6.8456 |  | 0.10712 |  | 34.0674 |  | 6.0942 |  | 0.26487 |  | 4.9997 |  | 15.0362 |  | 0 |  | 2.7656 |  | 0.28371 |  | 0 |  | 4.6184 |  | 4.416% |  | 2.159% |  | FAIL | 409.75
96 | 65 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Stepped Dimming and high VT | 172.8574 |  | 6.8339 |  | 0.10737 |  | 34.0528 |  | 6.1195 |  | 0.26471 |  | 4.9677 |  | 15.0362 |  | 0 |  | 2.7576 |  | 0.28388 |  | 0 |  | 4.6184 |  | 4.52% |  | 2.201% |  | FAIL | 408.25
97 |  | Stand Alone Retail CZ-7 Baseline | 279.3036 |  | 9.9747 |  | 0.11062 |  | 45.0945 |  | 2.6474 |  | 5.904 |  | 7.8851 |  | 10.726 |  | 0 |  | 9.5203 |  | 0 |  | 0 |  | 8.4121 | [6 empty] | 0
98 | 66 | Daylighting Tests Stand Alone Retail CZ-7 Skylight VT | 275.8255 |  | 9.8464 |  | 0.11076 |  | 44.6707 |  | 2.6612 |  | 5.8652 |  | 7.5081 |  | 10.726 |  | 0 |  | 9.4976 |  | 0 |  | 0 |  | 8.4121 |  | 1.245% |  | 0.9397% |  | FAIL | 0
99 | 67 | Daylighting Tests Stand Alone Retail CZ-7 SRR-5% | 273.9776 |  | 9.7463 |  | 0.11191 |  | 44.4434 |  | 2.7749 |  | 6.038 |  | 6.74 |  | 10.726 |  | 0 |  | 9.7514 |  | 0 |  | 0 |  | 8.4129 |  | 1.907% |  | 1.444% |  | FAIL | 0
100 | 68 | Daylighting Tests Stand Alone Retail CZ-7 SRR-5% and high VT | 273.1831 |  | 9.7129 |  | 0.11202 |  | 44.3406 |  | 2.786 |  | 6.028 |  | 6.6794 |  | 10.726 |  | 0 |  | 9.7087 |  | 0 |  | 0 |  | 8.4129 |  | 2.191% |  | 1.672% |  | FAIL | 0
101 |  | Stand Alone Retail CZ-1 Baseline | 247.4263 |  | 8.9523 |  | 0.19445 |  | 49.9863 |  | 11.0192 |  | 0.77768 |  | 8.1722 |  | 10.726 |  | 0 |  | 10.8703 |  | 0 |  | 0 |  | 8.4205 | [6 empty] | 0
102 | 69 | Daylighting Tests Stand Alone Retail CZ-1 Skylight VT | 244.2487 |  | 8.8212 |  | 0.19501 |  | 49.5959 |  | 11.0756 |  | 0.77116 |  | 7.7584 |  | 10.726 |  | 0 |  | 10.8442 |  | 0 |  | 0 |  | 8.4209 |  | 1.284% |  | 0.781% |  | FAIL | 0
103 | 70 | Daylighting Tests Stand Alone Retail CZ-1 SRR-5% | 237.9628 |  | 8.4889 |  | 0.20061 |  | 49.0209 |  | 11.633 |  | 0.80801 |  | 6.7558 |  | 10.726 |  | 0 |  | 10.6753 |  | 0 |  | 0 |  | 8.4221 |  | 3.825% |  | 1.931% |  | FAIL | 0
104 | 71 | Daylighting Tests Stand Alone Retail CZ-1 SRR-5% and high VT | 237.111 |  | 8.4456 |  | 0.20102 |  | 48.9145 |  | 11.6745 |  | 0.80993 |  | 6.6491 |  | 10.726 |  | 0 |  | 10.6327 |  | 0 |  | 0 |  | 8.4225 |  | 4.169% |  | 2.144% |  | FAIL | 0
105
106 |  | Medium Office CZ-15 Baseline | 294.5639 |  | 10.3283 |  | 0.15484 |  | 50.722 |  | 0.35207 |  | 14.9552 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1483 |  | 0.12814 |  | 0 |  | 15.1282 | [6 empty] | 677.25
107 | 72 | Equipment test Medium OfficeCZ-15 low EPD | 270.6055 |  | 9.3035 |  | 0.15517 |  | 47.2584 |  | 0.38529 |  | 14.1784 |  | 5.0586 |  | 10.3612 |  | 0 |  | 2.0171 |  | 0.12973 |  | 0 |  | 15.1282 |  | 8.134% |  | 6.829% |  | FAIL | 740.25
108 | 73 | Equipment test Medium OfficeCZ-15 high EPD | 318.5544 |  | 11.3561 |  | 0.15451 |  | 54.1958 |  | 0.31884 |  | 15.7381 |  | 5.0586 |  | 15.5416 |  | 0 |  | 2.2831 |  | 0.12725 |  | 0 |  | 15.1282 |  | -8.144% |  | -6.849% |  | FAIL | 623
109 |  | Medium Office CZ-16 Baseline | 207.5921 |  | 6.8524 |  | 0.2365 |  | 47.0258 |  | 8.5162 |  | 3.307 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4761 |  | 0.58519 |  | 0 |  | 15.1282 | [6 empty] | 822.5
110 | 74 | Equipment test Medium OfficeCZ-16 low EPD | 187.5602 |  | 5.9698 |  | 0.24029 |  | 44.3924 |  | 8.8941 |  | 3.0362 |  | 5.0618 |  | 10.3612 |  | 0 |  | 1.339 |  | 0.57193 |  | 0 |  | 15.1284 |  | 9.65% |  | 5.6% |  | FAIL | 873.75
111 | 75 | Equipment test Medium OfficeCZ-16 high EPD | 227.2777 |  | 7.7363 |  | 0.23071 |  | 49.4624 |  | 7.9367 |  | 3.5792 |  | 5.0618 |  | 15.5416 |  | 0 |  | 1.6195 |  | 0.59544 |  | 0 |  | 15.1282 |  | -9.483% |  | -5.181% |  | FAIL | 786.75
112 |  | Medium Office CZ-6 Baseline | 209.3173 |  | 7.505 |  | 0.15807 |  | 41.4112 |  | 0.67479 |  | 6.1474 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2533 |  | 0.19441 |  | 0 |  | 15.1282 | [6 empty] | 245.75
113 | 76 | Equipment test Medium OfficeCZ-6 low EPD | 187.3558 |  | 6.5496 |  | 0.15872 |  | 38.2166 |  | 0.74019 |  | 5.6035 |  | 5.0618 |  | 10.3612 |  | 0 |  | 1.1227 |  | 0.19883 |  | 0 |  | 15.1282 |  | 10.49% |  | 7.714% |  | FAIL | 277
114 | 77 | Equipment test Medium OfficeCZ-6 high EPD | 231.4286 |  | 8.4622 |  | 0.15755 |  | 44.6248 |  | 0.62265 |  | 6.6928 |  | 5.0618 |  | 15.5416 |  | 0 |  | 1.3883 |  | 0.18964 |  | 0 |  | 15.1282 |  | -10.56% |  | -7.76% |  | FAIL | 216.5
115 |  | Fast food Restaurant CZ-6 Baseline | 2590.0943 |  | 104.3119 |  | 0.80693 |  | 436.5992 |  | 20.2761 |  | 48.3405 |  | 20.7081 |  | 245.6894 |  | 0 |  | 40.5332 |  | 0 |  | 25.0362 |  | 36.0194 | [6 empty] | 97.66
116 | 78 | Equipment test Fast food RestaurantCZ-6 high Process load | 2678.0432 |  | 108.1705 |  | 0.80298 |  | 449.3712 |  | 19.8781 |  | 50.0952 |  | 20.7081 |  | 256.5361 |  | 0 |  | 41.0866 |  | 0 |  | 25.0514 |  | 36.0194 |  | -3.396% |  | -2.925% |  | FAIL | 94.17

## HVAC Results (hidden)
| TEST RESULTS |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  |  |  | 8 |  | 9 | [7 empty] | 10 |  | 11 |  | 12 |  | 13 |  |  | 14
| Test Case |  | Annual TDV |  | Annual Total End Use Site Energy |  | Annual End Use TDV Energy | [25 empty] | Variation from Baseline |  |  |  |  | Reference Model Occupied Unmet Load Hrs | Applicant Model Occupied Unmet Load Hrs | Area/CoolingCapcity (ft2/Ton) | Area/HeatingCapacity (ft2/kBtu/hr) | Source Energy-Electricity/Area (kBtu/ft2) | Source Energy-Gas/Area (kBtu/ft2)
|  |  | TDV (kBtu/sq.ft) |  | Total End Use (kBtu/sq.ft) |  | Heating (kBtu/sq.ft) |  | Cooling (kBtu/sq.ft) |  | Interior Lighting (kBtu/sq.ft) |  | Interior Equipment (kBtu/sq.ft) |  | Exterior Lighting (kBtu/sq.ft) |  | Exterior Equipment (kBtu/sq.ft) |  | Fans (kBtu/sq.ft) |  | Pumps (kBtu/sq.ft) |  | Heat Rejection (kBtu/sq.ft) |  | Humidification (kBtu/sq.ft) |  | Heat Recovery (kBtu/sq.ft) |  | Refrigeration (kBtu/sq.ft) |  | Water Heating (kBtu/sq.ft) |  | TDV % variation |  | Total End Use Site Energy % Variation
|  |  | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Pass/Fail
3 |  | PTAC Stripmall CZ-6 Baseline | 228.4444 |  | 31.0667 |  | 0.2341 |  | 65.1568 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 4.3674 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 1 | 0 | 396.6151 | 49.9263 | 228.4354 | 0
4 | 79 | PTAC Test Stripmall CZ-6 Low Eff | 316.4 |  | 44.1778 |  | 3.8605 |  | 80.4185 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 73.4601 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 38.5% |  | 42.2% |  |  | 35 | 0 | 396.6151 | 45.5672 | 316.4166 | 0
5 | 80 | PTAC Test Stripmall CZ-6 High Eff | 216.8444 |  | 29.7778 |  | 0.22525 |  | 55.3438 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 2.607 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -5.078% |  | -4.149% |  |  | 1 | 0 | 396.6151 | 55.2076 | 216.8532 | 0
3 |  | PTAC Stripmall CZ-15 Baseline | 280 |  | 36.5333 |  | 0.10694 |  | 113.0794 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 6.686 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 34 | 387.3439 | 50.1489 | 280.0177 | 0
4 | 81 | PTAC Test Stripmall CZ-15 Low Eff | 404.1778 |  | 54.0889 |  | 2.1304 |  | 166.7004 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 75.2183 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 44.35% |  | 48.05% |  |  | 19 | 155 | 387.3439 | 45.8085 | 404.1943 | 0
5 | 82 | PTAC Test Stripmall CZ-15 High Eff | 257.6 |  | 34.1333 |  | 0.10315 |  | 93.4293 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 3.9051 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -8% |  | -6.569% |  |  | 0 | 28 | 387.3439 | 55.3979 | 257.5824 | 0
3 |  | PTAC Stripmall CZ-16 Baseline | 225.4667 |  | 30.4889 |  | 3.7241 |  | 57.8296 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 4.2314 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 45 | 1 | 320.3664 | 54.149 | 225.4474 | 0
4 | 83 | PTAC Test Stripmall CZ-16 Low Eff | 343.9111 |  | 49.2889 |  | 28.2679 |  | 65.0486 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 90.944 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 52.53% |  | 61.66% |  |  | 85 | 2 | 320.3664 | 49.8745 | 343.9232 | 0
5 | 84 | PTAC Test Stripmall CZ-16 High Eff | 215.7333 |  | 29.4222 |  | 3.4912 |  | 50.0177 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 2.5578 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -4.317% |  | -3.499% |  |  | 48 | 1 | 320.3664 | 59.2248 | 215.7294 | 0
3 |  | PTHP Stripmall CZ-6 Baseline | 228.3111 |  | 31.0667 |  | 0.10231 |  | 65.1594 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 4.3657 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 0 | 396.6151 | 19.8859 | 228.3049 | 0
4 | 85 | PTHP Test Stripmall CZ-6 Low Eff | 314.3111 |  | 43.7778 |  | 1.7742 |  | 80.4215 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 73.4601 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 37.67% |  | 40.92% |  |  | 2 | 0 | 396.6151 | 19.156 | 314.3333 | 0
5 | 86 | PTHP Test Stripmall CZ-6 High Eff | 216.7111 |  | 29.7333 |  | 0.083786 |  | 55.3463 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 2.6058 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -5.081% |  | -4.292% |  |  | 0 | 0 | 396.6151 | 20.6736 | 216.713 | 0
|  | PTHP Stripmall CZ-15 Baseline | 279.9556 |  | 36.5333 |  | 0.047577 |  | 113.082 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 6.6856 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 34 | 387.3439 | 19.6378 | 279.9596 | 0
| 87 | PTHP Test Stripmall CZ-15 Low Eff | 403.0222 |  | 53.9111 |  | 0.9768 |  | 166.7016 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 75.2183 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 43.96% |  | 47.57% |  |  | 1 | 155 | 387.3439 | 18.9353 | 403.042 | 0
| 88 | PTHP Test Stripmall CZ-15 High Eff | 257.5111 |  | 34.1333 |  | 0.038735 |  | 93.4314 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 3.9047 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -8.017% |  | -6.569% |  |  | 0 | 28 | 387.3439 | 20.3945 | 257.5197 | 0
|  | PTHP Stripmall CZ-16 Baseline | 223.9556 |  | 30.1778 |  | 2.2109 |  | 57.8607 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 4.2175 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 10 | 1 | 320.3664 | 17.8807 | 223.9518 | 0
| 89 | PTHP Test Stripmall CZ-16 Low Eff | 330.4889 |  | 46.7556 |  | 14.8331 |  | 65.0507 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 90.944 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 47.57% |  | 54.93% |  |  | 27 | 2 | 320.3664 | 17.3886 | 330.4905 | 0
| 90 | PTHP Test Stripmall CZ-16 High Eff | 214.0889 |  | 29.1556 |  | 1.8399 |  | 50.0434 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 2.5447 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -4.406% |  | -3.387% |  |  | 10 | 1 | 320.3664 | 18.4015 | 214.0908 | 0
|  | PSZ Stripmall CZ-6 Baseline | 286.5778 |  | 40.7111 |  | 1.794 |  | 63.7569 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 59.2741 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0693 | [6 empty] | 31 | 9 | 461.1302 | 35.4294 | 281.7081 | 4.8638
| 91 | PSZ Test Stripmall CZ-6 Low Eff | 401.4222 |  | 56.5333 |  | 2.7317 |  | 119.4358 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 117.4961 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0988 |  | 40.07% |  | 38.86% |  |  | 36 | 19 | 372.1276 | 30.7175 | 395.609 | 5.8305
| 92 | PSZ Test Stripmall CZ-6 High Eff | 238.0889 |  | 34.0889 |  | 0.86649 |  | 38.3672 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 37.1403 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0475 |  | -16.92% |  | -16.27% |  |  | 2 | 10 | 570.0161 | 39.1198 | 234.1847 | 3.9144
|  | PSZ Stripmall CZ-15 Baseline | 360.5333 |  | 49.4222 |  | 1.1663 |  | 135.0747 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 61.1789 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 2.9822 | [6 empty] | 19 | 1155 | 450.8372 | 35.6132 | 356.3985 | 4.1485
| 93 | PSZ Test Stripmall CZ-15 Low Eff | 505.7778 |  | 68.6222 |  | 1.7646 |  | 220.0354 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 120.8307 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0243 |  | 40.29% |  | 38.85% |  |  | 21 | 1046 | 363.1311 | 30.8605 | 501.0105 | 4.7889
| 94 | PSZ Test Stripmall CZ-15 High Eff | 294.4889 |  | 40.8 |  | 0.54735 |  | 92.4311 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 38.4055 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 2.9418 |  | -18.32% |  | -17.45% |  |  | 2 | 1304 | 559.1744 | 39.3341 | 290.9818 | 3.4891
|  | PSZ Stripmall CZ-16 Baseline | 314.2667 |  | 54.1778 |  | 24.9594 |  | 52.5165 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 73.9704 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.1674 | [6 empty] | 76 | 3 | 376.3795 | 40.2861 | 286.1492 | 28.1272
| 95 | PSZ Test Stripmall CZ-16 Low Eff | 431.2444 |  | 70.8444 |  | 28.2809 |  | 93.3771 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 146.758 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.1616 |  | 37.22% |  | 30.76% |  |  | 88 | 18 | 302.176 | 36.1837 | 399.7979 | 31.4429
| 96 | PSZ Test Stripmall CZ-16 High Eff | 262.4444 |  | 44.8 |  | 18.4443 |  | 34.159 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 47.0191 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.1733 |  | -16.49% |  | -17.31% |  |  | 50 | 0 | 461.9885 | 45.09 | 240.8408 | 21.6176
|  | PVAV MediumOffice CZ-6 Baseline (No DataCenter) | 237.8422 |  | 38.2077 |  | 3.775 |  | 37.664 |  | 57.3965 |  | 104.6103 |  | 8.0991 |  | 0 |  | 20.2365 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 | [6 empty] | 120 | 186 | 473.9563 | 13.6307 | 231.7812 | 6.0597
| 97 | PVAV Test MediumOffice CZ-6 Low Eff | 382.3562 |  | 61.5537 |  | 57.6239 |  | 83.5766 |  | 57.3965 |  | 104.6103 |  | 8.0991 |  | 0 |  | 64.9814 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0596 |  | 60.76% |  | 61.1% |  |  | 41 | 6 | 465.2846 | 13.5888 | 376.2879 | 6.0596
| 98 | PVAV Test MediumOffice CZ-6 High Eff | 219.102 |  | 35.4852 |  | 2.0449 |  | 29.7608 |  | 57.3965 |  | 104.6103 |  | 8.0991 |  | 0 |  | 11.1394 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 |  | -7.879% |  | -7.125% |  |  | 192 | 267 | 480.6215 | 13.6307 | 213.0509 | 6.0597
|  | PVAV MediumOffice CZ-15 Baseline (No DataCenter) | 278.4926 |  | 43.5593 |  | 1.6522 |  | 83.5021 |  | 55.544 |  | 102.236 |  | 8.2157 |  | 0 |  | 21.2755 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 | [6 empty] | 90 | 358 | 427.696 | 14.4471 | 272.4253 | 6.0597
| 99 | PVAV Test MediumOffice CZ-15 Low Eff | 412.2287 |  | 63.1573 |  | 31.3298 |  | 144.5665 |  | 55.544 |  | 102.236 |  | 8.2157 |  | 0 |  | 64.2771 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 |  | 48.02% |  | 44.99% |  |  | 42 | 179 | 411.1942 | 14.4259 | 406.169 | 6.0597
| 100 | PVAV Test MediumOffice CZ-15 High Eff | 252.6852 |  | 40.3707 |  | 0.7315 |  | 67.5048 |  | 55.544 |  | 102.236 |  | 8.2157 |  | 0 |  | 12.4018 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0596 |  | -9.267% |  | -7.32% |  |  | 129 | 496 | 446.0173 | 14.4471 | 246.6336 | 6.0596
|  | PVAV MediumOffice CZ-16 Baseline (No DataCenter) | 248.6947 |  | 41.6387 |  | 23.5537 |  | 26.2752 |  | 56.24 |  | 102.9484 |  | 7.905 |  | 0 |  | 25.7041 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 | [6 empty] | 483 | 784 | 438.5266 | 14.7122 | 242.0803 | 6.6056
| 101 | PVAV Test MediumOffice CZ-16 Low Eff | 361.6394 |  | 60.006 |  | 63.9272 |  | 52.0388 |  | 56.24 |  | 102.9484 |  | 7.905 |  | 0 |  | 72.5156 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 |  | 45.42% |  | 44.11% |  |  | 319 | 41 | 438.5266 | 14.3014 | 355.5667 | 6.0677
| 102 | PVAV Test MediumOffice CZ-16 High Eff | 224.7893 |  | 37.5177 |  | 14.662 |  | 22.0761 |  | 56.24 |  | 102.9484 |  | 7.905 |  | 0 |  | 14.8989 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 |  | -9.612% |  | -9.897% |  |  | 806 | 905 | 438.5266 | 14.9555 | 218.7303 | 6.0597
|  | VAV LargeOffice CZ-6 Baseline | 221.4494 |  | 34.2327 |  | 2.8214 |  | 36.8729 |  | 55.9814 |  | 63.9083 |  | 5.8817 |  | 23.1495 |  | 13.4951 |  | 14.1879 |  | 4.036 |  | 0 |  | 0 |  | 0 |  | 1.1146 | [6 empty] | 0 | 195 | 620.2401 | 28.6892 | 217.5129 | 3.9361
| 103 | VAV Test LargeOffice CZ-6 Low Eff | 279.2285 |  | 45.679 |  | 9.534 |  | 53.9787 |  | 55.9814 |  | 63.9083 |  | 5.8817 |  | 23.1495 |  | 44.1035 |  | 16.4726 |  | 5.1051 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | 26.09% |  | 33.44% |  |  | 0 | 71 | 620.2401 | 28.6892 | 268.5808 | 10.6486
| 104 | VAV Test LargeOffice CZ-6 Low Eff | 212.3457 |  | 32.0625 |  | 0.86415 |  | 32.8345 |  | 55.9814 |  | 63.9083 |  | 5.8817 |  | 23.1495 |  | 10.5281 |  | 14.2966 |  | 3.7859 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | -4.111% |  | -6.339% |  |  | 2 | 310 | 620.2401 | 28.6892 | 210.366 | 1.9788
|  | VAV LargeOffice CZ-15 Baseline | 253.905 |  | 38.2661 |  | 1.1512 |  | 60.2573 |  | 54.175 |  | 62.7314 |  | 5.9708 |  | 23.4992 |  | 16.9821 |  | 19.1593 |  | 8.8637 |  | 0 |  | 0 |  | 0 |  | 1.1146 | [6 empty] | 0 | 324 | 567.2307 | 30.0576 | 251.6388 | 2.2658
| 105 | VAV Test LargeOffice CZ-15 Low Eff | 307.5325 |  | 47.1792 |  | 4.3985 |  | 76.1737 |  | 54.175 |  | 62.7314 |  | 5.9708 |  | 23.4992 |  | 49.6021 |  | 20.6993 |  | 9.168 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | 21.12% |  | 23.29% |  |  | 0 | 203 | 567.2307 | 30.0576 | 302.0194 | 5.5131
| 106 | VAV Test LargeOffice CZ-15 Low Eff | 243.5077 |  | 36.7016 |  | 0.42424 |  | 53.9208 |  | 54.175 |  | 62.7314 |  | 5.9708 |  | 23.4992 |  | 13.5943 |  | 19.4116 |  | 8.6655 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | -4.095% |  | -4.088% |  |  | 0 | 458 | 567.2307 | 30.0576 | 241.9686 | 1.5388
|  | VAV LargeOffice CZ-16 Baseline | 210.5887 |  | 38.6211 |  | 16.7317 |  | 20.6354 |  | 54.8529 |  | 63.0282 |  | 5.7388 |  | 23.4067 |  | 16.4024 |  | 7.9443 |  | 0.73476 |  | 0 |  | 0 |  | 0 |  | 1.1146 | [6 empty] | 28 | 572 | 571.6977 | 28.7398 | 192.7434 | 17.8463
| 107 | VAV Test LargeOffice CZ-16 Low Eff | 264.9282 |  | 47.2996 |  | 17.0744 |  | 33.9963 |  | 54.8529 |  | 63.0282 |  | 5.7388 |  | 23.4067 |  | 52.3573 |  | 12.3519 |  | 1.0062 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | 25.8% |  | 22.47% |  |  | 24 | 409 | 571.6977 | 28.7398 | 246.7383 | 18.189
| 108 | VAV Test LargeOffice CZ-16 Low Eff | 197.3573 |  | 34.1926 |  | 10.3486 |  | 17.8544 |  | 54.8529 |  | 63.0282 |  | 5.7388 |  | 23.4067 |  | 12.3661 |  | 7.9798 |  | 0.66729 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | -6.283% |  | -11.47% |  |  | 98 | 646 | 571.6977 | 28.7398 | 185.8939 | 11.4632
|  | FanCoil Stripmall CZ-6 Baseline | 335.9111 |  | 46.7556 |  | 0.092628 |  | 149.0426 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 2.0239 |  | 25.2671 |  | 0.81176 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 0 | 311.9674 | 43.9524 | 335.8225 | 0.092628
| 109 | FanCoil Test Stripmall CZ-6 Low Eff | 338.7111 |  | 47.0222 |  | 0.091786 |  | 150.8248 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 2.962 |  | 25.356 |  | 0.79912 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0.8336% |  | 0.5703% |  |  | 0 | 0 | 311.9674 | 43.9524 | 338.6186 | 0.091786
| 110 | FanCoil Test Stripmall CZ-6 High Eff | 335.5111 |  | 46.7111 |  | 0.092628 |  | 148.9676 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 1.6858 |  | 25.2671 |  | 0.81091 |  | 0 |  | 0 |  | 0 |  | 0 |  | -0.1191% |  | -0.09506% |  |  | 0 | 0 | 311.9674 | 43.9524 | 335.409 | 0.092628
|  | FanCoil Stripmall CZ-15 Baseline | 369.2444 |  | 50.5778 |  | 0.04084 |  | 178.2826 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 2.5094 |  | 26.2136 |  | 2.0391 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 25 | 306.7131 | 44.135 | 369.1895 | 0.04084
| 111 | FanCoil Test Stripmall CZ-15 Low Eff | 372.6222 |  | 51.1111 |  | 0.04084 |  | 179.795 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 4.1426 |  | 26.4477 |  | 2.0424 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0.9148% |  | 1.054% |  |  | 0 | 25 | 306.7131 | 44.135 | 372.5725 | 0.04084
| 112 | FanCoil Test Stripmall CZ-15 High Eff | 368.7111 |  | 50.5333 |  | 0.04084 |  | 178.1799 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 2.0904 |  | 26.2136 |  | 2.0361 |  | 0 |  | 0 |  | 0 |  | 0 |  | -0.1444% |  | -0.08787% |  |  | 0 | 25 | 306.7131 | 44.135 | 368.6649 | 0.04084
|  | FanCoil Stripmall CZ-16 Baseline | 325.3333 |  | 45.3333 |  | 1.525 |  | 137.4464 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 2.1165 |  | 24.1173 |  | 0.48082 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 46 | 2 | 264.8185 | 47.5087 | 323.8234 | 1.525
| 113 | FanCoil Test Stripmall CZ-16 Low Eff | 326.5778 |  | 45.3778 |  | 1.4715 |  | 137.7289 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 3.1131 |  | 24.1497 |  | 0.46651 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0.3825% |  | 0.09804% |  |  | 36 | 1 | 264.8185 | 47.5087 | 325.1206 | 1.4715
| 114 | FanCoil Test Stripmall CZ-16 High Eff | 324.9333 |  | 45.2889 |  | 1.5296 |  | 137.3795 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 1.7633 |  | 24.1173 |  | 0.4804 |  | 0 |  | 0 |  | 0 |  | 0 |  | -0.123% |  | -0.09804% |  |  | 46 | 2 | 264.8185 | 47.5087 | 323.4032 | 1.5296
|  | PSZ Stripmall CZ-6 Baseline | 286.5778 |  | 40.7111 |  | 1.794 |  | 63.7569 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 59.2741 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0693 | [6 empty] | 31 | 9 | 461.1302 | 35.4294 | 281.7081 | 4.8638
| 115 | VRF Test Stripmall CZ-6 Low Eff | 250.8889 |  | 34.9778 |  | 1.9599 |  | 65.7577 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 24.4865 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -12.45% |  | -14.08% |  |  | 33 | 0 | 396.6151 | 33.0499 | 250.8816 | 0
| 116 | VRF Test Stripmall CZ-6 High Eff | 234.8444 |  | 33.0667 |  | 1.5427 |  | 50.1457 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 24.4865 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -18.05% |  | -18.78% |  |  | 33 | 0 | 396.6151 | 33.0499 | 234.852 | 0
|  | PSZ Stripmall CZ-15 Baseline | 360.5333 |  | 49.4222 |  | 1.1663 |  | 135.0747 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 61.1789 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 2.9822 | [6 empty] | 19 | 1155 | 450.8372 | 35.6132 | 356.3985 | 4.1485
| 117 | VRF Test Stripmall CZ-15 Low Eff | 320.2222 |  | 43.1556 |  | 1.1646 |  | 133.8558 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 25.0726 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -11.18% |  | -12.68% |  |  | 15 | 134 | 387.3439 | 32.2773 | 320.2383 | 0
| 118 | VRF Test Stripmall CZ-15 High Eff | 287.8222 |  | 39.2889 |  | 0.91659 |  | 101.6694 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 25.0726 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -20.17% |  | -20.5% |  |  | 15 | 134 | 387.3439 | 32.2773 | 287.8039 | 0
|  | PSZ Stripmall CZ-16 Baseline | 314.2667 |  | 54.1778 |  | 24.9594 |  | 52.5165 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 73.9704 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.1674 | [6 empty] | 76 | 3 | 376.3795 | 40.2861 | 286.1492 | 28.1272
| 119 | VRF Test Stripmall CZ-16 Low Eff | 265.7333 |  | 37.2 |  | 14.9509 |  | 60.7899 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 30.3145 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -15.44% |  | -31.34% |  |  | 52 | 1 | 320.3664 | 26.6961 | 265.7181 | 0
| 120 | VRF Test Stripmall CZ-16 High Eff | 247.8222 |  | 35.0222 |  | 11.5393 |  | 46.3054 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 30.3145 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -21.14% |  | -35.36% |  |  | 52 | 1 | 320.3664 | 26.6961 | 247.822 | 0

## Summary(Reference) (hidden)
[17 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | [5 empty] | 16
|  |  | Annual Energy by End-Use [kBtu] | TDV | Total | Heating | Cooling | Interior Lighting | Interior Equipment | Exterior Lighting | Fans | Pumps | Refrigeration | Water Heating | Total Electric Use [kWh] | Total Gas Use [therms] | Total TDV EUI [kBtu/sf] | TDV EUI Electricity [kwh/sf] | TDV EUI Natural Gas[therm/sf] | Total EUI [kBtu/sf] | Heating EUI [kBtu/sf] | Cooling EUI [kBtu/sf] | Interior Lighting EUI [kBtu/sf] | Interior Equipment EUI [kBtu/sf] | Exterior Lighting EUI [kBtu/sf] | Fans EUI [kBtu/sf] | Pumps EUI [kBtu/sf] | Refrigeration EUI [kBtu/sf] | Water Heating EUI [kBtu/sf] | TDV Variation | Site Energy TDV EUI variation | Total Area [sf] | Gross Wall Area [sf] | Window Opening Area [sf] | Unmet Load Hrs - Occupied Heating | Unmet Load Hrs - Occupied Cooling | Total UMNL
3 |  | Medium Office CZ-15 Baseline | 0001 CZ15 MediumOffice Base | 15796829.7417 | 2720111.5391 | 18880.5144 | 802014.3007 | 271284.1783 | 694560.2887 | 0 | 115207.1549 | 6871.6732 | 0 | 811293.429 | 553886.1111 | 8303.829 | 294.5639 | 10.3283 | 0.15484 | 50.722 | 0.35207 | 14.9552 | 5.0586 | 12.9515 | 0 | 2.1483 | 0.12814 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 80.25 | 597 | 677.25
4 | 1 | Envelope Test Medium OfficeCZ-15 Roof Insulation | 0002 CZ15 MediumOffice RoofLtR+20 | 15752794.1645 | 2714604.7224 | 18207.5643 | 797426.8664 | 271284.1783 | 694560.2887 | 0 | 115027.0697 | 6814.8041 | 0 | 811293.429 | 552469.4444 | 8297.0978 | 293.7428 | 10.3019 | 0.15472 | 50.6193 | 0.33952 | 14.8696 | 5.0586 | 12.9515 | 0 | 2.1449 | 0.12708 | 0 | 15.1282 | 0.2788% | 0.2024% | 53627.8468 | 21287.4627 | 7027.0036 | 80.5 | 594 | 674.5
5 | 2 | Envelope Test Medium OfficeCZ-15 Wall Insulation | 0003 CZ15 MediumOffice WallLtR+20 | 15737458.4856 | 2713268.3005 | 17951.6538 | 796886.6108 | 271284.1783 | 694560.2887 | 0 | 114600.552 | 6710.5443 | 0 | 811293.429 | 552155.5556 | 8294.4432 | 293.4568 | 10.2961 | 0.15467 | 50.5944 | 0.33475 | 14.8596 | 5.0586 | 12.9515 | 0 | 2.137 | 0.12513 | 0 | 15.1282 | 0.3758% | 0.2516% | 53627.8468 | 21287.4627 | 7027.0036 | 79.75 | 597 | 676.75
6 | 3 | Envelope Test Medium OfficeCZ-15 Floor Slab Insulation | 0004 CZ15 MediumOffice UnhtSlabF24vR-5 | 15849566.2789 | 2725921.6572 | 18179.1298 | 807805.4625 | 271284.1783 | 694560.2887 | 0 | 116230.7972 | 6577.8499 | 0 | 811293.429 | 555797.2222 | 8296.7186 | 295.5473 | 10.364 | 0.15471 | 50.8303 | 0.33899 | 15.0632 | 5.0586 | 12.9515 | 0 | 2.1674 | 0.12266 | 0 | 15.1282 | -0.3338% | -0.2136% | 53627.8468 | 21287.4627 | 7027.0036 | 73.75 | 599.75 | 673.5
7 | 4 | Envelope Test Medium OfficeCZ-15 Infiltration | 0005 CZ15 MediumOffice BaseInfil+5 | 15823321.2266 | 2723021.3373 | 19667.2025 | 803815.1529 | 271284.1783 | 694560.2887 | 0 | 115358.8056 | 7042.2802 | 0 | 811293.429 | 554508.3333 | 8311.6979 | 295.0579 | 10.3399 | 0.15499 | 50.7763 | 0.36673 | 14.9888 | 5.0586 | 12.9515 | 0 | 2.1511 | 0.13132 | 0 | 15.1282 | -0.1677% | -0.107% | 53627.8468 | 21287.4627 | 7027.0036 | 82.25 | 593.75 | 676
8 |  | Medium Office CZ-16 Baseline | 0013 CZ16 MediumOffice Base | 11132717.1259 | 2521894.5724 | 456705.6156 | 177346.0366 | 271454.7853 | 694560.2887 | 0 | 79161.6748 | 31382.2205 | 0 | 811293.429 | 367480.5556 | 12683.182 | 207.5921 | 6.8524 | 0.2365 | 47.0258 | 8.5162 | 3.307 | 5.0618 | 12.9515 | 0 | 1.4761 | 0.58519 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 747.75 | 74.75 | 822.5
9 | 5 | Envelope Test Medium OfficeCZ-16 Roof Insulation | 0014 CZ16 MediumOffice RoofLtR+20 | 11100860.997 | 2511269.544 | 447530.7472 | 176398.2196 | 271454.7853 | 694560.2887 | 0 | 78981.5896 | 31059.9627 | 0 | 811293.429 | 367055.5556 | 12591.4102 | 206.9981 | 6.8445 | 0.23479 | 46.8277 | 8.3451 | 3.2893 | 5.0618 | 12.9515 | 0 | 1.4728 | 0.57918 | 0 | 15.1282 | 0.2861% | 0.4213% | 53627.8468 | 21287.4627 | 7027.0036 | 748 | 74.25 | 822.25
10 | 6 | Envelope Test Medium OfficeCZ-16 Wall Insulation | 0015 CZ16 MediumOffice WallLtR+20 | 11098861.1031 | 2508255.486 | 444184.9532 | 176834.2154 | 271454.7853 | 694560.2887 | 0 | 79019.5023 | 30908.312 | 0 | 811293.429 | 367152.7778 | 12557.9439 | 206.9608 | 6.8463 | 0.23417 | 46.7715 | 8.2827 | 3.2974 | 5.0618 | 12.9515 | 0 | 1.4735 | 0.57635 | 0 | 15.1282 | 0.3041% | 0.5408% | 53627.8468 | 21287.4627 | 7027.0036 | 747.25 | 73.75 | 821
11 | 7 | Envelope Test Medium OfficeCZ-16 Floor Slab Insulation | 0016 CZ16 MediumOffice UnhtSlabF24vR-5 | 11140991.5682 | 2519335.4666 | 452791.1315 | 178606.6332 | 271454.7853 | 694560.2887 | 0 | 79758.7995 | 30879.8775 | 0 | 811293.429 | 367877.7778 | 12644.0273 | 207.7464 | 6.8598 | 0.23577 | 46.9781 | 8.4432 | 3.3305 | 5.0618 | 12.9515 | 0 | 1.4873 | 0.57582 | 0 | 15.1282 | -0.07433% | 0.1015% | 53627.8468 | 21287.4627 | 7027.0036 | 741.5 | 75.25 | 816.75
12 | 8 | Envelope Test Medium OfficeCZ-16 Infiltration | 0017 CZ16 MediumOffice BaseInfil+5 | 11161985.7145 | 2536509.9104 | 470543.7436 | 177251.2549 | 271454.7853 | 694560.2887 | 0 | 79218.5438 | 32197.3431 | 0 | 811293.429 | 367708.3333 | 12821.5981 | 208.1379 | 6.8567 | 0.23908 | 47.2984 | 8.7742 | 3.3052 | 5.0618 | 12.9515 | 0 | 1.4772 | 0.60038 | 0 | 15.1282 | -0.2629% | -0.5795% | 53627.8468 | 21287.4627 | 7027.0036 | 743.75 | 73.25 | 817
13 |  | Medium Office CZ-6 Baseline | 0025 CZ06 MediumOffice Base | 11225233.5421 | 2220792.0717 | 36187.6526 | 329669.7047 | 271454.7853 | 694560.2887 | 0 | 67209.7026 | 10425.9869 | 0 | 811293.429 | 402477.7778 | 8476.9439 | 209.3173 | 7.505 | 0.15807 | 41.4112 | 0.67479 | 6.1474 | 5.0618 | 12.9515 | 0 | 1.2533 | 0.19441 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 181.25 | 64.5 | 245.75
14 | 9 | Envelope Test Medium OfficeCZ-6 Roof Insulation | 0026 CZ06 MediumOffice RoofLtR+20 | 11198941.0989 | 2216602.7206 | 33941.3263 | 327925.7215 | 271454.7853 | 694560.2887 | 0 | 67152.8336 | 10283.8143 | 0 | 811293.429 | 401911.1111 | 8454.3802 | 208.827 | 7.4944 | 0.15765 | 41.3331 | 0.6329 | 6.1148 | 5.0618 | 12.9515 | 0 | 1.2522 | 0.19176 | 0 | 15.1282 | 0.2342% | 0.1886% | 53627.8468 | 21287.4627 | 7027.0036 | 181.5 | 65.25 | 246.75
15 | 10 | Envelope Test Medium OfficeCZ-6 Wall Insulation | 0027 CZ06 MediumOffice WallLtR+20 | 11210779.333 | 2217692.7101 | 33742.2848 | 329252.6653 | 271454.7853 | 694560.2887 | 0 | 67313.9625 | 10075.2946 | 0 | 811293.429 | 402286.1111 | 8452.4841 | 209.0477 | 7.5014 | 0.15761 | 41.3534 | 0.62919 | 6.1396 | 5.0618 | 12.9515 | 0 | 1.2552 | 0.18787 | 0 | 15.1282 | 0.1288% | 0.1396% | 53627.8468 | 21287.4627 | 7027.0036 | 180.5 | 66 | 246.5
16 | 11 | Envelope Test Medium OfficeCZ-6 Floor Slab Insulation | 0028 CZ06 MediumOffice UnhtSlabF24vR-5 | 11245431.5221 | 2222100.0591 | 35372.53 | 331887.5965 | 271454.7853 | 694560.2887 | 0 | 67731.002 | 9819.384 | 0 | 811293.429 | 403102.7778 | 8468.6959 | 209.6939 | 7.5167 | 0.15792 | 41.4356 | 0.65959 | 6.1887 | 5.0618 | 12.9515 | 0 | 1.263 | 0.1831 | 0 | 15.1282 | -0.1799% | -0.0589% | 53627.8468 | 21287.4627 | 7027.0036 | 166.75 | 64.5 | 231.25
17 | 12 | Envelope Test Medium OfficeCZ-6 Infiltration | 0029 CZ06 MediumOffice BaseInfil+5 | 11225299.8893 | 2221692.4978 | 37476.6837 | 329186.3181 | 271454.7853 | 694560.2887 | 0 | 67067.5301 | 10653.4629 | 0 | 811293.429 | 402363.8889 | 8489.8375 | 209.3185 | 7.5029 | 0.15831 | 41.428 | 0.69883 | 6.1383 | 5.0618 | 12.9515 | 0 | 1.2506 | 0.19866 | 0 | 15.1282 | -0.0005911% | -0.04055% | 53627.8468 | 21287.4627 | 7027.0036 | 185.75 | 65 | 250.75
18 |  | Small Office CZ-15 SolarReflectance-Low Slope Baseline | 0037 CZ15 SmallOffice BaseLslope | 1237830.0299 | 185639.4353 | 4549.5215 | 48973.7038 | 33808.632 | 71256.8812 | 0 | 10710.332 | 0 | 0 | 16340.3649 | 48283.3333 | 208.9514 | 224.9749 | 8.7755 | 0.037977 | 33.7399 | 0.82687 | 8.9009 | 6.1447 | 12.9509 | 0 | 1.9466 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 25.33 | 121 | 146.33
19 | 13 | Envelope Test Small OfficeCZ-15 SolarReflectance-Low Slope | 0038 CZ15 SmallOffice SRefLSlope+20 | 1229233.3298 | 184672.6619 | 4615.8687 | 48149.103 | 33808.632 | 71256.8812 | 0 | 10511.2904 | 0 | 0 | 16340.3649 | 47980.5556 | 209.6151 | 223.4125 | 8.7204 | 0.038097 | 33.5642 | 0.83893 | 8.7511 | 6.1447 | 12.9509 | 0 | 1.9104 | 0 | 0 | 2.9699 | 0.6945% | 0.5208% | 5502.0804 | 3030.1484 | 642.3902 | 26 | 121.33 | 147.33
20 |  | Small Office CZ-16 SolarReflectance-Low Slope Baseline | 0045 CZ16 SmallOffice BaseLslope | 1253535.3574 | 187525.5911 | 4739.0849 | 50319.6039 | 33808.632 | 71256.8812 | 0 | 11051.5461 | 0 | 0 | 16340.3649 | 48780.5556 | 210.8476 | 227.8293 | 8.8658 | 0.038321 | 34.0827 | 0.86133 | 9.1456 | 6.1447 | 12.9509 | 0 | 2.0086 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 26 | 126.67 | 152.67
21 | 14 | Envelope Test Small OfficeCZ-16 SolarReflectance-Low Slope | 0046 CZ16 SmallOffice SRefLSlope+20 | 1241014.695 | 186122.8219 | 4843.3448 | 49115.8763 | 33808.632 | 71256.8812 | 0 | 10748.2446 | 0 | 0 | 16340.3649 | 48338.8889 | 211.8904 | 225.5537 | 8.7856 | 0.038511 | 33.8277 | 0.88028 | 8.9268 | 6.1447 | 12.9509 | 0 | 1.9535 | 0 | 0 | 2.9699 | 0.9988% | 0.748% | 5502.0804 | 3030.1484 | 642.3902 | 26.5 | 120.33 | 146.83
22 |  | Small Office CZ-6 SolarReflectance-Low Slope Baseline | 0041 CZ06 SmallOffice BaseLslope | 1018599.9606 | 166010.1454 | 11951.9722 | 24946.5431 | 33846.5446 | 71256.8812 | 0 | 7667.8394 | 0 | 0 | 16340.3649 | 40361.1111 | 282.9946 | 185.13 | 7.3356 | 0.051434 | 30.1722 | 2.1723 | 4.534 | 6.1516 | 12.9509 | 0 | 1.3936 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 52.33 | 26.5 | 78.83
23 | 15 | Envelope Test Small OfficeCZ-6 SolarReflectance-Low Slope | 0042 CZ06 SmallOffice SRefLSlope+20 | 1008117.1047 | 165043.3721 | 12226.8391 | 23989.248 | 33846.5446 | 71256.8812 | 0 | 7383.4943 | 0 | 0 | 16340.3649 | 39994.4444 | 285.8387 | 183.2247 | 7.269 | 0.051951 | 29.9965 | 2.2222 | 4.36 | 6.1516 | 12.9509 | 0 | 1.3419 | 0 | 0 | 2.9699 | 1.029% | 0.5824% | 5502.0804 | 3030.1484 | 642.3902 | 54.17 | 26.5 | 80.67
24 |  | Small Office CZ-15 SolarReflectance-Steep Slope Baseline | 0039 CZ15 SmallOffice BaseSslope | 1042883.0318 | 169137.9415 | 12577.5314 | 26794.7862 | 33846.5446 | 71256.8812 | 0 | 8312.355 | 0 | 0 | 16340.3649 | 41091.6667 | 289.3466 | 189.5434 | 7.4684 | 0.052589 | 30.7407 | 2.286 | 4.8699 | 6.1516 | 12.9509 | 0 | 1.5108 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 52.33 | 29.83 | 82.16
25 | 16 | Envelope Test Small OfficeCZ-15 SolarReflectance-Steep Slope | 0040 CZ15 SmallOffice SRefSSlope+20 | 1027111.3571 | 167640.3907 | 12994.5709 | 25344.6263 | 33846.5446 | 71256.8812 | 0 | 7866.881 | 0 | 0 | 16340.3649 | 40533.3333 | 293.4232 | 186.6769 | 7.3669 | 0.053329 | 30.4685 | 2.3618 | 4.6064 | 6.1516 | 12.9509 | 0 | 1.4298 | 0 | 0 | 2.9699 | 1.512% | 0.8854% | 5502.0804 | 3030.1484 | 642.3902 | 54.67 | 27.5 | 82.17
26 |  | Small Office CZ-16 SolarReflectance-Steep Slope Baseline | 0043 CZ06 SmallOffice BaseSslope | 999444.5792 | 187847.8488 | 42367.4194 | 16728.9698 | 33780.1974 | 71256.8812 | 0 | 7364.538 | 0 | 0 | 16340.3649 | 37847.2222 | 587.2256 | 181.6485 | 6.8787 | 0.10673 | 34.1412 | 7.7003 | 3.0405 | 6.1395 | 12.9509 | 0 | 1.3385 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 140.83 | 22.33 | 163.16
27 | 17 | Envelope Test Small OfficeCZ-16 SolarReflectance-Steep Slope | 0044 CZ06 SmallOffice SRefSSlope+20 | 994809.7542 | 187790.9798 | 42955.0659 | 16245.5832 | 33780.1974 | 71256.8812 | 0 | 7203.4091 | 0 | 0 | 16340.3649 | 37658.3333 | 593.1036 | 180.8061 | 6.8444 | 0.1078 | 34.1309 | 7.8071 | 2.9526 | 6.1395 | 12.9509 | 0 | 1.3092 | 0 | 0 | 2.9699 | 0.4637% | 0.03027% | 5502.0804 | 3030.1484 | 642.3902 | 140.83 | 19.67 | 160.5
28 |  | Small Office CZ-6 SolarReflectance-Steep Slope Baseline | 0047 CZ16 SmallOffice BaseSslope | 1011614.5494 | 189516.0067 | 42793.937 | 17610.4396 | 33780.1974 | 71256.8812 | 0 | 7734.1866 | 0 | 0 | 16340.3649 | 38211.1111 | 591.4919 | 183.8604 | 6.9448 | 0.1075 | 34.4444 | 7.7778 | 3.2007 | 6.1395 | 12.9509 | 0 | 1.4057 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 140.67 | 20.67 | 161.34
29 | 18 | Envelope Test Small OfficeCZ-6 SolarReflectance-Steep Slope | 0048 CZ16 SmallOffice SRefSSlope+20 | 1004714.4417 | 189373.8342 | 43618.5378 | 16890.0987 | 33780.1974 | 71256.8812 | 0 | 7487.7542 | 0 | 0 | 16340.3649 | 37927.7778 | 599.7399 | 182.6063 | 6.8934 | 0.109 | 34.4186 | 7.9276 | 3.0698 | 6.1395 | 12.9509 | 0 | 1.3609 | 0 | 0 | 2.9699 | 0.6821% | 0.07502% | 5502.0804 | 3030.1484 | 642.3902 | 140.33 | 18 | 158.33
30 |  | Envelope Test SmallOfficeCZ-15 Light | 0090 CZ15 SmallOffice BaseLt | 1230692.968 | 184852.7472 | 4710.6504 | 48215.4502 | 33808.632 | 71256.8812 | 0 | 10520.7686 | 0 | 0 | 16340.3649 | 48005.5556 | 210.5631 | 223.6777 | 8.725 | 0.03827 | 33.5969 | 0.85616 | 8.7631 | 6.1447 | 12.9509 | 0 | 1.9121 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 27.17 | 120.83 | 148
31 | 19 | Envelope Test Small OfficeCZ-15 Heavy | 0091 CZ15 SmallOffice Hvy | 1228465.598 | 184606.3147 | 4596.9124 | 48054.3213 | 33808.632 | 71256.8812 | 0 | 10539.7249 | 0 | 0 | 16340.3649 | 47966.6667 | 209.4255 | 223.2729 | 8.7179 | 0.038063 | 33.5521 | 0.83549 | 8.7338 | 6.1447 | 12.9509 | 0 | 1.9156 | 0 | 0 | 2.9699 | 0.181% | 0.08101% | 5502.0804 | 3030.1484 | 642.3902 | 26 | 124.67 | 150.67
32 |  | Envelope Test SmallofficeCZ-16 Light | 0092 CZ16 SmallOffice BaseLt | 997435.2072 | 187933.1524 | 42746.5462 | 16501.4938 | 33780.1974 | 71256.8812 | 0 | 7298.1908 | 0 | 0 | 16340.3649 | 37761.1111 | 591.0178 | 181.2833 | 6.8631 | 0.10742 | 34.1567 | 7.7692 | 2.9991 | 6.1395 | 12.9509 | 0 | 1.3264 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 138.5 | 21.67 | 160.17
33 | 20 | Envelope Test SmallOfficeCZ-16 Heavy | 0093 CZ16 SmallOffice Hvy | 995331.0535 | 187421.3312 | 42395.8539 | 16406.7121 | 33780.1974 | 71256.8812 | 0 | 7241.3218 | 0 | 0 | 16340.3649 | 37713.8889 | 587.51 | 180.9009 | 6.8545 | 0.10678 | 34.0637 | 7.7054 | 2.9819 | 6.1395 | 12.9509 | 0 | 1.3161 | 0 | 0 | 2.9699 | 0.211% | 0.1251% | 5502.0804 | 3030.1484 | 642.3902 | 139.67 | 19.67 | 159.34
34 |  | Envelope Test SmallOfficeCZ-6 Light | 0094 CZ06 SmallOffice BaseLt | 1014619.1292 | 165915.3637 | 12331.099 | 24576.8945 | 33846.5446 | 71256.8812 | 0 | 7573.0577 | 0 | 0 | 16340.3649 | 40222.2222 | 286.7868 | 184.4065 | 7.3104 | 0.052123 | 30.155 | 2.2412 | 4.4668 | 6.1516 | 12.9509 | 0 | 1.3764 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 53.67 | 26.17 | 79.84
35 | 21 | Envelope Test SmallOfficeCZ-6 Heavy | 0095 CZ06 SmallOffice Hvy | 1011756.7219 | 165242.4137 | 11866.6687 | 24415.7656 | 33846.5446 | 71256.8812 | 0 | 7516.1887 | 0 | 0 | 16340.3649 | 40161.1111 | 282.1413 | 183.8862 | 7.2993 | 0.051279 | 30.0327 | 2.1568 | 4.4376 | 6.1516 | 12.9509 | 0 | 1.3661 | 0 | 0 | 2.9699 | 0.2821% | 0.1519% | 5502.0804 | 3030.1484 | 642.3902 | 53.17 | 26.17 | 79.34
37 |  | Medium Office CZ-15 Baseline | 0001 CZ15 MediumOffice Base | 15796829.7417 | 2720111.5391 | 18880.5144 | 802014.3007 | 271284.1783 | 694560.2887 | 0 | 115207.1549 | 6871.6732 | 0 | 811293.429 | 553886.1111 | 8303.829 | 294.5639 | 10.3283 | 0.15484 | 50.722 | 0.35207 | 14.9552 | 5.0586 | 12.9515 | 0 | 2.1483 | 0.12814 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 80.25 | 597 | 677.25
38 | 22 | Envelope Glazing Test Medium OfficeCZ-15 Window U | 0006 CZ15 MediumOffice WinU-20 | 15689641.1186 | 2707666.7021 | 14871.2485 | 794336.9831 | 271303.1346 | 694560.2887 | 0 | 115264.0239 | 6037.5942 | 0 | 811293.429 | 551413.8889 | 8263.7262 | 292.5652 | 10.2822 | 0.15409 | 50.4899 | 0.2773 | 14.812 | 5.059 | 12.9515 | 0 | 2.1493 | 0.11258 | 0 | 15.1282 | 0.6785% | 0.4575% | 53627.8468 | 21287.4627 | 7027.0036 | 73.75 | 611 | 684.75
39 | 23 | Envelope Glazing Test Medium OfficeCZ-15 Window SHGC | 0007 CZ15 MediumOffice WinSHGC-20 | 15472913.2861 | 2682378.9448 | 21212.1442 | 767959.2363 | 271284.1783 | 694560.2887 | 0 | 109065.3008 | 7004.3675 | 0 | 811293.429 | 542144.4444 | 8327.1512 | 288.5239 | 10.1094 | 0.15528 | 50.0184 | 0.39554 | 14.3202 | 5.0586 | 12.9515 | 0 | 2.0337 | 0.13061 | 0 | 15.1282 | 2.051% | 1.387% | 53627.8468 | 21287.4627 | 7027.0036 | 94.25 | 542 | 636.25
40 | 24 | Envelope Glazing Test Medium OfficeCZ-15 Window U&SHGC | 0008 CZ15 MediumOffice WinU_SHGC-20 | 15360028.2829 | 2668597.6858 | 16349.843 | 759808.0102 | 271303.1346 | 694560.2887 | 0 | 109074.779 | 6217.6794 | 0 | 811293.429 | 539533.3333 | 8278.4211 | 286.4189 | 10.0607 | 0.15437 | 49.7614 | 0.30488 | 14.1682 | 5.059 | 12.9515 | 0 | 2.0339 | 0.11594 | 0 | 15.1282 | 2.765% | 1.894% | 53627.8468 | 21287.4627 | 7027.0036 | 89.25 | 544 | 633.25
41 |  | Medium Office CZ-16 Baseline | 0013 CZ16 MediumOffice Base | 11132717.1259 | 2521894.5724 | 456705.6156 | 177346.0366 | 271454.7853 | 694560.2887 | 0 | 79161.6748 | 31382.2205 | 0 | 811293.429 | 367480.5556 | 12683.182 | 207.5921 | 6.8524 | 0.2365 | 47.0258 | 8.5162 | 3.307 | 5.0618 | 12.9515 | 0 | 1.4761 | 0.58519 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 747.75 | 74.75 | 822.5
42 | 25 | Envelope Glazing Test Medium OfficeCZ-16 Window U | 0018 CZ16 MediumOffice WinU-20 | 11064180.4795 | 2476683.7021 | 409760.2402 | 179421.7558 | 271483.2198 | 694560.2887 | 0 | 80422.2714 | 29751.9753 | 0 | 811293.429 | 367988.8889 | 12213.6101 | 206.3141 | 6.8619 | 0.22775 | 46.1828 | 7.6408 | 3.3457 | 5.0624 | 12.9515 | 0 | 1.4996 | 0.55479 | 0 | 15.1282 | 0.6156% | 1.793% | 53627.8468 | 21287.4627 | 7027.0036 | 724.5 | 88.5 | 813
43 | 26 | Envelope Glazing Test Medium OfficeCZ-16 Window SHGC | 0019 CZ16 MediumOffice WinSHGC-20 | 10984772.3723 | 2512738.6603 | 463691.0268 | 166398.7504 | 271454.7853 | 694560.2887 | 0 | 74128.7666 | 31221.0916 | 0 | 811293.429 | 362750 | 12753.0537 | 204.8334 | 6.7642 | 0.23781 | 46.8551 | 8.6465 | 3.1028 | 5.0618 | 12.9515 | 0 | 1.3823 | 0.58218 | 0 | 15.1282 | 1.329% | 0.3631% | 53627.8468 | 21287.4627 | 7027.0036 | 796.5 | 46 | 842.5
44 | 27 | Envelope Glazing Test Medium OfficeCZ-16 Window U&SHGC | 0020 CZ16 MediumOffice WinU_SHGC-20 | 10910103.35 | 2466039.7173 | 415627.2274 | 168370.2097 | 271483.2198 | 694560.2887 | 0 | 75228.2343 | 29486.5865 | 0 | 811293.429 | 363150 | 12272.2947 | 203.441 | 6.7717 | 0.22884 | 45.9843 | 7.7502 | 3.1396 | 5.0624 | 12.9515 | 0 | 1.4028 | 0.54984 | 0 | 15.1282 | 2% | 2.215% | 53627.8468 | 21287.4627 | 7027.0036 | 764 | 51.5 | 815.5
45 |  | Medium Office CZ-6 Baseline | 0025 CZ06 MediumOffice Base | 11225233.5421 | 2220792.0717 | 36187.6526 | 329669.7047 | 271454.7853 | 694560.2887 | 0 | 67209.7026 | 10425.9869 | 0 | 811293.429 | 402477.7778 | 8476.9439 | 209.3173 | 7.505 | 0.15807 | 41.4112 | 0.67479 | 6.1474 | 5.0618 | 12.9515 | 0 | 1.2533 | 0.19441 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 181.25 | 64.5 | 245.75
46 | 28 | Envelope Glazing Test Medium OfficeCZ-6 Window U | 0030 CZ06 MediumOffice WinU-20 | 11250653.9937 | 2219569.3878 | 29714.0626 | 334456.1805 | 271483.2198 | 694560.2887 | 0 | 68830.4697 | 9241.2156 | 0 | 811293.429 | 404016.6667 | 8412.1917 | 209.7913 | 7.5337 | 0.15686 | 41.3884 | 0.55408 | 6.2366 | 5.0624 | 12.9515 | 0 | 1.2835 | 0.17232 | 0 | 15.1282 | -0.2265% | 0.05506% | 53627.8468 | 21287.4627 | 7027.0036 | 165.5 | 65.5 | 231
47 | 29 | Envelope Glazing Test Medium OfficeCZ-6 Window SHGC | 0031 CZ06 MediumOffice WinSHGC-20 | 11040352.3604 | 2201579.8214 | 38386.588 | 311973.9616 | 271454.7853 | 694560.2887 | 0 | 63200.4368 | 10719.8101 | 0 | 811293.429 | 396202.7778 | 8498.9388 | 205.8698 | 7.388 | 0.15848 | 41.0529 | 0.7158 | 5.8174 | 5.0618 | 12.9515 | 0 | 1.1785 | 0.19989 | 0 | 15.1282 | 1.647% | 0.8651% | 53627.8468 | 21287.4627 | 7027.0036 | 209.75 | 59.75 | 269.5
48 | 30 | Envelope Glazing Test Medium OfficeCZ-6 Window U&SHGC | 0032 CZ06 MediumOffice WinU_SHGC-20 | 11061744.5899 | 2199409.3205 | 31249.5261 | 316656.1775 | 271483.2198 | 694560.2887 | 0 | 64688.5094 | 9487.648 | 0 | 811293.429 | 397658.3333 | 8427.5502 | 206.2687 | 7.4151 | 0.15715 | 41.0124 | 0.58271 | 5.9047 | 5.0624 | 12.9515 | 0 | 1.2062 | 0.17692 | 0 | 15.1282 | 1.456% | 0.9628% | 53627.8468 | 21287.4627 | 7027.0036 | 195.75 | 62.75 | 258.5
49 |  | Large Office CZ-7 Baseline | 0049 CZ07 LargeOffice Base | 104292284.0115 | 17039484.1601 | 258346.4764 | 1653106.565 | 3073685.1883 | 7496853.2476 | 0 | 1270055.8075 | 840609.4084 | 0 | 2302664.5031 | 4243263.8889 | 25615.1338 | 209.1751 | 8.5106 | 0.051375 | 34.1755 | 0.51816 | 3.3156 | 6.1648 | 15.0362 | 0 | 2.5473 | 1.686 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 49903.1033 | 3.25 | 322.5 | 325.75
50 | 31 | Envelope Glazing Test Large OfficeCZ-7 WWR 20% | 0050 CZ07 LargeOffice WWR20 | 102825300.2684 | 16879151.4384 | 235759.9976 | 1578646.0624 | 3073685.1883 | 7496853.2476 | 0 | 1255743.7709 | 797862.8623 | 0 | 2302655.0249 | 4202897.2222 | 25389.1174 | 206.2328 | 8.4296 | 0.050922 | 33.8539 | 0.47285 | 3.1662 | 6.1648 | 15.0362 | 0 | 2.5186 | 1.6002 | 0 | 4.6183 | 1.407% | 0.9409% | 498588.4208 | 124748.7703 | 28752.8804 | 3 | 191 | 194
51 | 32 | Envelope Glazing Test Large OfficeCZ-7 WWR 60% | 0051 CZ07 LargeOffice WWR60 | 105474894.2236 | 17177173.5339 | 282961.2836 | 1715842.5714 | 3073685.1883 | 7496853.2476 | 0 | 1284367.844 | 871223.8971 | 0 | 2302664.5031 | 4276402.7778 | 25861.3439 | 211.547 | 8.577 | 0.051869 | 34.4516 | 0.56752 | 3.4414 | 6.1648 | 15.0362 | 0 | 2.576 | 1.7474 | 0 | 4.6184 | -1.134% | -0.8081% | 498588.4208 | 124748.7703 | 64961.5987 | 5.25 | 471.75 | 477
52 | 33 | Envelope Glazing Test Large OfficeCZ-7 WWR 60% with South overhang | 0052 CZ07 LargeOffice WWR60wSOverhg | 104616437.4213 | 17079557.8623 | 283710.059 | 1673266.6323 | 3073685.1883 | 7496853.2476 | 0 | 1247450.3723 | 855329.0062 | 0 | 2302664.5031 | 4247575 | 25868.8335 | 209.8252 | 8.5192 | 0.051884 | 34.2558 | 0.56903 | 3.356 | 6.1648 | 15.0362 | 0 | 2.502 | 1.7155 | 0 | 4.6184 | -0.3108% | -0.2352% | 498588.4208 | 124748.7703 | 64961.5987 | 5.25 | 475.5 | 480.75
53 |  | Large Office CZ-1 Baseline | 0065 CZ01 LargeOffice Base | 89859865.2583 | 17228365.1294 | 2667725.6942 | 135623.1328 | 3073685.1883 | 7496853.2476 | 0 | 1404968.0775 | 144409.3963 | 0 | 2302664.5031 | 3592875 | 49702.1917 | 180.2285 | 7.2061 | 0.099686 | 34.5543 | 5.3506 | 0.27201 | 6.1648 | 15.0362 | 0 | 2.8179 | 0.28964 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 49903.1033 | 140.5 | 206.5 | 347
54 | 34 | Envelope Glazing Test Large OfficeCZ-1 WWR 20% | 0066 CZ01 LargeOffice WWR20 | 89421888.5064 | 17042735.1724 | 2471650.7939 | 129860.4055 | 3073685.1883 | 7496853.2476 | 0 | 1427213.3422 | 138495.0183 | 0 | 2302664.5031 | 3595927.7778 | 47741.2336 | 179.3501 | 7.2122 | 0.095753 | 34.182 | 4.9573 | 0.26046 | 6.1648 | 15.0362 | 0 | 2.8625 | 0.27777 | 0 | 4.6184 | 0.4874% | 1.077% | 498588.4208 | 124748.7703 | 28752.8804 | 124.75 | 156 | 280.75
55 | 35 | Envelope Glazing Test Large OfficeCZ-1 WWR 60% | 0067 CZ01 LargeOffice WWR60 | 90264412.5051 | 17360414.9922 | 2779217.4065 | 137660.9393 | 3073685.1883 | 7496853.2476 | 0 | 1419507.5901 | 148342.8368 | 0 | 2302664.5031 | 3598902.7778 | 50817.2947 | 181.0399 | 7.2182 | 0.10192 | 34.8191 | 5.5742 | 0.2761 | 6.1648 | 15.0362 | 0 | 2.8471 | 0.29753 | 0 | 4.6184 | -0.4502% | -0.7665% | 498588.4208 | 124748.7703 | 64961.5987 | 151 | 240 | 391
57 |  | Medium Office CZ-15 Baseline | 0001 CZ15 MediumOffice Base | 15796829.7417 | 2720111.5391 | 18880.5144 | 802014.3007 | 271284.1783 | 694560.2887 | 0 | 115207.1549 | 6871.6732 | 0 | 811293.429 | 553886.1111 | 8303.829 | 294.5639 | 10.3283 | 0.15484 | 50.722 | 0.35207 | 14.9552 | 5.0586 | 12.9515 | 0 | 2.1483 | 0.12814 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 80.25 | 597 | 677.25
58 | 36 | Lighting Tests Medium OfficeCZ-15 low LPD | 0009 CZ15 MediumOffice LPD-20 | 15326996.8608 | 2651536.98 | 19705.1152 | 787417.919 | 217021.6557 | 694560.2887 | 0 | 114676.3774 | 6862.195 | 0 | 811293.429 | 533547.2222 | 8312.0771 | 285.803 | 9.9491 | 0.155 | 49.4433 | 0.36744 | 14.683 | 4.0468 | 12.9515 | 0 | 2.1384 | 0.12796 | 0 | 15.1282 | 2.974% | 2.521% | 53627.8468 | 21287.4627 | 7027.0036 | 85.25 | 624.25 | 709.5
59 | 37 | Lighting Tests Medium OfficeCZ-15 high LPD | 0010 CZ15 MediumOffice LPD+20 | 16271430.1421 | 2789074.7031 | 18065.3918 | 816857.1147 | 325537.2227 | 694560.2887 | 0 | 115851.6704 | 6919.064 | 0 | 811293.429 | 574336.1111 | 8295.6757 | 303.4138 | 10.7097 | 0.15469 | 52.008 | 0.33687 | 15.232 | 6.0703 | 12.9515 | 0 | 2.1603 | 0.12902 | 0 | 15.1282 | -3.004% | -2.535% | 53627.8468 | 21287.4627 | 7027.0036 | 75.5 | 571 | 646.5
60 |  | Medium Office CZ-16 Baseline | 0013 CZ16 MediumOffice Base | 11132717.1259 | 2521894.5724 | 456705.6156 | 177346.0366 | 271454.7853 | 694560.2887 | 0 | 79161.6748 | 31382.2205 | 0 | 811293.429 | 367480.5556 | 12683.182 | 207.5921 | 6.8524 | 0.2365 | 47.0258 | 8.5162 | 3.307 | 5.0618 | 12.9515 | 0 | 1.4761 | 0.58519 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 747.75 | 74.75 | 822.5
61 | 38 | Lighting Tests Medium OfficeCZ-16 low LPD | 0021 CZ16 MediumOffice LPD-20 | 10721639.4201 | 2464561.1228 | 461103.4865 | 172407.9101 | 217163.8283 | 694560.2887 | 0 | 77171.2592 | 30870.3993 | 0 | 811293.429 | 349388.8889 | 12727.1718 | 199.9267 | 6.5151 | 0.23732 | 45.9567 | 8.5982 | 3.2149 | 4.0495 | 12.9515 | 0 | 1.439 | 0.57564 | 0 | 15.1282 | 3.693% | 2.273% | 53627.8468 | 21287.4627 | 7027.0036 | 763.25 | 82.5 | 845.75
62 | 39 | Lighting Tests Medium OfficeCZ-16 high LPD | 0022 CZ16 MediumOffice LPD+20 | 11533397.2794 | 2573124.0806 | 446109.0217 | 182322.0758 | 325745.7424 | 694560.2887 | 0 | 81190.0032 | 31894.0416 | 0 | 811293.429 | 385597.2222 | 12577.2842 | 215.0636 | 7.1902 | 0.23453 | 47.9811 | 8.3186 | 3.3998 | 6.0742 | 12.9515 | 0 | 1.514 | 0.59473 | 0 | 15.1282 | -3.599% | -2.031% | 53627.8468 | 21287.4627 | 7027.0036 | 739.25 | 67 | 806.25
63 |  | Medium Office CZ-6 Baseline | 0025 CZ06 MediumOffice Base | 11225233.5421 | 2220792.0717 | 36187.6526 | 329669.7047 | 271454.7853 | 694560.2887 | 0 | 67209.7026 | 10425.9869 | 0 | 811293.429 | 402477.7778 | 8476.9439 | 209.3173 | 7.505 | 0.15807 | 41.4112 | 0.67479 | 6.1474 | 5.0618 | 12.9515 | 0 | 1.2533 | 0.19441 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 181.25 | 64.5 | 245.75
64 | 40 | Lighting Tests Medium OfficeCZ-6 low LPD | 0033 CZ06 MediumOffice LPD-20 | 10786517.4929 | 2156463.7327 | 37817.8978 | 320001.9715 | 217163.8283 | 694560.2887 | 0 | 65276.156 | 10359.6397 | 0 | 811293.429 | 383150 | 8493.1557 | 201.1365 | 7.1446 | 0.15837 | 40.2116 | 0.70519 | 5.9671 | 4.0495 | 12.9515 | 0 | 1.2172 | 0.19318 | 0 | 15.1282 | 3.908% | 2.897% | 53627.8468 | 21287.4627 | 7027.0036 | 191.5 | 67.25 | 258.75
65 | 41 | Lighting Tests Medium OfficeCZ-6 high LPD | 0034 CZ06 MediumOffice LPD+20 | 11668347.4621 | 2285215.1924 | 34585.8419 | 339422.7415 | 325745.7424 | 694560.2887 | 0 | 69162.2056 | 10454.4214 | 0 | 811293.429 | 421830.5556 | 8460.827 | 217.58 | 7.8659 | 0.15777 | 42.6125 | 0.64492 | 6.3292 | 6.0742 | 12.9515 | 0 | 1.2897 | 0.19494 | 0 | 15.1282 | -3.947% | -2.901% | 53627.8468 | 21287.4627 | 7027.0036 | 170.5 | 64.5 | 235
67 |  | Large Office CZ-7 Baseline | 0049 CZ07 LargeOffice Base | 104292284.0115 | 17039484.1601 | 258346.4764 | 1653106.565 | 3073685.1883 | 7496853.2476 | 0 | 1270055.8075 | 840609.4084 | 0 | 2302664.5031 | 4243263.8889 | 25615.1338 | 209.1751 | 8.5106 | 0.051375 | 34.1755 | 0.51816 | 3.3156 | 6.1648 | 15.0362 | 0 | 2.5473 | 1.686 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 49903.1033 | 3.25 | 322.5 | 325.75
68 | 42 | Daylighting Tests Large OfficeCZ-7 Continuous Dimming | 0053 CZ07 LargeOffice BaseContDim | 100548331.0838 | 16522885.989 | 278023.1571 | 1611848.0915 | 2631812.9085 | 7496853.2476 | 0 | 1244170.9255 | 817075.1126 | 0 | 2302664.5031 | 4086102.7778 | 25811.7606 | 201.666 | 8.1953 | 0.05177 | 33.1393 | 0.55762 | 3.2328 | 5.2785 | 15.0362 | 0 | 2.4954 | 1.6388 | 0 | 4.6184 | 3.59% | 3.032% | 498588.4208 | 124748.7703 | 49903.1033 | 4 | 362.5 | 366.5
69 | 43 | Daylighting Tests Large OfficeCZ-7 Continuous Dimming and high VT | 0054 CZ07 LargeOffice BaseContDimVT+20 | 100572149.7248 | 16521208.3529 | 278516.0219 | 1613355.1205 | 2628647.1998 | 7496853.2476 | 0 | 1243706.4952 | 817008.7654 | 0 | 2302664.5031 | 4085466.6667 | 25816.6904 | 201.7138 | 8.1941 | 0.05178 | 33.136 | 0.55861 | 3.2358 | 5.2722 | 15.0362 | 0 | 2.4945 | 1.6386 | 0 | 4.6184 | 3.567% | 3.042% | 498588.4208 | 124748.7703 | 49903.1033 | 4 | 362.5 | 366.5
70 | 44 | Daylighting Tests Large OfficeCZ-7 Stepped Dimming | 0055 CZ07 LargeOffice BaseStDim | 99182934.3656 | 16325019.7146 | 285169.6972 | 1595185.4688 | 2462902.4431 | 7496853.2476 | 0 | 1236285.0882 | 807028.2525 | 0 | 2302664.5031 | 4026019.4444 | 25883.2439 | 198.9275 | 8.0748 | 0.051913 | 32.7425 | 0.57195 | 3.1994 | 4.9398 | 15.0362 | 0 | 2.4796 | 1.6186 | 0 | 4.6184 | 4.899% | 4.193% | 498588.4208 | 124748.7703 | 49903.1033 | 4.5 | 379.25 | 383.75
71 | 45 | Daylighting Tests Large OfficeCZ-7 Stepped Dimming and high VT | 0056 CZ07 LargeOffice BaseStDimVT+20 | 99105601.9775 | 16311465.9317 | 286553.51 | 1591536.3734 | 2453481.1422 | 7496853.2476 | 0 | 1234797.0155 | 806781.8201 | 0 | 2302664.5031 | 4021641.6667 | 25897.0856 | 198.7724 | 8.0661 | 0.051941 | 32.7153 | 0.57473 | 3.1921 | 4.9209 | 15.0362 | 0 | 2.4766 | 1.6181 | 0 | 4.6184 | 4.973% | 4.273% | 498588.4208 | 124748.7703 | 49903.1033 | 4.5 | 379.75 | 384.25
72 |  | Large Office CZ-7 WWR 20% Baseline | 0050 CZ07 LargeOffice WWR20 | 102825300.2684 | 16879151.4384 | 235759.9976 | 1578646.0624 | 3073685.1883 | 7496853.2476 | 0 | 1255743.7709 | 797862.8623 | 0 | 2302655.0249 | 4202897.2222 | 25389.1174 | 206.2328 | 8.4296 | 0.050922 | 33.8539 | 0.47285 | 3.1662 | 6.1648 | 15.0362 | 0 | 2.5186 | 1.6002 | 0 | 4.6183 |  |  | 498588.4208 | 124748.7703 | 28752.8804 | 3 | 191 | 194
73 | 46 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Continuous Dimming | 0057 CZ07 LargeOffice WWR20ContDim | 99257574.9534 | 16381395.869 | 249209.5206 | 1528061.0697 | 2659716.6406 | 7496853.2476 | 0 | 1235507.8783 | 775247.9489 | 0 | 2302664.5031 | 4053080.5556 | 25523.5517 | 199.0772 | 8.1291 | 0.051192 | 32.8555 | 0.49983 | 3.0648 | 5.3345 | 15.0362 | 0 | 2.478 | 1.5549 | 0 | 4.6184 | 3.47% | 2.949% | 498588.4208 | 124748.7703 | 28752.8804 | 3.25 | 212.25 | 215.5
74 | 47 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Continuous Dimming and high VT | 0058 CZ07 LargeOffice WWR20ContDimVT+20 | 99099877.1629 | 16370391.7138 | 250839.7659 | 1527719.8556 | 2649347.5228 | 7496853.2476 | 0 | 1234105.1091 | 774840.3876 | 0 | 2302664.5031 | 4049377.7778 | 25539.8582 | 198.7609 | 8.1217 | 0.051224 | 32.8335 | 0.5031 | 3.0641 | 5.3137 | 15.0362 | 0 | 2.4752 | 1.5541 | 0 | 4.6184 | 3.623% | 3.014% | 498588.4208 | 124748.7703 | 28752.8804 | 3.25 | 212 | 215.25
75 | 48 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Stepped Dimming | 0059 CZ07 LargeOffice WWR20StDim | 98273049.0135 | 16246502.5553 | 249512.8221 | 1516630.3969 | 2548310.2319 | 7496853.2476 | 0 | 1231043.6602 | 768537.4046 | 0 | 2302655.0249 | 4013458.3333 | 25526.5854 | 197.1025 | 8.0496 | 0.051198 | 32.585 | 0.50044 | 3.0418 | 5.111 | 15.0362 | 0 | 2.4691 | 1.5414 | 0 | 4.6183 | 4.427% | 3.748% | 498588.4208 | 124748.7703 | 28752.8804 | 3.25 | 221.75 | 225
76 | 49 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Stepped Dimming and high VT | 0060 CZ07 LargeOffice WWR20StDimVT+20 | 98055761.969 | 16214608.5137 | 252214.1005 | 1517132.7399 | 2516292.974 | 7496853.2476 | 0 | 1230143.2341 | 766471.1636 | 0 | 2302664.5031 | 4003316.6667 | 25553.6998 | 196.6667 | 8.0293 | 0.051252 | 32.521 | 0.50586 | 3.0429 | 5.0468 | 15.0362 | 0 | 2.4673 | 1.5373 | 0 | 4.6184 | 4.638% | 3.937% | 498588.4208 | 124748.7703 | 28752.8804 | 3.25 | 222 | 225.25
77 |  | Large Office CZ-7 WWR 60% Baseline | 0051 CZ07 LargeOffice WWR60 | 105474894.2236 | 17177173.5339 | 282961.2836 | 1715842.5714 | 3073685.1883 | 7496853.2476 | 0 | 1284367.844 | 871223.8971 | 0 | 2302664.5031 | 4276402.7778 | 25861.3439 | 211.547 | 8.577 | 0.051869 | 34.4516 | 0.56752 | 3.4414 | 6.1648 | 15.0362 | 0 | 2.576 | 1.7474 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 64961.5987 | 5.25 | 471.75 | 477
78 | 50 | Daylighting Tests Large OfficeCZ-7WWR-60%,Continuous Dimming | 0061 CZ07 LargeOffice WWR60ContDim | 101790445.2465 | 16660480.5811 | 300856.0683 | 1673863.757 | 2633082.9833 | 7496853.2476 | 0 | 1259923.6439 | 847462.1252 | 0 | 2302664.5031 | 4119736.1111 | 26040.1471 | 204.1573 | 8.2628 | 0.052228 | 33.4153 | 0.60342 | 3.3572 | 5.2811 | 15.0362 | 0 | 2.527 | 1.6997 | 0 | 4.6184 | 3.493% | 3.008% | 498588.4208 | 124748.7703 | 64961.5987 | 6.25 | 516.25 | 522.5
79 | 51 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Continuous Dimming and high VT | 0062 CZ07 LargeOffice WWR60ContDimVT+20 | 101728827.6641 | 16652187.1825 | 301311.0205 | 1669181.5411 | 2629632.9294 | 7496853.2476 | 0 | 1259402.3445 | 847471.6034 | 0 | 2302664.5031 | 4117172.2222 | 26044.6978 | 204.0337 | 8.2577 | 0.052237 | 33.3987 | 0.60433 | 3.3478 | 5.2742 | 15.0362 | 0 | 2.5259 | 1.6997 | 0 | 4.6184 | 3.552% | 3.056% | 498588.4208 | 124748.7703 | 64961.5987 | 6.25 | 516 | 522.25
80 | 52 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Stepped Dimming | 0063 CZ07 LargeOffice WWR60StDim | 100346180.6767 | 16455799.5026 | 306997.9224 | 1648376.9582 | 2466267.1934 | 7496853.2476 | 0 | 1252710.7566 | 837841.7828 | 0 | 2302664.5031 | 4057952.7778 | 26101.4863 | 201.2606 | 8.1389 | 0.052351 | 33.0048 | 0.61573 | 3.3061 | 4.9465 | 15.0362 | 0 | 2.5125 | 1.6804 | 0 | 4.6184 | 4.862% | 4.2% | 498588.4208 | 124748.7703 | 64961.5987 | 6.25 | 530 | 536.25
81 | 53 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Stepped Dimming and high VT | 0064 CZ07 LargeOffice WWR60StDimVT+20 | 100260204.1977 | 16441591.7259 | 308457.5605 | 1644225.5198 | 2456172.9425 | 7496853.2476 | 0 | 1251326.9438 | 837964.999 | 0 | 2302664.5031 | 4053361.1111 | 26116.0864 | 201.0881 | 8.1297 | 0.05238 | 32.9763 | 0.61866 | 3.2978 | 4.9263 | 15.0362 | 0 | 2.5097 | 1.6807 | 0 | 4.6184 | 4.944% | 4.282% | 498588.4208 | 124748.7703 | 64961.5987 | 6.25 | 530 | 536.25
82 |  | Large Office CZ-1 Baseline | 0065 CZ01 LargeOffice Base | 89859865.2583 | 17228365.1294 | 2667725.6942 | 135623.1328 | 3073685.1883 | 7496853.2476 | 0 | 1404968.0775 | 144409.3963 | 0 | 2302664.5031 | 3592875 | 49702.1917 | 180.2285 | 7.2061 | 0.099686 | 34.5543 | 5.3506 | 0.27201 | 6.1648 | 15.0362 | 0 | 2.8179 | 0.28964 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 49903.1033 | 140.5 | 206.5 | 347
83 | 54 | Daylighting Tests Large OfficeCZ-1 Continuous Dimming | 0068 CZ01 LargeOffice BaseContDim | 86954891.4939 | 16987050.9243 | 2909400.0698 | 130419.6175 | 2639812.4839 | 7496853.2476 | 0 | 1365387.2401 | 140144.2198 | 0 | 2302664.5031 | 3451375 | 52117.8373 | 174.4021 | 6.9223 | 0.10453 | 34.0703 | 5.8353 | 0.26158 | 5.2946 | 15.0362 | 0 | 2.7385 | 0.28108 | 0 | 4.6184 | 3.233% | 1.401% | 498588.4208 | 124748.7703 | 49903.1033 | 144.5 | 210.25 | 354.75
84 | 55 | Daylighting Tests Large OfficeCZ-1 Continuous Dimming and high VT | 0069 CZ01 LargeOffice BaseContDimVT+20 | 86922703.629 | 16984965.7269 | 2913902.2005 | 130419.6175 | 2634296.189 | 7496853.2476 | 0 | 1364306.7287 | 140153.698 | 0 | 2302664.5031 | 3449444.4444 | 52162.8699 | 174.3376 | 6.9184 | 0.10462 | 34.0661 | 5.8443 | 0.26158 | 5.2835 | 15.0362 | 0 | 2.7363 | 0.2811 | 0 | 4.6184 | 3.269% | 1.413% | 498588.4208 | 124748.7703 | 49903.1033 | 144.5 | 210 | 354.5
85 | 56 | Daylighting Tests Large OfficeCZ-1 Stepped Dimming | 0070 CZ01 LargeOffice BaseStDim | 85912321.2417 | 16903462.9441 | 2990267.8152 | 128523.9836 | 2487867.9426 | 7496853.2476 | 0 | 1356790.54 | 138163.2823 | 0 | 2302664.5031 | 3403197.2222 | 52926.0546 | 172.3111 | 6.8257 | 0.10615 | 33.9026 | 5.9975 | 0.25778 | 4.9898 | 15.0362 | 0 | 2.7213 | 0.27711 | 0 | 4.6184 | 4.393% | 1.886% | 498588.4208 | 124748.7703 | 49903.1033 | 146 | 213.25 | 359.25
86 | 57 | Daylighting Tests Large OfficeCZ-1 Stepped Dimming and high VT | 0071 CZ01 LargeOffice BaseStDimVT+20 | 85823795.135 | 16898174.1254 | 3004854.7186 | 128457.6364 | 2472247.9186 | 7496853.2476 | 0 | 1352743.3615 | 138021.1098 | 0 | 2302664.5031 | 3397375 | 53071.8656 | 172.1336 | 6.814 | 0.10644 | 33.892 | 6.0267 | 0.25764 | 4.9585 | 15.0362 | 0 | 2.7131 | 0.27682 | 0 | 4.6184 | 4.492% | 1.917% | 498588.4208 | 124748.7703 | 49903.1033 | 146.25 | 213 | 359.25
87 |  | Large Office CZ-1 WWR-20% Baseline | 0066 CZ01 LargeOffice WWR20 | 89421888.5064 | 17042735.1724 | 2471650.7939 | 129860.4055 | 3073685.1883 | 7496853.2476 | 0 | 1427213.3422 | 138495.0183 | 0 | 2302664.5031 | 3595927.7778 | 47741.2336 | 179.3501 | 7.2122 | 0.095753 | 34.182 | 4.9573 | 0.26046 | 6.1648 | 15.0362 | 0 | 2.8625 | 0.27777 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 28752.8804 | 124.75 | 156 | 280.75
88 | 58 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Continuous Dimming | 0072 CZ01 LargeOffice WWR20ContDim | 86770607.437 | 16845371.241 | 2714822.7203 | 126344.0045 | 2683288.8491 | 7496853.2476 | 0 | 1384684.794 | 134466.7961 | 0 | 2302655.0249 | 3466872.2222 | 50171.7636 | 174.0325 | 6.9534 | 0.10063 | 33.7861 | 5.445 | 0.2534 | 5.3818 | 15.0362 | 0 | 2.7772 | 0.26969 | 0 | 4.6183 | 2.965% | 1.158% | 498588.4208 | 124748.7703 | 28752.8804 | 129.5 | 165.75 | 295.25
89 | 59 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Continuous Dimming and high VT | 0073 CZ01 LargeOffice WWR20ContDimVT+20 | 86691578.4565 | 16843579.8669 | 2731125.1725 | 126268.1791 | 2668408.1224 | 7496853.2476 | 0 | 1381604.3888 | 134390.9707 | 0 | 2302664.5031 | 3461569.4444 | 50334.8292 | 173.874 | 6.9427 | 0.10095 | 33.7825 | 5.4777 | 0.25325 | 5.3519 | 15.0362 | 0 | 2.771 | 0.26954 | 0 | 4.6184 | 3.053% | 1.169% | 498588.4208 | 124748.7703 | 28752.8804 | 130 | 166 | 296
90 | 60 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Stepped Dimming | 0074 CZ01 LargeOffice WWR20StDim | 86098074.415 | 16770218.832 | 2729826.6632 | 124865.41 | 2601511.1994 | 7496853.2476 | 0 | 1379386.497 | 132874.4635 | 0 | 2302655.0249 | 3440455.5556 | 50321.6512 | 172.6837 | 6.9004 | 0.10093 | 33.6354 | 5.4751 | 0.25044 | 5.2178 | 15.0362 | 0 | 2.7666 | 0.2665 | 0 | 4.6183 | 3.717% | 1.599% | 498588.4208 | 124748.7703 | 28752.8804 | 130.25 | 171.75 | 302
91 | 61 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Stepped Dimming and high VT | 0075 CZ01 LargeOffice WWR20StDimVT+20 | 85893345.9456 | 16768863.4537 | 2771236.7874 | 124571.5867 | 2563873.3868 | 7496853.2476 | 0 | 1374941.2353 | 132485.8586 | 0 | 2302655.0249 | 3427930.5556 | 50735.5723 | 172.273 | 6.8753 | 0.10176 | 33.6327 | 5.5582 | 0.24985 | 5.1423 | 15.0362 | 0 | 2.7577 | 0.26572 | 0 | 4.6183 | 3.946% | 1.607% | 498588.4208 | 124748.7703 | 28752.8804 | 130.25 | 171.5 | 301.75
92 |  | Large Office CZ-1 WWR-60% Baseline | 0067 CZ01 LargeOffice WWR60 | 90264412.5051 | 17360414.9922 | 2779217.4065 | 137660.9393 | 3073685.1883 | 7496853.2476 | 0 | 1419507.5901 | 148342.8368 | 0 | 2302664.5031 | 3598902.7778 | 50817.2947 | 181.0399 | 7.2182 | 0.10192 | 34.8191 | 5.5742 | 0.2761 | 6.1648 | 15.0362 | 0 | 2.8471 | 0.29753 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 64961.5987 | 151 | 240 | 391
93 | 62 | Daylighting Tests Large OfficeCZ-1WWR-60%,Continuous Dimming | 0076 CZ01 LargeOffice WWR60ContDim | 87318076.0073 | 17081567.2343 | 2976609.7724 | 132694.3783 | 2641954.5503 | 7496853.2476 | 0 | 1385026.0081 | 143338.3631 | 0 | 2302664.5031 | 3459369.4444 | 52790.3879 | 175.1306 | 6.9383 | 0.10588 | 34.2599 | 5.9701 | 0.26614 | 5.2989 | 15.0362 | 0 | 2.7779 | 0.28749 | 0 | 4.6184 | 3.264% | 1.606% | 498588.4208 | 124748.7703 | 64961.5987 | 155.25 | 249.25 | 404.5
94 | 63 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Continuous Dimming and high VT | 0077 CZ01 LargeOffice WWR60ContDimVT+20 | 87282599.2175 | 17078534.22 | 2981073.9904 | 132675.422 | 2636021.2159 | 7496853.2476 | 0 | 1383500.0227 | 143328.8849 | 0 | 2302664.5031 | 3457175 | 52834.9465 | 175.0594 | 6.9339 | 0.10597 | 34.2538 | 5.979 | 0.2661 | 5.287 | 15.0362 | 0 | 2.7748 | 0.28747 | 0 | 4.6184 | 3.303% | 1.624% | 498588.4208 | 124748.7703 | 64961.5987 | 155.75 | 249 | 404.75
95 | 64 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Stepped Dimming | 0078 CZ01 LargeOffice WWR60StDim | 86278690.4202 | 16985629.1988 | 3038473.7872 | 132059.3409 | 2492796.5909 | 7496853.2476 | 0 | 1378912.5885 | 141452.2073 | 0 | 2302664.5031 | 3413138.8889 | 53408.6149 | 173.0459 | 6.8456 | 0.10712 | 34.0674 | 6.0942 | 0.26487 | 4.9997 | 15.0362 | 0 | 2.7656 | 0.28371 | 0 | 4.6184 | 4.416% | 2.159% | 498588.4208 | 124748.7703 | 64961.5987 | 157.75 | 252 | 409.75
96 | 65 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Stepped Dimming and high VT | 0079 CZ01 LargeOffice WWR60StDimVT+20 | 86184704.8877 | 16978321.5299 | 3051089.2313 | 131983.5156 | 2476835.3528 | 7496853.2476 | 0 | 1374931.7572 | 141537.5108 | 0 | 2302664.5031 | 3407300 | 53534.8011 | 172.8574 | 6.8339 | 0.10737 | 34.0528 | 6.1195 | 0.26471 | 4.9677 | 15.0362 | 0 | 2.7576 | 0.28388 | 0 | 4.6184 | 4.52% | 2.201% | 498588.4208 | 124748.7703 | 64961.5987 | 158 | 250.25 | 408.25
97 |  | Stand Alone Retail CZ-7 Baseline | 0080 CZ07 SAloneRetail BaseStDim | 6896648.14 | 1113485.9192 | 65370.9377 | 145783.7309 | 194700.5657 | 264848.5009 | 0 | 235077.5693 | 0 | 0 | 207714.0929 | 246297.2222 | 2731.5377 | 279.3036 | 9.9747 | 0.11062 | 45.0945 | 2.6474 | 5.904 | 7.8851 | 10.726 | 0 | 9.5203 | 0 | 0 | 8.4121 |  |  | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
98 | 66 | Daylighting Tests Stand Alone Retail CZ-7 Skylight VT | 0081 CZ07 SAloneRetail BaseStDimSVT+20 | 6810766.4427 | 1103022.0197 | 65712.1518 | 144826.4358 | 185393.0028 | 264848.5009 | 0 | 234518.3573 | 0 | 0 | 207714.0929 | 243130.5556 | 2734.9507 | 275.8255 | 9.8464 | 0.11076 | 44.6707 | 2.6612 | 5.8652 | 7.5081 | 10.726 | 0 | 9.4976 | 0 | 0 | 8.4121 | 1.245% | 0.9397% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
99 | 67 | Daylighting Tests Stand Alone Retail CZ-7 SRR-5% | 0082 CZ07 SAloneRetail SkyLt5StDim | 6765138.5329 | 1097410.9431 | 68517.6901 | 149091.6122 | 166427.1849 | 264848.5009 | 0 | 240783.4276 | 0 | 0 | 207733.0492 | 240658.3333 | 2763.2027 | 273.9776 | 9.7463 | 0.11191 | 44.4434 | 2.7749 | 6.038 | 6.74 | 10.726 | 0 | 9.7514 | 0 | 0 | 8.4129 | 1.907% | 1.444% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
100 | 68 | Daylighting Tests Stand Alone Retail CZ-7 SRR-5% and high VT | 0083 CZ07 SAloneRetail SkyLt5StDimSVT+20 | 6745518.7213 | 1094870.7936 | 68792.557 | 148845.1798 | 164929.6341 | 264848.5009 | 0 | 239731.3508 | 0 | 0 | 207733.0492 | 239833.3333 | 2765.9521 | 273.1831 | 9.7129 | 0.11202 | 44.3406 | 2.786 | 6.028 | 6.6794 | 10.726 | 0 | 9.7087 | 0 | 0 | 8.4129 | 2.191% | 1.672% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
101 |  | Stand Alone Retail CZ-1 Baseline | 0084 CZ01 SAloneRetail BaseStDim | 6109524.0442 | 1234275.7162 | 272089.8227 | 19202.7722 | 201790.2367 | 264848.5009 | 0 | 268412.2928 | 0 | 0 | 207922.6126 | 221052.7778 | 4801.3326 | 247.4263 | 8.9523 | 0.19445 | 49.9863 | 11.0192 | 0.77768 | 8.1722 | 10.726 | 0 | 10.8703 | 0 | 0 | 8.4205 |  |  | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
102 | 69 | Daylighting Tests Stand Alone Retail CZ-1 Skylight VT | 0085 CZ01 SAloneRetail BaseStDimSVT+20 | 6031063.754 | 1224636.4174 | 273483.1137 | 19041.6433 | 191572.7696 | 264848.5009 | 0 | 267767.7773 | 0 | 0 | 207932.0908 | 217816.6667 | 4815.3638 | 244.2487 | 8.8212 | 0.19501 | 49.5959 | 11.0756 | 0.77116 | 7.7584 | 10.726 | 0 | 10.8442 | 0 | 0 | 8.4209 | 1.284% | 0.781% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
103 | 70 | Daylighting Tests Stand Alone Retail CZ-1 SRR-5% | 0086 CZ01 SAloneRetail SkyLt5StDim | 5875849.244 | 1210438.1189 | 287245.4164 | 19951.5476 | 166815.7899 | 264848.5009 | 0 | 263597.3825 | 0 | 0 | 207960.5253 | 209611.1111 | 4953.4007 | 237.9628 | 8.4889 | 0.20061 | 49.0209 | 11.633 | 0.80801 | 6.7558 | 10.726 | 0 | 10.6753 | 0 | 0 | 8.4221 | 3.825% | 1.931% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
104 | 71 | Daylighting Tests Stand Alone Retail CZ-1 SRR-5% and high VT | 0087 CZ01 SAloneRetail SkyLt5StDimSVT+20 | 5854817.1851 | 1207812.6659 | 288269.0587 | 19998.9384 | 164180.8586 | 264848.5009 | 0 | 262545.3057 | 0 | 0 | 207970.0035 | 208541.6667 | 4963.6397 | 237.111 | 8.4456 | 0.20102 | 48.9145 | 11.6745 | 0.80993 | 6.6491 | 10.726 | 0 | 10.6327 | 0 | 0 | 8.4225 | 4.169% | 2.144% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
106 |  | Medium Office CZ-15 Baseline | 0001 CZ15 MediumOffice Base | 15796829.7417 | 2720111.5391 | 18880.5144 | 802014.3007 | 271284.1783 | 694560.2887 | 0 | 115207.1549 | 6871.6732 | 0 | 811293.429 | 553886.1111 | 8303.829 | 294.5639 | 10.3283 | 0.15484 | 50.722 | 0.35207 | 14.9552 | 5.0586 | 12.9515 | 0 | 2.1483 | 0.12814 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 80.25 | 597 | 677.25
107 | 72 | Equipment test Medium OfficeCZ-15 low EPD | 0011 CZ15 MediumOffice EPD-20 | 14511987.9893 | 2534367.844 | 20662.4103 | 760357.744 | 271284.1783 | 555648.231 | 0 | 108174.3528 | 6956.9767 | 0 | 811293.429 | 498927.7778 | 8321.6524 | 270.6055 | 9.3035 | 0.15517 | 47.2584 | 0.38529 | 14.1784 | 5.0586 | 10.3612 | 0 | 2.0171 | 0.12973 | 0 | 15.1282 | 8.134% | 6.829% | 53627.8468 | 21287.4627 | 7027.0036 | 92.25 | 648 | 740.25
108 | 73 | Equipment test Medium OfficeCZ-15 high EPD | 0012 CZ15 MediumOffice EPD+20 | 17083387.043 | 2906404.9681 | 17098.6185 | 844002.5932 | 271284.1783 | 833462.8683 | 0 | 122438.9985 | 6824.2823 | 0 | 811293.429 | 609005.5556 | 8286.0056 | 318.5544 | 11.3561 | 0.15451 | 54.1958 | 0.31884 | 15.7381 | 5.0586 | 15.5416 | 0 | 2.2831 | 0.12725 | 0 | 15.1282 | -8.144% | -6.849% | 53627.8468 | 21287.4627 | 7027.0036 | 70.5 | 552.5 | 623
109 |  | Medium Office CZ-16 Baseline | 0013 CZ16 MediumOffice Base | 11132717.1259 | 2521894.5724 | 456705.6156 | 177346.0366 | 271454.7853 | 694560.2887 | 0 | 79161.6748 | 31382.2205 | 0 | 811293.429 | 367480.5556 | 12683.182 | 207.5921 | 6.8524 | 0.2365 | 47.0258 | 8.5162 | 3.307 | 5.0618 | 12.9515 | 0 | 1.4761 | 0.58519 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 747.75 | 74.75 | 822.5
110 | 74 | Equipment test Medium OfficeCZ-16 low EPD | 0023 CZ16 MediumOffice EPD-20 | 10058451.8736 | 2380669.8412 | 476969.9428 | 162825.4804 | 271454.7853 | 555648.231 | 0 | 71806.615 | 30671.3577 | 0 | 811302.9071 | 320150 | 12885.9711 | 187.5602 | 5.9698 | 0.24029 | 44.3924 | 8.8941 | 3.0362 | 5.0618 | 10.3612 | 0 | 1.339 | 0.57193 | 0 | 15.1284 | 9.65% | 5.6% | 53627.8468 | 21287.4627 | 7027.0036 | 791 | 82.75 | 873.75
111 | 75 | Equipment test Medium OfficeCZ-16 high EPD | 0024 CZ16 MediumOffice EPD+20 | 12188414.6434 | 2652560.6224 | 425626.6966 | 191942.4182 | 271454.7853 | 833462.8683 | 0 | 86848.4706 | 31931.9543 | 0 | 811293.429 | 414883.3333 | 12372.3146 | 227.2777 | 7.7363 | 0.23071 | 49.4624 | 7.9367 | 3.5792 | 5.0618 | 15.5416 | 0 | 1.6195 | 0.59544 | 0 | 15.1282 | -9.483% | -5.181% | 53627.8468 | 21287.4627 | 7027.0036 | 722.5 | 64.25 | 786.75
112 |  | Medium Office CZ-6 Baseline | 0025 CZ06 MediumOffice Base | 11225233.5421 | 2220792.0717 | 36187.6526 | 329669.7047 | 271454.7853 | 694560.2887 | 0 | 67209.7026 | 10425.9869 | 0 | 811293.429 | 402477.7778 | 8476.9439 | 209.3173 | 7.505 | 0.15807 | 41.4112 | 0.67479 | 6.1474 | 5.0618 | 12.9515 | 0 | 1.2533 | 0.19441 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 181.25 | 64.5 | 245.75
113 | 76 | Equipment test Medium OfficeCZ-6 low EPD | 0035 CZ06 MediumOffice EPD-20 | 10047485.6311 | 2049474.1511 | 39694.5755 | 300505.376 | 271454.7853 | 555648.231 | 0 | 60205.3351 | 10662.9411 | 0 | 811293.429 | 351241.6667 | 8512.022 | 187.3558 | 6.5496 | 0.15872 | 38.2166 | 0.74019 | 5.6035 | 5.0618 | 10.3612 | 0 | 1.1227 | 0.19883 | 0 | 15.1282 | 10.49% | 7.714% | 53627.8468 | 21287.4627 | 7027.0036 | 210.25 | 66.75 | 277
114 | 77 | Equipment test Medium OfficeCZ-6 high EPD | 0036 CZ06 MediumOffice EPD+20 | 12411018.9412 | 2393133.6346 | 33391.5925 | 358919.337 | 271454.7853 | 833462.8683 | 0 | 74451.0244 | 10170.0763 | 0 | 811293.429 | 453808.3333 | 8448.8815 | 231.4286 | 8.4622 | 0.15755 | 44.6248 | 0.62265 | 6.6928 | 5.0618 | 15.5416 | 0 | 1.3883 | 0.18964 | 0 | 15.1282 | -10.56% | -7.76% | 53627.8468 | 21287.4627 | 7027.0036 | 153.75 | 62.75 | 216.5
115 |  | Fast food Restaurant CZ-6 Baseline | 0088 CZ06 QSRest Base | 6477532.9461 | 1091885.1701 | 50708.2089 | 120894.0568 | 51788.7202 | 614441.3188 | 0 | 101369.0269 | 0 | 62612.7902 | 90080.5265 | 260872.2222 | 2018.0311 | 2590.0943 | 104.3119 | 0.80693 | 436.5992 | 20.2761 | 48.3405 | 20.7081 | 245.6894 | 0 | 40.5332 | 0 | 25.0362 | 36.0194 |  |  | 2500.8869 | 2000.9033 | 280.0769 | 22.33 | 75.33 | 97.66
116 | 78 | Equipment test Fast food RestaurantCZ-6 high Process load | 0089 CZ06 QSRest ProsLoad5h | 6697483.3563 | 1123826.6026 | 49713.001 | 125282.4495 | 51788.7202 | 641567.8409 | 0 | 102752.8397 | 0 | 62650.7029 | 90080.5265 | 270522.2222 | 2008.1713 | 2678.0432 | 108.1705 | 0.80298 | 449.3712 | 19.8781 | 50.0952 | 20.7081 | 256.5361 | 0 | 41.0866 | 0 | 25.0514 | 36.0194 | -3.396% | -2.925% | 2500.8869 | 2000.9033 | 280.0769 | 21.17 | 73 | 94.17
117

## ConstructionAssembly
Name | Layers | Overall U Value-CZ1 | Overall U Value-CZ6 | Overall U Value-CZ7 | Overall U Value-CZ15 | Overall U Value-CZ16 | Material Name | Thickness(in) | Conductivity (Btu.in/hft2.F) | Density(lb/ft³) | Specific Heat (Btu/lb.F) | Rvalue (ft2.F.hr/Btu)
T24NRWallMetalFrame |  | 0.098 | 0.098093 | 0.098093 | 0.061991 | 0.061991 | 7/8in layer of Stucco | 0.875 | 4.9931 | 115.866 | 0.20063
Outside Layer | 7/8in layer of Stucco | [5 empty] | Building Paper |  |  |  |  | 0.06
Layer 2 | Building Paper | [5 empty] | Ins&Framing-MetalFramedWall |  |  |  |  | varies with CZ(R-14.59 for overall U value 0.062 & R-8.66 for overall U 0.098)
Layer 3 | Ins&Framing-MetalFramedWall | [5 empty] | Gypsum Board 1/2in | 0.45 | 1.1096 | 50 | 0.26051
Layer 4 | Gypsum Board 1/2in | [5 empty] | T24 NR Metal Roofing | 0.031496 | 314.0083 | 488.436 | 0.11942
T24NRRoofMetal |  | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | Ins&Framing-MetalBldgRoof |  |  |  |  | 14.6046
Outside Layer | T24 NR Metal Roofing | [5 empty] | 100mmNWConcrete | 4 | 16.0194 | 144.9578 | 0.19885
Layer 2 | Ins&Framing-MetalBldgRoof | [5 empty] | CarpetPad |  |  |  |  | 2.08
T24Basement_wall | [6 empty] | Acoustic Tile | 0.5 | 0.39528 | 17.9793 | 0.32003
Outside Layer | T24BwallInsulation | [5 empty] | T24BwallInsulation |  |  |  |  | 0.0056783
Layer 2 | T24 200mm concrete block basement wall | [5 empty] | T24 200mm concrete block basement wall | 8 | 9.0846 | 140.026 | 0.20005
Int_wall | [6 empty] | T24BfloorInsulation |  |  |  |  | 0.028391
Outside Layer | Gypsum Board 1/2in | [5 empty] | T24 200mm NW Concrete | 8 | 9.0846 | 140.026 | 0.20005
Layer 2 | Gypsum Board 1/2in | [5 empty] | T24 150mm concrete floor | 6 | 9.0846 | 2243 | 0.20005
Int_slab_floor | [6 empty] | T24 NR Built-up roofing | 0.37402 | 1.1096 | 69.9194 | 0.34895
Outside Layer | 100mmNWConcrete | [5 empty] | T24NRRoofInsAboveDeck |  |  |  |  | 0
Layer 2 | CarpetPad | [5 empty] | T24NRRoofInsAboveDeckDC |  |  |  |  | CZ6-R-0.4, CZ-16-R-0.8
Drop Ceiling | [6 empty] | T24 F08 Metal surface | 0.031496 | 314.0083 | 488.4367 | 0.1195
Outside Layer | Acoustic Tile | [5 empty] | 1in layer of Stucco | 1 | 4.9931 | 115.866 | 0.20063
T24Floor_with_carpet | [6 empty] | Ins-HeavyMassWall |  |  |  |  | CZ6-R-8.2, CZ 15&16-R-14.12
Outside Layer | T24 200mm concrete floor | [5 empty] | Ins-WoodRoof |  |  |  |  | 12.29
Layer 2 | CarpetPad | [5 empty] | T24NRWoodShingles | 0.25197 | 0.27739 | 36.9574 | 0.31071
T24BFloor_with_carpet | [6 empty] | T2425mm Wood | 1 | 1.0402 | 37.9562 | 0.38958
Outside Layer | T24BfloorInsulation
Layer 2 | T24 200mm concrete floor
Layer 3 | CarpetPad
T24NRRoofInsAboveDeck |  | NA | 0.708 | NA | NA | 0.708
Outside Layer | T24 NR Built-up roofing
Layer 2 | T24NRRoofInsAboveDeck
Layer 3 | T24 F08 Metal surface
DropCeiling2
Outside Layer | T24NRRoofInsAboveDeckDC
Layer 2 | Acoustic Tile
T24NRWallMassHeavy |  |  | 0.098 |  | 0.062 | 0.062
Outside Layer | 1 in layer of Stucco
Layer 2 | T24 200mm NW Concrete Wall
Layer 3 | Ins- HeavyMassWall
Layer 4 | Gypsum Board 1/2in
T24NRRoofWood |  |  | 0.065 |  | 0.065 | 0.065
Outside Layer | T24NRWoodShingles
Layer 2 | T2425mm Wood
Layer 3 | Ins-WoodRoof
Layer 4 | Gypsum Board 1/2in

## Zonelvl
LARGE OFFICE
Baseline Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2
| PerimeterSouthZones | 1967.9098 | 1405.715 | 0 | in Prim.Daylit zone, 8.2 ft from exterior wall | in Sec.Daylit zone, 14.8 ft from exterior wall | 0.58332 | 0.41668 | 450 lux | 1800 lux
| PerimeterEastZones | 1311.9399 | 862.1548 | 0 | in Prim.Daylit zone, 8.2 ft from exterior wall | in Sec.Daylit zone, 14.8 ft from exterior wall | 0.60344 | 0.39656 | 450 lux | 1800 lux
| PerimeterNorthZones | 1967.9098 | 1405.715 | 0 | in Prim.Daylit zone, 8.2 ft from exterior wall | in Sec.Daylit zone, 14.8 ft from exterior wall | 0.58334 | 0.41666 | 450 lux | 1800 lux
| PerimeterWestZones | 1311.9399 | 862.1548 | 0 | in Prim.Daylit zone, 8.2 ft from exterior wall | in Sec.Daylit zone, 14.8 ft from exterior wall | 0.60344 | 0.39656 | 450 lux | 1800 lux
WWR20 Case Daylighting | PerimeterSouthZones | 1343.8462 | 1343.8462 | 0 | in Prim.Daylit zone, 5.6 ft from exterior wall | in Sec.Daylit zone, 11.2 ft from exterior wall | 0.39834 | 0.39834 | 450 lux | 1800 lux
| PerimeterEastZones | 895.8975 | 895.8975 | 0 | in Prim.Daylit zone, 5.6 ft from exterior wall | in Sec.Daylit zone, 11.2 ft from exterior wall | 0.41208 | 0.41208 | 450 lux | 1800 lux
| PerimeterNorthZones | 1343.8462 | 1343.8462 | 0 | in Prim.Daylit zone, 5.6 ft from exterior wall | in Sec.Daylit zone, 11.2 ft from exterior wall | 0.39834 | 0.39834 | 450 lux | 1800 lux
| PerimeterWestZones | 895.8975 | 895.8975 | 0 | in Prim.Daylit zone, 5.6 ft from exterior wall | in Sec.Daylit zone, 11.2 ft from exterior wall | 0.41208 | 0.41208 | 450 lux | 1800 lux
WWR60 Case Daylighting | PerimeterSouthZones | 2015.9268 | 1357.698 | 0 | in Prim.Daylit zone, 8.2 ft from exterior wall | in Sec.Daylit zone, 14.8 ft from exterior wall | 0.59756 | 0.40244 | 450 lux | 1800 lux
| PerimeterEastZones | 1343.9512 | 830.1434 | 0 | in Prim.Daylit zone, 8.2 ft from exterior wall | in Sec.Daylit zone, 14.8 ft from exterior wall | 0.61817 | 0.38183 | 450 lux | 1800 lux
| PerimeterNorthZones | 2015.9268 | 1357.698 | 0 | in Prim.Daylit zone, 8.2 ft from exterior wall | in Sec.Daylit zone, 14.8 ft from exterior wall | 0.59756 | 0.40244 | 450 lux | 1800 lux
| PerimeterWestZones | 1343.9512 | 830.1434 | 0 | in Prim.Daylit zone, 8.2 ft from exterior wall | in Sec.Daylit zone, 14.8 ft from exterior wall | 0.61817 | 0.38183 | 450 lux | 1800 lux
STAND ALONE RETAIL
Name | Area [ft2] | Conditioned
BACK_SPACE | 4089 | Yes
CORE_RETAIL | 17227 | Yes
POINT_OF_SALE | 1623 | Yes
FRONT_RETAIL | 1623 | Yes
FRONT_ENTRY | 129 | Yes
Conditioned Total | 24692
Unconditioned Total | 0
Baseline Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2 | SRR3.04 Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2
| Core_Retail | NA | NA | 1024 | UnderSkylight | UnderSkylight | 0.05944 | 0.05944 | 950 lux | 950 lux |  | Core_Retail | NA | NA | 1149.44 | UnderSkylight | UnderSkylight | 0.066722 | 0.066722 | 950 lux | 950 lux
| Point_Of_Sale | 717.0473 | 717.0473 | NA | In Prim. Daylit Zn | In Sec. daylit Zone | 0.44172 | 0.44172 | 950 lux | 3800 lux |  | Point_Of_Sale | 717.0473 | 717.0473 | NA | In Prim. Daylit Zn | In Sec. daylit Zone | 0.44172 | 0.44172 | 950 lux | 3800 lux
| Front_Retial | 717.0473 | 717.0473 | NA | In Prim. Daylit Zn | In Sec. daylit Zone | 0.44172 | 0.44172 | 950 lux | 3800 lux |  | Front_Retial | 717.0473 | 717.0473 | NA | In Prim. Daylit Zn | In Sec. daylit Zone | 0.44172 | 0.44172 | 950 lux | 3800 lux
| Front_Entry | 85.9294 | 12.5006 | NA | In Prim. Daylit Zn | NA | 0.66526 | NA | 950 lux | NA |  | Front_Entry | 85.9294 | 12.5006 | NA | In Prim. Daylit Zn | NA | 0.66526 | NA | 950 lux | NA
Baseline Skylight Layout | [10 empty] | TestCase Skylight Layout
STRIP MALL
Name | Area [ft2] | Conditioned
LGSTORE1 | 3750.0388 | Yes
SMSTORE1 | 1874.9656 | Yes
SMSTORE2 | 1874.9656 | Yes
SMSTORE3 | 1874.9656 | Yes
SMSTORE4 | 1874.9656 | Yes
LGSTORE2 | 3750.0388 | Yes
SMSTORE5 | 1874.9656 | Yes
SMSTORE6 | 1874.9656 | Yes
SMSTORE7 | 1874.9656 | Yes
SMSTORE8 | 1874.9656 | Yes
Total | 18749.7632
Conditioned Total | 18749.7632
Unconditioned Total | 0

## Schedules
Input | Schedule | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Small Office Hourly Operation Schedules
Interior Light | T24BLDG_LIGHT_SCH | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | T-24 BLDG_EQUIP_SCH_ADV | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupancy | T24 BLDG_OCC_SCH | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5
|  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  | Sunday, Holiday, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Service Hot Water | T24 BLDG_SWH_SCH | WD, SummerDesignDay | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  | Saturday, WinterDesignDay | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Envelope Infiltration | T24 INFIL_SCH | WD, SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  | Saturday, WinterDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sunday, Holiday, Other | bar: 1 to 24
Door Infiltration | INFIL_Door_Opening_SCH | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
|  | Saturday, Sun,Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC Fan operation | T24 HVACOperationSchd | WD, SummerDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
| (Fan Schedule) | Saturday,WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sunday, Holiday, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating Setpoint | T24 HTGSETP_SCH | WD | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556 | Heating | WD | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  | Saturday | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 |  | Sat | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60
|  | Sunday, Holiday, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 |  | Sun | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | SummerDesignDay | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  | WinterDesignDay | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
Cooling Setpoint | T24 CLGSETP_SCH | WD | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444 | Cooling | WD | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  | Saturday | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 |  | Sat | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 85
|  | Sunday, Holiday, Other | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 |  | Sun | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  | SummerDesignDay | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
|  | WinterDesignDay | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
Medium Office Hourly Operation Schedules
Input | Schedule | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Interior Light | T24BLDG_LIGHT_SCH | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
fraction |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | T-24 BLDG_EQUIP_SCH_ADV | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
fraction |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupancy | T24 BLDG_OCC_SCH | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5
fraction |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  | Sunday, Holiday, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Service Hot Water | T24 BLDG_SWH_SCH | WD, SummerDesignDay | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
fraction |  | Saturday, WinterDesignDay | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
temperature(C) | Hot Water Setpoint Temperature Schedule | WD | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22
|  | Sat | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22
|  | Sun | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22
Envelope Infiltration | T24 INFIL_SCH | WD, SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
fraction |  | Saturday, WinterDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sunday, Holiday, Other | bar: 1 to 24
Door Infiltration | INFIL_Door_Opening_SCH | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
fraction |  | Saturday, Sun,Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC Fan operation | T24 HVACOperationSchd | WD, SummerDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
fraction | (Fan Schedule) | Saturday,WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sunday, Holiday, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating Setpoint (◦C) | T24 HTGSETP_SCH | WD | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556
temperature |  | Saturday | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  | Sunday, Holiday, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  | SummerDesignDay | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  | WinterDesignDay | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
Cooling Setpoint(◦C) | T24 CLGSETP_SCH | WD | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444
temperature |  | Saturday | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444
|  | Sunday, Holiday, Other | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444
|  | SummerDesignDay | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
|  | WinterDesignDay | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
Large Office Operation Schedules
Input | Schedule | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Interior Light | T24BLDG_LIGHT_SCH | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
fraction |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | T-24 BLDG_EQUIP_SCH_ADV | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
fraction |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupancy | T24 BLDG_OCC_SCH | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.5
fraction |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  | Sunday, Holiday, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Service Hot Water | T24 BLDG_SWH_SCH | WD, SummerDesignDay | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
fraction |  | Saturday, WinterDesignDay | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sunday, Holiday, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
temperature(C) | Hot Water Setpoint Temperature Schedule | WD | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22
|  | Sat | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22
|  | Sun | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22 | 57.22
Envelope Infiltration | T24 INFIL_SCH | WD, SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
fraction |  | Saturday, WinterDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sunday, Holiday, Other | bar: 1 to 24
HVAC Fan operation | T24 HVACOperationSchd | WD, SummerDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
fraction | (Fan Schedule) | Saturday,WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sunday, Holiday, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating Setpoint(◦C) | T24 HTGSETP_SCH | WD | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556
temperature |  | Saturday | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  | Sunday, Holiday, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  | SummerDesignDay | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  | WinterDesignDay | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
Cooling Setpoint(◦C) | T24 CLGSETP_SCH | WD | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444
temperature |  | Saturday | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444
|  | Sunday, Holiday, Other | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444
|  | SummerDesignDay | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
|  | WinterDesignDay | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
Stand Alone Retail Hourly Operation Schedules
Input | Schedule | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Interior Lighting | T24AssemblyLightSch | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.35 | 0.35 | 0.35 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.25 | 0.05
fraction |  | SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat. | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05
|  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.05 | 0.05
| T24RetailLightSch | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05
|  | Sat. | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inerior Equipment | T24RetailReceptacleSch | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05
fraction |  | SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat. | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| T24AssemblyReceptacleSch | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.25 | 0.05
|  | Sat. | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.05
|  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupancy | T24RetailOccupancySch | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
fraction |  | SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
| T24AssemblyOccupancySch | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0
|  | Sat. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.1 | 0
|  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Service Hot Water | BLDG_SWH_SCH | WD, SummerDesign | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.04 | 0.04 | 0.04
fraction |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.06 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.06 | 0.06
|  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
temperature(F) | Hot Water Setpoint Temperature Schedule | WD | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F
|  | Sat | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F
|  | Sun | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F | 135F
Infiltration | T24RetailInfiltrationSch | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
fraction |  | Sat, WinterDesign | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| T24AssemblyInfiltrationSch | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1
|  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1
|  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1
HVACOperation | T24RetailHVACAvailSch | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
fraction | (FAN_SCH) | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| T24AssemblyHVACAvailSch | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
|  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
|  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
Heating Setpoint(◦C) | T24RetailHtgSetPtSch | WD, WinterDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556 | 15.5556
temperature |  | SummerDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  | Sat | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556
|  | Sun, Hol, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
| T24AssemblyHtgSetPtSch | WD, WinterDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556
|  | SummerDesign | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  | Sat | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556
|  | Sun, Hol, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556
Cooling Setpoint (◦C) | T24RetailClgSetPtSch | WD, SummerDesign | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444 | 29.4444
temperature |  | WinterDesign | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
|  | Sat | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444
|  | Sun, Hol, Other | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444
| T24AssemblyClgSetPtSch | WD, SummerDesign | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444
|  | WinterDesign | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
|  | Sat | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444
|  | Sun, Hol, Other | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444
Quick Service Restaurant Hourly Operation Schedules
Input | Schedule | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Interior Light | T24RestaurantLightSch | WD | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
|  | Sun, Hol, Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | T24RestaurantReceptacleSch | WD | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  | Sun, Hol, Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
|  | SummerDesign | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas Equipment | T24RestaurantGasSch | WD | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
|  | Sat | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.5
|  | Sun, Hol, Other | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.5 | 0.5
|  | SummerDesign | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupancy | T24RestaurantOccupancySch | WD | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  | Sat | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  | Sun, Hol, Other | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | Exterior_lighting_schedule_a | All Days | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Exterior_lighting_schedule_b | All Days | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Service Hot Water | BLDG_SWH_SCH | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Envelope Infiltration | T24RestaurantInfiltrationSch | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Sat, WinterDesign | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HVAC Availability | T24RestaurantHVACAvailSch | WD, SummerDesign | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| (FAN_SCH) | Sat, WinterDesign | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Sun, Hol, Other | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Heating Setpoint | T24RestaurantHtgSetPt | WD, WinterDesign | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
|  | SummerDesign | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
|  | Sun, Hol, Other | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
Cooling Setpoint | T24RestaurantClgSetPt | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
|  | Sat | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
|  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
Exhaust Fan | T24RestExhtSch | All Days | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Strip Mall Hourly Operation Schedules
Input | Schedule | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Interior Lighting | T24RetailLightSch | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05
fraction |  | Sat. | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inerior Equipment | T24RetailReceptacleSch | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05
fraction |  | SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat. | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Occupancy | T24RetailOccupancySch | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
fraction |  | SummerDesign | bar: 1 to 24
|  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sat. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
Infiltration | T24RetailInfiltrationSch | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
fraction |  | Sat, WinterDesign | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HVACOperation | T24RetailHVACAvailSch | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
fraction | (FAN_SCH) | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating Setpoint(◦C) | T24RetailHtgSetPtSch | WD, WinterDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556 | 15.5556
temperature |  | SummerDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  | Sat | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556
|  | Sun, Hol, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
Cooling Setpoint(◦C) | T24RetailClgSetPtSch | WD, SummerDesign | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444 | 29.4444
temperature |  | WinterDesign | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
|  | Sat | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444
|  | Sun, Hol, Other | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444 | 29.4444

## Test Criteria
| 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106
Test Run Name | 01CZ15StandAloneRetail-EnvelopeRoofInsulation | 02CZ15StandAloneRetail Envelope WallInsulation | 03CZ15StandAloneRetail Envelope Heavy | 04CZ16StandAloneRetail Envelope RoofInsulation | 05CZ16StandAloneRetail Envelope WallInsulation | 06CZ16StandAloneRetail Envelope Heavy | 07CZ06StandAloneRetail Envelope RoofInsulation | 08CZ06StandAloneRetail Envelope WallInsulation | 09CZ06StandAloneRetail Envelope Heavy | 10CZ15MediumOffice Envelope FloorslabInsulation | 11CZ15MediumOffice Envelope Infiltration | 12CZ15MediumOffice Glazing WindowU | 13CZ15MediumOffice Glazing WindowSHGC | 14CZ15MediumOffice Glazing WindowUSHGC | 15CZ16MediumOffice Envelope FloorslabInsulation | 16CZ16MediumOffice Envelope Infiltration | 17CZ16MediumOffice Glazing WindowU | 18CZ16MediumOffice Glazing WindowSHGC | 19CZ16MediumOffice Glazing WindowUSHGC | 20CZ06MediumOffice Envelope FloorslabInsulation | 21CZ06MediumOffice Envelope Infiltration | 22CZ06MediumOffice Glazing WindowU | 23CZ06MediumOffice Glazing WindowSHGC | 24CZ06MediumOffice Glazing WindowUSHGC | 25CZ07LargeOffice WWR20% | 26CZ07LargeOffice WWR60% | 27CZ07LargeOffice Glazing WWR60%SouthOverhang | 28CZ01LargeOffice WWR20% | 29CZ01LargeOffice WWR60% | 30CZ15MediumOffice Lighting LowLPD | 31CZ15MediumOffice Lighting HIghLPD | 32CZ16MediumOffice Lighting LowLPD | 33CZ16MediumOffice Lighting HIghLPD | 34CZ06MediumOffice Lighting LowLPD | 35CZ06MediumOffice Lighting HIghLPD | 36CZ15MediumOffice Int.Eqpt LowEPD | 37CZ15MediumOffice Int.Eqpt HighEPD | 38CZ16MediumOffice Int.Eqpt LowEPD | 39CZ16MediumOffice Int.Eqpt HighEPD | 40CZ06MediumOffice Int.Eqpt LowEPD | 41CZ06MediumOffice Int.Eqpt HighEPD | 42CZ07LargeOffice Daylighting Cont.DimHighVT | 43CZ07LargeOffice Daylighting StepDim | 44CZ07LargeOffice Daylighting StepDimHighVT | 45CZ07LargeOffice Daylighting WWR20Cont.DimHighVT | 46CZ07LargeOffice Daylighting WWR20StepDim | 47CZ07LargeOffice Daylighting WWR20StepDimHighVT | 48CZ07LargeOffice Daylighting WWR60Cont.DimHighVT | 49CZ07LargeOffice Daylighting WWR60StepDim | 50CZ07LargeOffice Daylighting WWR60StepDimHighVT | 51CZ01LargeOffice Daylighting Cont.DimHighVT | 52CZ01LargeOffice Daylighting StepDim | 53CZ01LargeOffice Daylighting StepDimHighVT | 54CZ01LargeOffice Daylighting WWR20Cont.DimHighVT | 55CZ01LargeOffice Daylighting WWR20StepDim | 56CZ01LargeOffice Daylighting WWR20StepDimHighVT | 57CZ01LargeOffice Daylighting WWR60Cont.DimHighVT | 58CZ01LargeOffice Daylighting WWR60StepDim | 59CZ01LargeOffice Daylighting WWR60StepDimHighVT | 60CZ07StandAloneRetail Daylighting SRRBaseHighVT | 61CZ07StandAloneRetail Daylighting SRR3.04 | 62CZ07StandAloneRetail Daylighting SRR3.04HighVT | 63CZ01StandAloneRetail Daylighting SRRBaseHighVT | 64CZ01StandAloneRetail Daylighting SRR3.04 | 65CZ01StandAloneRetail Daylighting SRR3.04HighVT | 66CZ16StandAloneRetail HVAC DuctLoss | 67CZ06StandAloneRetail HVAC DuctLoss | 68CZ15MediumOffice HVACPVAV Design | 69CZ15MediumOffice HVACPVAV SATControl | 70CZ15MediumOffice HVACPVAV VAVControl | 71CZ15MediumOffice HVACPVAV EconomizerType | 72CZ16MediumOffice HVACPVAV Design | 73CZ16MediumOffice HVACPVAV SATControl | 74CZ16MediumOffice HVACPVAV VAVControl | 75CZ16MediumOffice HVACPVAV EconomizerType | 76CZ06MediumOffice HVACPVAV Design | 77CZ06MediumOffice HVACPVAV SATControl | 78CZ06MediumOffice HVACPVAV VAVControl | 79CZ06MediumOffice HVACPVAV EconomizerType | 80CZ15LargeOffice HVACVAV ChillerCOP | 81CZ15LargeOffice HVACVAV CHWdeltaT | 82CZ15LargeOffice HVACVAV CWSetpoint | 83CZ15LargeOffice HVACVAV TowerEff | 84CZ16LargeOffice HVACVAV ChillerCOP | 85CZ16LargeOffice HVACVAV CHWdeltaT | 86CZ16LargeOffice HVACVAV CWSetpoint | 87CZ16LargeOffice HVACVAV TowerEff | 88CZ06LargeOffice HVACVAV ChillerCOP | 89CZ06LargeOffice HVACVAV CHWdeltaT | 90CZ06LargeOffice HVACVAV CWSetpoint | 91CZ06LargeOffice HVACVAV TowerEff | 92CZ15StripMall HVACPSZ DXCOP | 93CZ15StripMall HVACPSZ HeatEff | 94CZ15StripMall HVACPSZ EconomizerControl | 95CZ16StripMall HVACPSZ DXCOP | 96CZ16StripMall HVACPSZ HeatEff | 97CZ16StripMall HVACPSZ EconomizerControl | 98CZ06StripMall HVACPSZ DXCOP | 99CZ06StripMall HVACPSZ HeatEff | 100CZ06StripMall HVACPSZ EconomizerControl | 101CZ15StripMall HVACPTAC DXCOP | 102CZ16StripMall HVACPTAC DXCOP | 103CZ06StripMall HVACPTAC DXCOP | 104CZ15StripMall HVACPTAC vsFanCoil | 105CZ16StripMall HVACPTAC vsFanCoil | 106CZ06StripMall HVACPTAC vsFanCoil
Baseline | CZ15StandAloneRetail | CZ15StandAloneRetail | CZ15StandAloneRetail | CZ16StandAloneRetail | CZ16StandAloneRetail | CZ16StandAloneRetail | CZ06StandAloneRetail | CZ06StandAloneRetail | CZ06StandAloneRetail | CZ15MediumOffice | CZ15MediumOffice | CZ15MediumOfficeBaseline | CZ15MediumOfficeBaseline | CZ15MediumOfficeBaseline | CZ16MediumOffice | CZ16MediumOffice | CZ16MediumOfficeBaseline | CZ16MediumOfficeBaseline | CZ16MediumOfficeBaseline | CZ06MediumOffice | CZ06MediumOffice | CZ06MediumOffice | CZ06MediumOffice | CZ06MediumOffice | CZ07LargeOffice | CZ07LargeOffice | CZ07LargeOffice | CZ01LargeOffice | CZ01LargeOffice | CZ15MediumOffice | CZ15MediumOffice | CZ16MediumOffice | CZ16MediumOffice | CZ06MediumOffice | CZ06MediumOffice | CZ15MediumOffice | CZ15MediumOffice | CZ16MediumOffice | CZ16MediumOffice | CZ06MediumOffice | CZ06MediumOffice | CZ07LargeOffice | CZ07LargeOffice | CZ07LargeOffice | 25CZ07LargeOffice WWR20% | 25CZ07LargeOffice WWR20% | 25CZ07LargeOffice WWR20% | 26CZ07LargeOffice WWR60% | 26CZ07LargeOffice WWR60% | 26CZ07LargeOffice WWR60% | CZ01LargeOffice | CZ01LargeOffice | CZ01LargeOffice | 28CZ07LargeOffice WWR20% | 28CZ07LargeOffice WWR20% | 28CZ07LargeOffice WWR20% | 29CZ07LargeOffice WWR60% | 29CZ07LargeOffice WWR60% | 29CZ07LargeOffice WWR60% | CZ07StandAloneRetail | CZ07StandAloneRetail | CZ07StandAloneRetail | CZ01StandAloneRetail | CZ01StandAloneRetail | CZ01StandAloneRetail | CZ16StandAloneRetailDuctlossBaseline | CZ06StandAloneRetailDuctlossBaseline | CZ15MediumOffice | CZ15MediumOffice | CZ15MediumOffice | CZ15MediumOffice | CZ16MediumOffice | CZ16MediumOffice | CZ16MediumOffice | CZ16MediumOffice | CZ06MediumOffice | CZ06MediumOffice | CZ06MediumOffice | CZ06MediumOffice | CZ15LargeOffice | CZ15LargeOffice | CZ15LargeOffice | CZ15LargeOffice | CZ16LargeOffice | CZ16LargeOffice | CZ16LargeOffice | CZ16LargeOffice | CZ06LargeOffice | CZ06LargeOffice | CZ06LargeOffice | CZ06LargeOffice | CZ15StripMall PSZ | CZ15StripMall PSZ | CZ15StripMall PSZ | CZ16StripMall PSZ | CZ16StripMall PSZ | CZ16StripMall PSZ | CZ06StripMall PSZ | CZ06StripMall PSZ | CZ06StripMall PSZ | CZ15StripMall PTAC | CZ16StripMall PTAC | CZ06StripMall PTAC | CZ15StripMall PTAC | CZ16StripMall PTAC | CZ06StripMall PTAC
Test Description | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Change Roof and Wall construction asssembly to Wood Framed Roof and Heavy Mass wall. Roof and Wall assembly overall U value of test case= Baseline construction assembly U value | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Change Roof and Wall construction asssembly to Wood Framed Roof and Heavy Mass wall. Roof and Wall assembly overall U value of test case= Baseline construction assembly U value | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Change Roof and Wall construction asssembly to Wood Framed Roof and Heavy Mass wall. Roof and Wall assembly overall U value of test case= Baseline construction assembly U value | Change Floor slab F factor of permiter zones in the bottom floor to 0.45 | Increase Exterior Wall Infiltration by 10% compared to baseline case | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case | Change Floor slab F factor of permiter zones in the bottom floor to 0.45 | Increase Exterior Wall Infiltration by 10% compared to baseline case | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case | Change Floor slab F factor of permiter zones in the bottom floor to 0.45 | Increase Exterior Wall Infiltration by 10% compared to baseline case | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case | Reduce window area such that overall window to wall ratio is 20% | Increase window area such that overall window to wall ratio is 60% | Increase window area such that overall window to wall ratio is 60%. Include horizontal overhang of two feet for all south facing windows | Reduce window area such that overall window to wall ratio is 20% | Increase window area such that overall window to wall ratio is 60% | Decrease LPD by 20% compared to baseline case | Increase LPD by 20% compared to baseline case | Decrease LPD by 20% compared to baseline case | Increase LPD by 20% compared to baseline case | Decrease LPD by 20% compared to baseline case | Increase LPD by 20% compared to baseline case | Decrease EPD by 20% compared to baseline case | Increase EPD by 20% compared to baseline case | Decrease EPD by 20% compared to baseline case | Increase EPD by 20% compared to baseline case | Decrease EPD by 20% compared to baseline case | Increase EPD by 20% compared to baseline case | Increase Visible Transmittance of windows by 20% compared to baseline case | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20% | Increase Visible Transmittance of windows by 20% compared to baseline case. Reduce window area such that overall window to wall ratio is 20% Note for this test, Run 25CZ07LargeOfficeWWR20% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps.Reduce window area such that overall window to wall ratio is 20% Note for this test, Run 25CZ07LargeOfficeWWR20% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20%. Reduce window area such that overall window to wall ratio is 0.2 Note for this test, Run 25CZ07LargeOfficeWWR0.2 is the baseline | Increase Visible Transmittance of windows by 20% compared to baseline case. Reduce window area such that overall window to wall ratio is 60% Note for this test, Run 26CZ07LargeOfficeWWR60% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps.Reduce window area such that overall window to wall ratio is 60% Note for this test, Run 26CZ07LargeOffice WWR60% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20%. Reduce window area such that overall window to wall ratio is 60% Note for this test, Run 26CZ07LargeOffice WWR60% is the baseline | Increase Visible Transmittance of windows by 20% compared to baseline case | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20% | Increase Visible Transmittance of windows by 20% compared to baseline case. Reduce window area such that overall window to wall ratio is 20% Note for this test, Run 28CZ07LargeOffice Galzing WWR20% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps.Reduce window area such that overall window to wall ratio is 20% Note for this test, Run 28CZ07LargeOfficeWWR20% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20%. Reduce window area such that overall window to wall ratio is 20% Note for this test, Run 28CZ07LargeOffice WWR20% is the baseline | Increase Visible Transmittance of windows by 20% compared to baseline case. Reduce window area such that overall window to wall ratio is 60% Note for this test, Run 29CZ07LargeOffice WWR60% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps.Reduce window area such that overall window to wall ratio is 60% Note for this test, Run 29CZ07LargeOffice WWR60% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20%. Reduce window area such that overall window to wall ratio is 60% Note for this test, Run 29CZ07LargeOffice WWR60% is the baseline | Increase Visible Transmittance of skylights by 20% compared to baseline case | Increase skylight area such that overall skylight to roof ratio is 3.04. | Increase skylight area such that overall skylight to roof ratio is 3.04 and visible transmittance of skylights by 20% compared to baseline case. | Increase Visible Transmittance of skylights by 20% compared to baseline case | Increase skylight area such that overall skylight to roof ratio is 3.04. | Increase skylight area such that overall skylight to roof ratio is 3.04 and visible transmittance of skylights by 20% compared to baseline case | Increase ductloss in the zones served by Pacakaged Single Zone systems to 14%. The baseline for this test is a modified version of Stand-Alone Retail prototype. See details below | Increase ductloss in the zones served by Pacakaged Single Zone systems to 14%. The baseline for this test is a modified version of Stand-Alone Retail prototype. See details below | Change static pressure and motor efficiency of all VAV fans. See details below | Change supply air temperature reset based on Outside air. See details below | Change VAV damper control to dual maximum. | Change Economizer Type to Fixed Dry bulb with 70 F high limit | Change static pressure and motor efficiency of all VAV fans. See details below | Change supply air temperature reset based on Outside air. See details below | Change VAV damper control to dual maximum. | Change Economizer Type to Fixed Dry bulb with 70 F high limit | Change static pressure and motor efficiency of all VAV fans. See details below | Change supply air temperature reset based on Outside air. See details below | Change VAV damper control to dual maximum. | Change Economizer Type to Fixed Dry bulb with 70 F high limit | Increase Chiller COP by 11% compared to baseline case | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 25 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 25 gpm/hp | Increase Chiller COP by 11% compared to baseline case | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 25 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 25 gpm/hp | Increase Chiller COP by 11% compared to baseline case | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 25 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 25 gpm/hp | Increase COP of DX coil to 3.8 | Increase efficiency of the Heating coil to 90% | Change Economizer from Integrated as in baseline to NonIntegrated. See below for details | Increase COP of DX coil to 3.8 | Increase efficiency of the Heating coil to 90% | Change Economizer from Integrated as in baseline to NonIntegrated. See below for details | Increase COP of DX coil to 3.8 | Increase efficiency of the Heating coil to 90% | Change Economizer from Integrated as in baseline to NonIntegrated. See below for details | Increase COP of DX coil to 3.8 | Increase COP of DX coil to 3.8 | Increase COP of DX coil to 3.8 | Comparison of PTAC system with Fan Coil System. For details on Fan Coil system, refer StripMall FanCoil | Comparison of PTAC system with Fan Coil System. For details on Fan Coil system, refer StripMall FanCoil | Comparison of PTAC system with Fan Coil System. For details on Fan Coil system, refer StripMall FanCoil
Location | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ06 | CZ06 | CZ07 | CZ07 | CZ07 | CZ01 | CZ01 | CZ15 | CZ15 | CZ16 | CZ16 | CZ06 | CZ06 | CZ15 | CZ15 | CZ16 | CZ16 | CZ06 | CZ06 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ07 | CZ07 | CZ07 | CZ01 | CZ01 | CZ01 | CZ16 | CZ06 | CZ15 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ06 | CZ15 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ06 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ15 | CZ16 | CZ06 | CZ15 | CZ16 | CZ06
Fuel Type | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer MediumOffice | Refer MediumOffice | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer MediumOffice | Refer MediumOffice | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer MediumOffice | Refer MediumOffice | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail Ductloss Baseline | Refer StandAloneRetail Ductloss Baseline | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC
Total Floor Area (sq feet)
Building shape
Aspect Ratio
Number of Floors
Window Fraction (Window-to-Wall Ratio) | [24 empty] | 20% of above-grade gross wall | 60% of above-grade gross wall | 60% of above-grade gross wall | 20% of above-grade gross wall | 60% of above-grade gross wall | [15 empty] | 20% of above-grade gross wall | 20% of above-grade gross wall | 20% of above-grade gross wall | 60% of above-grade gross wall | 60% of above-grade gross wall | 60% of above-grade gross wall |  |  |  | 20% of above-grade gross wall | 20% of above-grade gross wall | 20% of above-grade gross wall | 60% of above-grade gross wall | 60% of above-grade gross wall | 60% of above-grade gross wall
Window Locations | [24 empty] | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | [15 empty] | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office |  |  |  | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office
Shading Geometry | [26 empty] | 2 feet deep overhang on South windows
Azimuth | [26 empty] | Refer Large Office
Thermal Zoning
Floor to floor height (feet)
Floor to ceiling height (feet)
Glazing sill height (feet)
Exterior walls
Construction |  |  | HeavyMass Wall |  |  | HeavyMass Wall |  |  | HeavyMass Wall
Construction Assembly Layers |  |  | Refer T24NRWallMassHeavy |  |  | Refer T24NRWallMassHeavy |  |  | Refer T24NRWallMassHeavy
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) |  | U=0.050 Btu / h * ft2 * °F | U=0.062 Btu / h * ft2 * °F |  | U=0.050 Btu / h * ft2 * °F | U=0.062 Btu / h * ft2 * °F |  | U=0.078 Btu / h * ft2 * °F | U=0.098 Btu / h * ft2 * °F
Dimensions |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail
Tilts and orientations
Roof
Construction |  |  | Wood Framed Roof |  |  | Wood Framed Roof |  |  | Wood Framed Roof
Construction Assembly Layers |  |  | Refer T24NRRoofWood |  |  | Refer T24NRRoofWood |  |  | Refer T24NRRoofWood
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | U=0.052 Btu / h * ft2 * °F |  | U=0.065 Btu / h * ft2 * °F | U=0.052 Btu / h * ft2 * °F |  | U=0.065 Btu / h * ft2 * °F | U=0.052 Btu / h * ft2 * °F |  | U=0.065 Btu / h * ft2 * °F
Dimensions | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail
Tilts and orientations
Window
Dimensions
Glass-Type and frame
U-factor (Btu / h * ft2 * °F) | [11 empty] | 0.29 |  | 0.29 |  |  | 0.29 |  | 0.29 |  |  | 0.29 |  | 0.29
SHGC | [11 empty] | Refer Medium Office | 0.2 | 0.2 |  |  | Refer Medium Office | 0.2 | 0.2 |  |  | Refer Medium Office | 0.2 | 0.2
Visible transmittance | [12 empty] | Refer Medium Office | Refer Medium Office |  |  |  | Refer Medium Office | Refer Medium Office |  |  |  | Refer Medium Office | Refer Medium Office | [17 empty] | 0.504 |  | 0.504 | 0.504 |  | 0.504 | 0.504 |  | 0.504 | 0.504 |  | 0.504 | 0.504 |  | 0.504 | 0.504 |  | 0.504
Operable area | [41 empty] | Refer Large Office |  | Refer Large Office | Refer Large Office |  | Refer Large Office | Refer Large Office |  | Refer Large Office | Refer Large Office |  | Refer Large Office | Refer Large Office |  | Refer Large Office | Refer Large Office |  | Refer Large Office
Skylight
Dimensions | [60 empty] | Skylight to Roof Ratio- 3.04 Core Retail, Refer Skylight Layout for details | Skylight to Roof Ratio- 3.04 Core Retail, Refer Skylight Layout for details |  | Skylight to Roof Ratio- 3.04 Core Retail, Refer Skylight Layout for details | Skylight to Roof Ratio- 3.04 Core Retail, Refer Skylight Layout for details
Glass-Type and frame | [60 empty] | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail
U-factor (Btu / h * ft2 * °F)
SHGC
Visible transmittance | [59 empty] | 0.588 |  | 0.588 | 0.588 |  | 0.588
Foundation | [59 empty] | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail
Foundation Type
Construction
Construction Assembly Layers
Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | [9 empty] | F factor= 0.45 |  |  |  |  | F factor= 0.45 |  |  |  |  | F factor= 0.45
Thermal properties for basement walls | [9 empty] | Refer MediumOffice |  |  |  |  | Refer MediumOffice |  |  |  |  | Refer MediumOffice
Dimensions
Interior Surfaces
Construction
Construction Assembly Layers
Dimensions
Internal Mass
Air Barrier System
Infiltration | [10 empty] | Peak: 0.2218 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  |  |  | Peak: 0.2218 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  |  |  | Peak: 0.2218 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on)
HVAC System Type | [10 empty] | Refer MediumOffice |  |  |  |  | Refer MediumOffice |  |  |  |  | Refer MediumOffice
System Type
Heating type
Cooling type
Distribution and terminal units | [65 empty] | 3 single-zone roof top units serving thermal zones back_space, point_of_sale, and front_retail with Duct loss - 14% of design flow rate. | 3 single-zone roof top units serving thermal zones back_space, point_of_sale, and front_retail with Duct loss - 14% of design flow rate. |  |  | Dual- max control on all VAV dampers |  |  |  | Dual- max control on all VAV dampers |  |  |  | Dual- max control on all VAV dampers
HVAC Sizing | [65 empty] | Refer StandAloneRetail Ductloss Baseline | Refer StandAloneRetail Ductloss Baseline |  |  | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | Refer Medium Office
Cooling
Heating
HVAC Efficiency
Cooling | [79 empty] | Chiller COP -6.8 |  |  |  | Chiller COP -6.8 |  |  |  | Chiller COP -6.8 |  |  |  | 3.8 (COP)/ 13 (EER) |  |  | 3.8 (COP)/ 13 (EER) |  |  | 3.8 (COP)/ 13 (EER) |  |  | 3.8 (COP)/ 13 (EER) | 3.8 (COP)/ 13 (EER) | 3.8 (COP)/ 13 (EER)
Heating | [79 empty] | Refer Large Office |  |  |  | Refer Large Office |  |  |  | Refer Large Office |  |  |  | Refer StripMall PSZ | 90% |  | Refer StripMall PSZ | 90% |  | Refer StripMall PSZ | 90% |  | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC
HVAC Control | [92 empty] | Refer StripMall PSZ |  |  | Refer StripMall PSZ |  |  | Refer StripMall PSZ
Thermostat Setpoint
Thermostat Setback
Design Supply air temperature
Supply air temperature reset | [68 empty] | Reset by Outdoor Air. Outdoor temperature- max 80F, min 60 F Setpoint at Outdor low- 64.4 F, high- 55.04F |  |  |  | Reset by Outdoor Air. Outdoor temperature- max 80F, min 60 F Setpoint at Outdor low- 64.4 F, high- 55.04F |  |  |  | Reset by Outdoor Air. Outdoor temperature- max 80F, min 60 F Setpoint at Outdor low- 64.4 F, high- 55.04F
Chilled water supply temperatures | [68 empty] | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | 44 F |  |  |  | 44 F |  |  |  | 44 F
Chilled water return temperatures | [80 empty] | 56 F |  |  |  | 56 F |  |  |  | 56 F
Chilled water supply temperature reset | [80 empty] | Refer Large Office |  |  |  | Refer Large Office |  |  |  | Refer Large Office
Condenser Type | [81 empty] | Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature |  |  |  | Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature |  |  |  | Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature
Hot water supply temperatures | [81 empty] | Refer Large Office |  |  |  | Refer Large Office |  |  |  | Refer Large Office
Hot water supply temperature reset
Economizers | [70 empty] | Fixed Dry bulb -70F high limit |  |  |  | Fixed Dry bulb -70F high limit |  |  |  | Fixed Dry bulb -70F high limit | [14 empty] | Non-Integrated Economizer (Diff. DB) Economizer max limit set to 55 F(cooling supply temperature) |  |  | Non-Integrated Economizer (Diff. DB) Economizer max limit set to 55 F(cooling supply temperature) |  |  | Non-Integrated Economizer (Diff. DB) Economizer max limit set to 55 F(cooling supply temperature)
Ventilation | [70 empty] | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | Refer Medium Office | [14 empty] | Refer StripMall PSZ |  |  | Refer StripMall PSZ |  |  | Refer StripMall PSZ
Supply Fan
Fan type
Fan schedules
Supply Fan Total Efficiency (%)
Fan Motor Efficiency | [67 empty] | 93.6% |  |  |  | 93.6% |  |  |  | 93.6%
Supply Fan Pressure Rise | [67 empty] | 4 in H20 |  |  |  | 4 inH20 |  |  |  | 4 in H20
Pump | [67 empty] | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | Refer Medium Office
Pump Type
Rated Pump Head
Pump Power
Pump Efficiency
Cooling Tower
Cooling Tower Type
Tower range
Tower Approach
Design Flow rate
Cooling Tower Efficiency | [82 empty] | 25 gpm/hp |  |  |  | 25 gpm/hp |  |  |  | 25 gpm/hp
Service Water Heating | [82 empty] | Refer Large Office |  |  |  | Refer Large Office |  |  |  | Refer Large Office
SWH type
Fuel type
Thermal efficiency (%)
Peak Use Flow rate (gpm)
Peak Use Flow rate Schedule
Water temperature setpoint
Water temperature setpoint Schedule
Water Heater Max Capacity (Btuh)
Water consumption
Lighting Load
Lighting power density (W/ft2) | [29 empty] | 0.6 W/ft2 | 0.9 W/ft2 | 0.6 W/ft2 | 0.9 W/ft2 | 0.6 W/ft2 | 0.9 W/ft2
Schedule | [29 empty] | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office
Daylighting Controls | [24 empty] | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details | [13 empty] | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | Refer LargeOfficeDaylight for details | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | Refer LargeOfficeDaylight for details | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. |  | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | Refer LargeOfficeDaylight for details | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | Refer LargeOfficeDaylight for details | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. | 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones. |  | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . |  | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry .
[46 empty] | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details |  | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details |  |  |  |  | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details |  | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details |  | Refer StandAloneDaylight for more details | Refer StandAloneDaylight for more details |  | Refer StandAloneDaylight for more details | Refer StandAloneDaylight for more details
Plug load | [24 empty] | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | [13 empty] | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office |  | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office |  | Refer Stand Alone Retail | Refer Stand Alone Retail |  | Refer Stand Alone Retail | Refer Stand Alone Retail
Electric power density (W/ft2) | [35 empty] | 1.2 W/ft2 | 1.8 W/ft2 | 1.2 W/ft2 | 1.8 W/ft2 | 1.2 W/ft2 | 1.8 W/ft2
Schedule | [35 empty] | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office
Occupancy
Average people
Schedule
0.062167
| 0.049734 | 0.052129

## Performance Curve
Performance Curves
The performance curves described below have been used in the prototype models. The coefficients and variable ranges are in S.I units
Prototype | Component | CurveName | Curve Type | Variables |  |  | Coefficients | [9 empty] | Min for Var 2 | Max for Var 2 | Min for Var 3 | Max for Var 3
|  |  |  | Dependant | Independent
|  |  |  | Var1 | Var2 | Var3 | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10
Large Office | Boiler | HeatSys1 Boiler Efficiency Curve | Quadratic | Dependant Var1: FIRRatio; Independent Var2: QRatio; Independent C1: 1; Independent C2: 0; Independent C3: 0 | 0 | 1
Large Office | Chiller | ACMChillerCapFT | Biquadratic | Capacity | Leaving CHW temperature | Leaving CW temperature | 0.98596 | 0.049487 | -0.00029808 | -0.0037368 | -4.536e-05 | -0.0005022 |  |  |  |  | 5 | 20 | 10 | 46.11
Large Office | Chiller | ACMChillerEIRFT | Biquadratic | EIR | Leaving CHW temperature | Leaving CW temperature | 0.57062 | 0.011954 | -0.00052164 | -3.24e-05 | 0.0004212 | -0.00060588 |  |  |  |  | 5 | 20 | 10 | 46.11
Large Office | Chiller | WC_Cent_300TO600_2010_PB_EIRFPLR | Bicubic | EIR | Leaving CW temperature | PartLoadRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 18 | 40.94 | 0.1 | 1
Medium Office | DXCoil | DX Coil Cap-FT | Biquadratic | Capacity | WB temperature | OA DB Temperature | 0.47643 | 0.040115 | 0.00022641 | -0.00082714 | -7.3224e-06 | -0.00044628 |  |  |  |  | 12.78 | 24 | 24 | 46.11
Medium Office | DXCoil | DX Coil Cap-FF | Cubic | Dependant Var1: Capacity; Independent Var2: Flow Fraction; Independent C1: 0.47279; Independent C2: 1.2433; Independent C3: -1.0387; Independent C4: 0.32258 | 0.5 | 1.5
Medium Office | DXCoil | DX Coil EIR-FT | Biquadratic | EIR | WB temperature | OA DB Temperature | 0.63248 | -0.012132 | 0.00050777 | 0.015538 | 0.00027284 | -0.0006792 |  |  |  |  | 12.78 | 24 | 24 | 46.11
Medium Office | DXCoil | DX Coil EIR-FF | Cubic | Dependant Var1: EIR; Independent Var2: Flow Fraction; Independent C1: 1.0079; Independent C2: 0.34544; Independent C3: -0.69229; Independent C4: 0.3389 | 0.5 | 1.5
Medium Office | DXCoil | DX Coil PLF | Quadratic | Dependant Var1: Power; Independent Var2: PLF; Independent C1: 0.85; Independent C2: 0.15; Independent C3: 0 | 0 | 1
MediumOffice | Boiler | Boiler1 Efficiency Curve | Quadratic | Dependant Var1: FIRRatio; Independent Var2: QRatio; Independent C1: 0.97; Independent C2: 0.0633; Independent C3: -0.0333 | 0 | 1
StripMall-PSZ | DXCoil | Unitary_PackagecoolCapFT | Biquadratic | Capacity | WB temperature | OA DB Temperature | 0.76696 | 0.010776 | -4.147e-05 | 0.0013496 | -0.00026114 | 0.00045749 |  |  |  |  | 12.78 | 24 | 21.11 | 46.11
StripMall-PSZ | DXCoil | Unitary_PackagecoolFFF | Quadratic | Dependant Var1: Capacity; Independent Var2: Flow Fraction; Independent C1: 0.8; Independent C2: 0.2; Independent C3: 0 | 0.5 | 1.5
StripMall-PSZ | DXCoil | Unitary_PackagecoolEIRFT | Biquadratic | EIR | WB temperature | OA DB Temperature | 0.29714 | 0.043093 | -0.00074877 | 0.0059773 | 0.00048211 | -0.00095645 |  |  |  |  | 12.78 | 24 | 21.11 | 46.11
StripMall-PSZ | DXCoil | Unitary_PackagecoolEIRFFF | Quadratic | Dependant Var1: EIR; Independent Var2: Flow Fraction; Independent C1: 1.156; Independent C2: -0.1816; Independent C3: 0.0256 | 0.5 | 1.5
StripMall-PSZ | DXCoil | Unitary_PackagecoolPLR | Quadratic | Dependant Var1: Power; Independent Var2: PLF; Independent C1: 0.75; Independent C2: 0.25; Independent C3: 0 | 0 | 1
StripMall- PTAC | DXCoil | PTAC Cooling Coil Cap-FT | Biquadratic | Capacity | WB temperature | OA DB Temperature | 0.94259 | 0.0095433 | 0.00068377 | -0.011043 | 5.249e-06 | -9.72e-06 |  |  |  |  | 12.78 | 24 | 18 | 46.11
StripMall- PTAC | DXCoil | PTAC Cooling Coil Cap-FF | Quadratic | Dependant Var1: Capacity; Independent Var2: Flow Fraction; Independent C1: 0.8; Independent C2: 0.2; Independent C3: 0 | 0.5 | 1.5
StripMall- PTAC | DXCoil | PTAC Cooling Coil EIR-FT | Biquadratic | EIR | WB temperature | OA DB Temperature | 0.34241 | 0.034885 | -0.0006237 | 0.0049772 | 0.00043795 | -0.00072803 |  |  |  |  | 12.78 | 24 | 18 | 46.11
StripMall- PTAC | DXCoil | PTAC Cooling Coil EIR-FF | Quadratic | Dependant Var1: EIR; Independent Var2: Flow Fraction; Independent C1: 1.1552; Independent C2: -0.1808; Independent C3: 0.0256 | 0.5 | 1.5
StripMall- PTAC | DXCoil | PTAC Cooling Coil PLF | Quadratic | Dependant Var1: Power; Independent Var2: PLF; Independent C1: 0.85; Independent C2: 0.15; Independent C3: 0 | 0 | 1
StripMall-FPFC | Chiller | Main Chiller RecipCapFT | Biquadratic | Capacity | Leaving CHW temperature | Leaving CW temperature | 0.50788 | 0.14523 | -0.0062564 | -0.0011178 | -0.0001296 | -0.00028188 |  |  |  |  | 5 | 10 | 24 | 35
StripMall-FPFC | Chiller | Main Chiller RecipEIRFT | Biquadratic | EIR | Leaving CHW temperature | Leaving CW temperature | 1.0308 | -0.10354 | 0.0071021 | 0.0093186 | 0.00031752 | -0.0010433 |  |  |  |  | 5 | 10 | 24 | 35
StripMall-FPFC | Chiller | Main Chiller RecipEIRFPLR | Quadratic | Dependant Var1: EIR; Independent Var2: PartLoadRatio; Independent C1: 0.088065; Independent C2: 1.1377; Independent C3: -0.22581 | 0 | 1
StripMall-FPFC | Boiler | Main Boiler Efficiency Curve | Quadratic | Dependant Var1: FIRRatio; Independent Var2: QRatio; Independent C1: 0.97; Independent C2: 0.0633; Independent C3: -0.0333 | 0 | 1
StandAloneRetail | DXCoil | Unitary_PackagecoolFFF | Quadratic | Dependant Var1: Capacity; Independent Var2: Flow Fraction; Independent C1: 0.8; Independent C2: 0.2; Independent C3: 0 | 0.5 | 1.5
StandAloneRetail | DXCoil | Unitary_PackagecoolEIRFFF | Quadratic | Dependant Var1: EIR; Independent Var2: Flow Fraction; Independent C1: 1.156; Independent C2: -0.1816; Independent C3: 0.0256 | 0.5 | 1.5
StandAloneRetail | DXCoil | Unitary_PackagecoolPLR | Quadratic | Dependant Var1: Power; Independent Var2: PLF; Independent C1: 0.75; Independent C2: 0.25; Independent C3: 0 | 0 | 1
StandAloneRetail | DXCoil | Unitary_PackagecoolCapFT | Biquadratic | Capacity | WB temperature | OA DB Temperature | 0.76696 | 0.010776 | -4.147e-05 | 0.0013496 | -0.00026114 | 0.00045749 |  |  |  |  | 12.78 | 24 | 21.11 | 46.11
StandAloneRetail | DXCoil | Unitary_PackagecoolEIRFT | Biquadratic | EIR | WB temperature | OA DB Temperature | 0.29714 | 0.043093 | -0.00074877 | 0.0059773 | 0.00048211 | -0.00095645 |  |  |  |  | 12.78 | 24 | 21.11 | 46.11