## Results
| TEST RESULTS |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 10 |  | 11 |  | 12 |  | 13 |  |  | 14 |  | 15 | 16
| Test Case |  | Annual TDV EUI |  | EUI- Electricity |  | EUI- Natural Gas |  | Annual Total End Use Site Energy EUI |  | Annual End Use Site Energy EUI | [15 empty] | Variation from Baseline |  |  |  |  | Pass/Fail
|  |  | (kBtu/sqft) |  | (kwh/sqft) |  | (therm/sqft) |  | (kBtu/sqft) |  | Heating (kBtu/sqft) |  | Cooling (kBtu/sqft) |  | Interior Lighting (kBtu/sqft) |  | Interior Equipment (kBtu/sqft) |  | Fans (kBtu/sqft) |  | Pumps (kBtu/sqft) |  | Tower (kBtu/sqft) |  | Water Heating (kBtu/sqft) |  | TDV % variation |  | Total End Use Site Energy % Variation |  |  |  | Reference Model Occupied Unmet Load Hrs | Applicant Model Occupied Unmet Load Hrs
|  |  | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model
3 |  | CZ15StandAloneRetailBaseline | 402.13 |  | 14.89 |  | 0.08 |  | 59.26 |  | 0.89 |  | 18.26 |  | 12.15 |  | 10.73 |  | 9.66 |  | 0 |  | 0 |  | 7.58 | [7 empty] | 677.25
4 | 1 | 01CZ15StandAloneRetail Envelope RoofInsulation | 392.01 |  | 14.5 |  | 0.08 |  | 57.86 |  | 0.82 |  | 17.41 |  | 12.15 |  | 10.73 |  | 9.17 |  | 0 |  | 0 |  | 7.57 |  | 2.52% |  | 2.37% |  | No | Fail | 674.5
5 | 2 | 02CZ15StandAloneRetail Envelope WallInsulation | 399.15 |  | 14.79 |  | 0.08 |  | 58.88 |  | 0.85 |  | 18.03 |  | 12.15 |  | 10.73 |  | 9.55 |  | 0 |  | 0 |  | 7.58 |  | 0.74% |  | 0.64% |  | No | Fail | 676.75
6 | 3 | 03CZ15StandAloneRetail Envelope Heavy | 422.87 |  | 15.61 |  | 0.08 |  | 61.45 |  | 0.62 |  | 20.06 |  | 12.13 |  | 10.73 |  | 10.34 |  | 0 |  | 0 |  | 7.57 |  | -5.16% |  | -3.69% |  | No | Fail | 673.5
7 |  | CZ16StandAloneRetailBaseline | 329.44 |  | 11.65 |  | 0.17 |  | 56.65 |  | 7.18 |  | 4.96 |  | 12.18 |  | 10.73 |  | 11.88 |  | 0 |  | 0 |  | 9.73 | [7 empty] | 676
8 | 4 | 04CZ16StandAloneRetail Envelope RoofInsulation | 322.83 |  | 11.42 |  | 0.17 |  | 55.49 |  | 6.81 |  | 4.74 |  | 12.18 |  | 10.73 |  | 11.31 |  | 0 |  | 0 |  | 9.73 |  | 2.01% |  | 2.04% |  | No | Fail | 822.5
9 | 5 | 05CZ16StandAloneRetail Envelope WallInsulation | 327.62 |  | 11.6 |  | 0.17 |  | 56.2 |  | 6.9 |  | 4.92 |  | 12.18 |  | 10.73 |  | 11.76 |  | 0 |  | 0 |  | 9.73 |  | 0.55% |  | 0.79% |  | No | Fail | 822.25
10 | 6 | 06CZ16StandAloneRetail Envelope Heavy | 338.78 |  | 11.92 |  | 0.16 |  | 56.83 |  | 6.43 |  | 5.54 |  | 12.15 |  | 10.73 |  | 12.25 |  | 0 |  | 0 |  | 9.72 |  | -2.84% |  | -0.32% |  | No | Fail | 821
11 |  | CZ06StandAloneRetailBaseline | 324.87 |  | 11.89 |  | 0.11 |  | 51.13 |  | 1.9 |  | 8.85 |  | 12.11 |  | 10.73 |  | 8.89 |  | 0 |  | 0 |  | 8.65 | [7 empty] | 816.75
12 | 7 | 07CZ06StandAloneRetail Envelope RoofInsulation | 322.23 |  | 11.83 |  | 0.1 |  | 50.84 |  | 1.81 |  | 8.73 |  | 12.11 |  | 10.73 |  | 8.81 |  | 0 |  | 0 |  | 8.65 |  | 0.81% |  | 0.57% |  | No | Fail | 817
13 | 8 | 08CZ06StandAloneRetail Envelope WallInsulation | 323.28 |  | 11.85 |  | 0.1 |  | 50.89 |  | 1.79 |  | 8.8 |  | 12.11 |  | 10.73 |  | 8.81 |  | 0 |  | 0 |  | 8.65 |  | 0.49% |  | 0.48% |  | No | Fail | 245.75
14 | 9 | 09CZ06StandAloneRetail Envelope Heavy | 328.92 |  | 11.96 |  | 0.1 |  | 50.76 |  | 1.3 |  | 9.26 |  | 12.08 |  | 10.73 |  | 8.74 |  | 0 |  | 0 |  | 8.64 |  | -1.25% |  | 0.72% |  | No | Fail | 246.75
15 |  | CZ15MediumOfficeBaseline | 265.68 |  | 10.3 |  | 0.03 |  | 37.83 |  | 0.65 |  | 12.96 |  | 5.78 |  | 14.5 |  | 1.88 |  | 0.04 |  | 0 |  | 2.03 | [7 empty] | 246.5
16 | 10 | 10CZ15MediumOffice Envelope FloorslabInsulation | 267.74 |  | 10.38 |  | 0.03 |  | 38.03 |  | 0.58 |  | 13.19 |  | 5.78 |  | 14.5 |  | 1.92 |  | 0.03 |  | 0 |  | 2.03 |  | -0.77% |  | -0.53% |  | No | Fail | 231.25
17 | 11 | 11CZ15MediumOffice Envelope Infiltration | 266.37 |  | 10.32 |  | 0.03 |  | 37.94 |  | 0.71 |  | 13 |  | 5.78 |  | 14.5 |  | 1.88 |  | 0.04 |  | 0 |  | 2.03 |  | -0.26% |  | -0.29% |  | No | Fail | 250.75
18 |  | CZ15MediumOfficeBaseline | 265.68 |  | 10.3 |  | 0.03 |  | 37.83 |  | 0.65 |  | 12.96 |  | 5.78 |  | 14.5 |  | 1.88 |  | 0.04 |  | 0 |  | 2.03 | [7 empty] | 146.33
19 | 12 | 12CZ15MediumOffice Glazing WindowU | 264.15 |  | 10.27 |  | 0.03 |  | 37.63 |  | 0.55 |  | 12.86 |  | 5.78 |  | 14.5 |  | 1.88 |  | 0.03 |  | 0 |  | 2.03 |  | 0.58% |  | 0.54% |  | No | Fail | 147.33
20 | 13 | 13CZ15MediumOffice Glazing WindowSHGC | 260.75 |  | 10.11 |  | 0.03 |  | 37.26 |  | 0.75 |  | 12.39 |  | 5.78 |  | 14.5 |  | 1.79 |  | 0.04 |  | 0 |  | 2.03 |  | 1.86% |  | 1.49% |  | No | Fail | 152.67
21 | 14 | 14CZ15MediumOffice Glazing WindowUSHGC | 259.06 |  | 10.07 |  | 0.03 |  | 37.03 |  | 0.63 |  | 12.27 |  | 5.78 |  | 14.5 |  | 1.79 |  | 0.04 |  | 0 |  | 2.03 |  | 2.49% |  | 2.12% |  | No | Fail | 146.83
22 |  | CZ16MediumOfficeBaseline | 193.83 |  | 7.09 |  | 0.12 |  | 36.57 |  | 9.66 |  | 2.53 |  | 5.78 |  | 14.5 |  | 1.25 |  | 0.12 |  | 0 |  | 2.73 | [7 empty] | 78.83
23 | 15 | 15CZ16MediumOffice Envelope FloorslabInsulation | 194.14 |  | 7.11 |  | 0.12 |  | 36.37 |  | 9.38 |  | 2.59 |  | 5.78 |  | 14.5 |  | 1.28 |  | 0.12 |  | 0 |  | 2.72 |  | -0.16% |  | 0.55% |  | No | Fail | 80.67
24 | 16 | 16CZ16MediumOffice Envelope Infiltration | 194.49 |  | 7.09 |  | 0.13 |  | 36.94 |  | 10.03 |  | 2.53 |  | 5.78 |  | 14.5 |  | 1.25 |  | 0.13 |  | 0 |  | 2.73 |  | -0.34% |  | -1% |  | No | Fail | 82.16
25 |  | CZ16MediumOfficeBaseline | 193.83 |  | 7.09 |  | 0.12 |  | 36.57 |  | 9.66 |  | 2.53 |  | 5.78 |  | 14.5 |  | 1.25 |  | 0.12 |  | 0 |  | 2.73 | [7 empty] | 82.17
26 | 17 | 17CZ16MediumOffice Glazing WindowU | 192.46 |  | 7.1 |  | 0.11 |  | 35.65 |  | 8.68 |  | 2.57 |  | 5.78 |  | 14.5 |  | 1.27 |  | 0.12 |  | 0 |  | 2.73 |  | 0.71% |  | 2.53% |  | No | Fail | 163.16
27 | 18 | 18CZ16MediumOffice Glazing WindowSHGC | 192.05 |  | 7.01 |  | 0.13 |  | 36.9 |  | 10.27 |  | 2.34 |  | 5.78 |  | 14.5 |  | 1.15 |  | 0.13 |  | 0 |  | 2.73 |  | 0.92% |  | -0.91% |  | No | Fail | 160.5
28 | 19 | 19CZ16MediumOffice Glazing WindowUSHGC | 190.58 |  | 7.02 |  | 0.12 |  | 35.94 |  | 9.26 |  | 2.38 |  | 5.78 |  | 14.5 |  | 1.17 |  | 0.12 |  | 0 |  | 2.73 |  | 1.67% |  | 1.74% |  | No | Fail | 161.34
29 |  | CZ06MediumOfficeBaseline | 190.08 |  | 7.56 |  | 0.03 |  | 29.27 |  | 1.12 |  | 4.39 |  | 5.78 |  | 14.5 |  | 1.09 |  | 0.05 |  | 0 |  | 2.34 | [7 empty] | 158.33
30 | 20 | 20CZ06MediumOffice Envelope FloorslabInsulation | 190.88 |  | 7.6 |  | 0.03 |  | 29.26 |  | 1.01 |  | 4.48 |  | 5.78 |  | 14.5 |  | 1.12 |  | 0.05 |  | 0 |  | 2.34 |  | -0.42% |  | 0.01% |  | No | Fail | 148
31 | 21 | 21CZ06MediumOffice Envelope Infiltration | 190.1 |  | 7.56 |  | 0.04 |  | 29.31 |  | 1.18 |  | 4.38 |  | 5.78 |  | 14.5 |  | 1.08 |  | 0.06 |  | 0 |  | 2.34 |  | -0.01% |  | -0.15% |  | No | Fail | 150.67
32 |  | CZ06MediumOfficeBaseline | 190.08 |  | 7.56 |  | 0.03 |  | 29.27 |  | 1.12 |  | 4.39 |  | 5.78 |  | 14.5 |  | 1.09 |  | 0.05 |  | 0 |  | 2.34 | [7 empty] | 160.17
33 | 22 | 22CZ06MediumOffice Glazing WindowU | 190.5 |  | 7.6 |  | 0.03 |  | 29.2 |  | 0.94 |  | 4.46 |  | 5.78 |  | 14.5 |  | 1.13 |  | 0.05 |  | 0 |  | 2.34 |  | -0.22% |  | 0.23% |  | No | Fail | 159.34
34 | 23 | 23CZ06MediumOffice Glazing WindowSHGC | 186.86 |  | 7.46 |  | 0.04 |  | 28.99 |  | 1.22 |  | 4.1 |  | 5.78 |  | 14.5 |  | 1 |  | 0.06 |  | 0 |  | 2.34 |  | 1.69% |  | 0.93% |  | No | Fail | 79.84
35 | 24 | 24CZ06MediumOffice Glazing WindowUSHGC | 187.22 |  | 7.49 |  | 0.03 |  | 28.91 |  | 1.03 |  | 4.17 |  | 5.78 |  | 14.5 |  | 1.04 |  | 0.05 |  | 0 |  | 2.34 |  | 1.5% |  | 1.23% |  | No | Fail | 79.34
36 |  | CZ07LargeOfficeBaseline | 192.22 |  | 7.99 |  | 0.02 |  | 29.54 |  | 0.08 |  | 3.11 |  | 5.06 |  | 14.5 |  | 2.18 |  | 1.8 |  | 0 |  | 2.19
37 | 25 | 25CZ07LargeOffice WWR20 | 191.65 |  | 8.01 |  | 0.02 |  | 29.57 |  | 0.06 |  | 2.9 |  | 5.29 |  | 14.5 |  | 2.34 |  | 1.73 |  | 0 |  | 2.19 |  | 0.3% |  | -0.12% |  | No | Fail | 677.25
38 | 26 | 26CZ07LargeOffice WWR60 | 193.72 |  | 8.04 |  | 0.02 |  | 29.7 |  | 0.09 |  | 3.23 |  | 5.05 |  | 14.5 |  | 2.16 |  | 1.83 |  | 0 |  | 2.19 |  | -0.78% |  | -0.57% |  | No | Fail | 684.75
39 | 27 | 27CZ07LargeOffice WWR60SouthOverhang | 193.72 |  | 8.04 |  | 0.02 |  | 29.7 |  | 0.09 |  | 3.23 |  | 5.05 |  | 14.5 |  | 2.16 |  | 1.83 |  | 0 |  | 2.19 |  | -0.78% |  | -0.57% |  | No | Fail | 636.25
40 |  | CZ01LargeOfficeBaseline | 159.2 |  | 6.69 |  | 0.04 |  | 26.79 |  | 1.46 |  | 0.6 |  | 5.09 |  | 14.5 |  | 2.08 |  | 0.51 |  | 0 |  | 2.52 | [7 empty] | 633.25
41 | 28 | 28CZ01LargeOffice WWR20 | 159.77 |  | 6.74 |  | 0.04 |  | 26.62 |  | 1.1 |  | 0.58 |  | 5.32 |  | 14.5 |  | 2.08 |  | 0.5 |  | 0 |  | 2.52 |  | -0.36% |  | 0.62% |  | No | Fail | 822.5
42 | 29 | 29CZ01LargeOffice WWR60 | 160.41 |  | 6.71 |  | 0.04 |  | 27.21 |  | 1.81 |  | 0.62 |  | 5.08 |  | 14.5 |  | 2.12 |  | 0.53 |  | 0 |  | 2.52 |  | -0.76% |  | -1.58% |  | No | Fail | 813
43 |  | CZ15MediumOfficeBaseline | 265.68 |  | 10.3 |  | 0.03 |  | 37.83 |  | 0.65 |  | 12.96 |  | 5.78 |  | 14.5 |  | 1.88 |  | 0.04 |  | 0 |  | 2.03 | [7 empty] | 842.5
44 | 30 | 30CZ15MediumOffice Lighting LowLPD | 255.94 |  | 9.88 |  | 0.03 |  | 36.42 |  | 0.68 |  | 12.72 |  | 4.62 |  | 14.5 |  | 1.83 |  | 0.04 |  | 0 |  | 2.03 |  | 3.67% |  | 3.73% |  | No | Fail | 815.5
45 | 31 | 31CZ15MediumOffice Lighting HIghLPD | 275.5 |  | 10.73 |  | 0.03 |  | 39.26 |  | 0.63 |  | 13.21 |  | 6.94 |  | 14.5 |  | 1.92 |  | 0.04 |  | 0 |  | 2.03 |  | -3.69% |  | -3.77% |  | No | Fail | 245.75
46 |  | CZ16MediumOfficeBaseline | 193.83 |  | 7.09 |  | 0.12 |  | 36.57 |  | 9.66 |  | 2.53 |  | 5.78 |  | 14.5 |  | 1.25 |  | 0.12 |  | 0 |  | 2.73 | [7 empty] | 231
47 | 32 | 32CZ16MediumOffice Lighting LowLPD | 185.93 |  | 6.72 |  | 0.13 |  | 35.72 |  | 10.08 |  | 2.46 |  | 4.62 |  | 14.5 |  | 1.21 |  | 0.13 |  | 0 |  | 2.73 |  | 4.07% |  | 2.34% |  | No | Fail | 269.5
48 | 33 | 33CZ16MediumOffice Lighting HIghLPD | 201.77 |  | 7.46 |  | 0.12 |  | 37.45 |  | 9.27 |  | 2.61 |  | 6.94 |  | 14.5 |  | 1.29 |  | 0.12 |  | 0 |  | 2.73 |  | -4.1% |  | -2.41% |  | No | Fail | 258.5
49 |  | CZ06MediumOfficeBaseline | 190.08 |  | 7.56 |  | 0.03 |  | 29.27 |  | 1.12 |  | 4.39 |  | 5.78 |  | 14.5 |  | 1.09 |  | 0.05 |  | 0 |  | 2.34 | [7 empty] | 325.75
50 | 34 | 34CZ06MediumOffice Lighting LowLPD | 181.14 |  | 7.17 |  | 0.04 |  | 27.99 |  | 1.18 |  | 4.25 |  | 4.62 |  | 14.5 |  | 1.05 |  | 0.06 |  | 0 |  | 2.34 |  | 4.71% |  | 4.36% |  | No | Fail | 194
51 | 35 | 35CZ06MediumOffice Lighting HIghLPD | 199.06 |  | 7.96 |  | 0.03 |  | 30.54 |  | 1.06 |  | 4.53 |  | 6.94 |  | 14.5 |  | 1.13 |  | 0.05 |  | 0 |  | 2.34 |  | -4.73% |  | -4.35% |  | No | Fail | 477
52 |  | CZ15MediumOfficeBaseline | 265.68 |  | 10.3 |  | 0.03 |  | 37.83 |  | 0.65 |  | 12.96 |  | 5.78 |  | 14.5 |  | 1.88 |  | 0.04 |  | 0 |  | 2.03 | [7 empty] | 480.75
53 | 36 | 36CZ15MediumOffice Int.Eqpt LowEPD | 240.35 |  | 9.2 |  | 0.03 |  | 34.19 |  | 0.77 |  | 12.26 |  | 5.78 |  | 11.6 |  | 1.71 |  | 0.04 |  | 0 |  | 2.03 |  | 9.54% |  | 9.63% |  | No | Fail | 347
54 | 37 | 37CZ15MediumOffice Int.Eqpt HighEPD | 291.21 |  | 11.41 |  | 0.03 |  | 41.52 |  | 0.56 |  | 13.67 |  | 5.78 |  | 17.4 |  | 2.05 |  | 0.03 |  | 0 |  | 2.03 |  | -9.61% |  | -9.76% |  | No | Fail | 280.75
55 |  | CZ16MediumOfficeBaseline | 193.83 |  | 7.09 |  | 0.12 |  | 36.57 |  | 9.66 |  | 2.53 |  | 5.78 |  | 14.5 |  | 1.25 |  | 0.12 |  | 0 |  | 2.73 | [7 empty] | 391
56 | 38 | 38CZ16MediumOffice Int.Eqpt LowEPD | 173.49 |  | 6.13 |  | 0.13 |  | 34.41 |  | 10.76 |  | 2.31 |  | 5.78 |  | 11.6 |  | 1.11 |  | 0.13 |  | 0 |  | 2.73 |  | 10.49% |  | 5.9% |  | No | Fail
57 | 39 | 39CZ16MediumOffice Int.Eqpt HighEPD | 214.4 |  | 8.04 |  | 0.11 |  | 38.84 |  | 8.66 |  | 2.76 |  | 5.78 |  | 17.4 |  | 1.4 |  | 0.12 |  | 0 |  | 2.72 |  | -10.61% |  | -6.19% |  | No | Fail | 677.25
58 |  | CZ06MediumOfficeBaseline | 190.08 |  | 7.56 |  | 0.03 |  | 29.27 |  | 1.12 |  | 4.39 |  | 5.78 |  | 14.5 |  | 1.09 |  | 0.05 |  | 0 |  | 2.34 | [7 empty] | 709.5
59 | 40 | 40CZ06MediumOffice Int.Eqpt LowEPD | 166.8 |  | 6.55 |  | 0.04 |  | 25.97 |  | 1.28 |  | 3.97 |  | 5.78 |  | 11.6 |  | 0.94 |  | 0.06 |  | 0 |  | 2.34 |  | 12.25% |  | 11.27% |  | No | Fail | 646.5
60 | 41 | 41CZ06MediumOffice Int.Eqpt HighEPD | 213.51 |  | 8.58 |  | 0.03 |  | 32.6 |  | 0.99 |  | 4.81 |  | 5.78 |  | 17.4 |  | 1.24 |  | 0.05 |  | 0 |  | 2.34 |  | -12.33% |  | -11.39% |  | No | Fail | 822.5
61 |  | CZ07LargeOfficeBaseline | 192.22 |  | 7.99 |  | 0.02 |  | 29.54 |  | 0.08 |  | 3.11 |  | 5.06 |  | 14.5 |  | 2.18 |  | 1.8 |  | 0 |  | 2.19 | [7 empty] | 845.75
62 | 42 | 42CZ07LargeOffice Daylighting Cont.DimHighVT | 192.01 |  | 7.98 |  | 0.02 |  | 29.5 |  | 0.08 |  | 3.11 |  | 5.03 |  | 14.5 |  | 2.18 |  | 1.8 |  | 0 |  | 2.19 |  | 0.11% |  | 0.11% |  | No | Fail | 806.25
63 | 43 | 43CZ07LargeOffice Daylighting StepDim | 190.6 |  | 7.92 |  | 0.02 |  | 29.3 |  | 0.08 |  | 3.09 |  | 4.86 |  | 14.5 |  | 2.18 |  | 1.79 |  | 0 |  | 2.19 |  | 0.85% |  | 0.8% |  | No | Fail | 245.75
64 | 44 | 44CZ07LargeOffice Daylighting StepDimHighVT | 190.21 |  | 7.91 |  | 0.02 |  | 29.25 |  | 0.08 |  | 3.08 |  | 4.82 |  | 14.5 |  | 2.18 |  | 1.79 |  | 0 |  | 2.19 |  | 1.05% |  | 0.98% |  | No | Fail | 258.75
65 |  | 25CZ07LargeOffice WWR20 | 191.65 |  | 8.01 |  | 0.02 |  | 29.57 |  | 0.06 |  | 2.9 |  | 5.29 |  | 14.5 |  | 2.34 |  | 1.73 |  | 0 |  | 2.19 | [7 empty] | 235
66 | 45 | 45CZ07LargeOffice Daylighting WWR20Cont.DimHighVT | 191.46 |  | 8 |  | 0.02 |  | 29.54 |  | 0.06 |  | 2.9 |  | 5.27 |  | 14.5 |  | 2.34 |  | 1.73 |  | 0 |  | 2.19 |  | 0.1% |  | 0.09% |  | No | Fail
67 | 46 | 46CZ07LargeOffice Daylighting WWR20StepDim | 190.86 |  | 7.97 |  | 0.02 |  | 29.46 |  | 0.06 |  | 2.88 |  | 5.2 |  | 14.5 |  | 2.34 |  | 1.72 |  | 0 |  | 2.19 |  | 0.42% |  | 0.38% |  | No | Fail | 325.75
68 | 47 | 47CZ07LargeOffice Daylighting WWR20StepDimHighVT | 190.52 |  | 7.96 |  | 0.02 |  | 29.41 |  | 0.06 |  | 2.88 |  | 5.16 |  | 14.5 |  | 2.34 |  | 1.72 |  | 0 |  | 2.19 |  | 0.59% |  | 0.55% |  | No | Fail | 366.5
69 |  | 26CZ07LargeOffice WWR60 | 193.72 |  | 8.04 |  | 0.02 |  | 29.7 |  | 0.09 |  | 3.23 |  | 5.05 |  | 14.5 |  | 2.16 |  | 1.83 |  | 0 |  | 2.19 | [7 empty] | 366.5
70 | 48 | 48CZ07LargeOffice Daylighting WWR60Cont.DimHighVT | 193.53 |  | 8.03 |  | 0.02 |  | 29.68 |  | 0.09 |  | 3.23 |  | 5.02 |  | 14.5 |  | 2.16 |  | 1.83 |  | 0 |  | 2.19 |  | 0.1% |  | 0.09% |  | No | Fail | 383.75
71 | 49 | 49CZ07LargeOffice Daylighting WWR60StepDim | 192.01 |  | 7.96 |  | 0.02 |  | 29.46 |  | 0.1 |  | 3.21 |  | 4.84 |  | 14.5 |  | 2.15 |  | 1.83 |  | 0 |  | 2.19 |  | 0.88% |  | 0.82% |  | No | Fail | 384.25
72 | 50 | 50CZ07LargeOffice Daylighting WWR60StepDimHighVT | 191.64 |  | 7.95 |  | 0.02 |  | 29.41 |  | 0.1 |  | 3.21 |  | 4.8 |  | 14.5 |  | 2.15 |  | 1.83 |  | 0 |  | 2.19 |  | 1.08% |  | 1% |  | No | Fail | 194
73 |  | CZ01LargeOfficeBaseline | 159.2 |  | 6.69 |  | 0.04 |  | 26.79 |  | 1.46 |  | 0.6 |  | 5.09 |  | 14.5 |  | 2.08 |  | 0.51 |  | 0 |  | 2.52 | [7 empty] | 215.5
74 | 51 | 51CZ01LargeOffice Daylighting Cont.DimHighVT | 157.47 |  | 6.61 |  | 0.04 |  | 26.55 |  | 1.47 |  | 0.59 |  | 4.87 |  | 14.5 |  | 2.06 |  | 0.51 |  | 0 |  | 2.52 |  | 1.09% |  | 0.91% |  | No | Fail | 215.25
75 | 52 | 52CZ01LargeOffice Daylighting StepDim | 157.84 |  | 6.63 |  | 0.04 |  | 26.6 |  | 1.46 |  | 0.6 |  | 4.92 |  | 14.5 |  | 2.06 |  | 0.51 |  | 0 |  | 2.52 |  | 0.85% |  | 0.72% |  | No | Fail | 225
76 | 53 | 53CZ01LargeOffice Daylighting StepDimHighVT | 157.47 |  | 6.61 |  | 0.04 |  | 26.55 |  | 1.47 |  | 0.59 |  | 4.87 |  | 14.5 |  | 2.06 |  | 0.51 |  | 0 |  | 2.52 |  | 1.09% |  | 0.91% |  | No | Fail | 225.25
77 |  | 28CZ01LargeOffice WWR20 | 159.77 |  | 6.74 |  | 0.04 |  | 26.62 |  | 1.1 |  | 0.58 |  | 5.32 |  | 14.5 |  | 2.08 |  | 0.5 |  | 0 |  | 2.52 | [7 empty] | 477
78 | 54 | 54CZ01LargeOffice Daylighting WWR20Cont.DimHighVT | 159.59 |  | 6.73 |  | 0.04 |  | 26.6 |  | 1.11 |  | 0.58 |  | 5.3 |  | 14.5 |  | 2.08 |  | 0.5 |  | 0 |  | 2.52 |  | 0.11% |  | 0.09% |  | No | Fail | 522.5
79 | 55 | 55CZ01LargeOffice Daylighting WWR20StepDim | 159.13 |  | 6.72 |  | 0.04 |  | 26.54 |  | 1.1 |  | 0.58 |  | 5.24 |  | 14.5 |  | 2.07 |  | 0.5 |  | 0 |  | 2.52 |  | 0.4% |  | 0.33% |  | No | Fail | 522.25
80 | 56 | 56CZ01LargeOffice Daylighting WWR20StepDimHighVT | 158.82 |  | 6.7 |  | 0.04 |  | 26.49 |  | 1.11 |  | 0.58 |  | 5.2 |  | 14.5 |  | 2.07 |  | 0.49 |  | 0 |  | 2.52 |  | 0.59% |  | 0.49% |  | No | Fail | 536.25
81 |  | 29CZ01LargeOffice WWR60 | 160.41 |  | 6.71 |  | 0.04 |  | 27.21 |  | 1.81 |  | 0.62 |  | 5.08 |  | 14.5 |  | 2.12 |  | 0.53 |  | 0 |  | 2.52 | [7 empty] | 536.25
82 | 57 | 57CZ01LargeOffice Daylighting WWR60Cont.DimHighVT | 160.2 |  | 6.7 |  | 0.04 |  | 27.18 |  | 1.81 |  | 0.61 |  | 5.06 |  | 14.5 |  | 2.12 |  | 0.53 |  | 0 |  | 2.52 |  | 0.13% |  | 0.12% |  | No | Fail | 347
83 | 58 | 58CZ01LargeOffice Daylighting WWR60StepDim | 158.93 |  | 6.65 |  | 0.04 |  | 26.99 |  | 1.8 |  | 0.61 |  | 4.9 |  | 14.5 |  | 2.11 |  | 0.53 |  | 0 |  | 2.52 |  | 0.92% |  | 0.8% |  | No | Fail | 354.75
84 | 59 | 59CZ01LargeOffice Daylighting WWR60StepDimHighVT | 158.59 |  | 6.63 |  | 0.04 |  | 26.95 |  | 1.81 |  | 0.61 |  | 4.86 |  | 14.5 |  | 2.11 |  | 0.52 |  | 0 |  | 2.52 |  | 1.13% |  | 0.97% |  | No | Fail | 354.5
85 |  | CZ07StandAloneRetailBaseline | 309.29 |  | 11.3 |  | 0.1 |  | 48.55 |  | 1.46 |  | 7.61 |  | 12.13 |  | 10.73 |  | 8.08 |  | 0 |  | 0 |  | 8.54 | [7 empty] | 359.25
86 | 60 | 60CZ07StandAloneRetail Daylighting SRRBaseHighVT | 308.89 |  | 11.28 |  | 0.1 |  | 48.5 |  | 1.46 |  | 7.61 |  | 12.09 |  | 10.73 |  | 8.08 |  | 0 |  | 0 |  | 8.54 |  | 0.13% |  | 0.11% |  | No | Fail | 359.25
87 | 61 | 61CZ07StandAloneRetail Daylighting SRR3.04 | 311.48 |  | 11.37 |  | 0.1 |  | 48.82 |  | 1.48 |  | 7.87 |  | 11.85 |  | 10.73 |  | 8.34 |  | 0 |  | 0 |  | 8.54 |  | -0.71% |  | -0.55% |  | No | Fail | 280.75
88 | 62 | 62CZ07StandAloneRetail Daylighting SRR3.04HighVT | 311.1 |  | 11.35 |  | 0.1 |  | 48.77 |  | 1.49 |  | 7.87 |  | 11.81 |  | 10.73 |  | 8.34 |  | 0 |  | 0 |  | 8.54 |  | -0.59% |  | -0.45% |  | No | Fail | 295.25
89 |  | CZ01StandAloneRetailBaseline | 262.95 |  | 9.77 |  | 0.16 |  | 49.15 |  | 6.32 |  | 0.72 |  | 12.16 |  | 10.73 |  | 9.74 |  | 0 |  | 0 |  | 9.5 | [7 empty] | 296
90 | 63 | 63CZ01StandAloneRetail Daylighting SRRBaseHighVT | 262.59 |  | 9.76 |  | 0.16 |  | 49.1 |  | 6.32 |  | 0.72 |  | 12.11 |  | 10.73 |  | 9.74 |  | 0 |  | 0 |  | 9.5 |  | 0.14% |  | 0.09% |  | No | Fail | 302
91 | 64 | 64CZ01StandAloneRetail Daylighting SRR3.04 | 261.19 |  | 9.7 |  | 0.16 |  | 48.96 |  | 6.37 |  | 0.72 |  | 11.89 |  | 10.73 |  | 9.75 |  | 0 |  | 0 |  | 9.5 |  | 0.67% |  | 0.38% |  | No | Fail | 301.75
92 | 65 | 65CZ01StandAloneRetail Daylighting SRR3.04HighVT | 260.83 |  | 9.68 |  | 0.16 |  | 48.92 |  | 6.38 |  | 0.72 |  | 11.84 |  | 10.73 |  | 9.75 |  | 0 |  | 0 |  | 9.5 |  | 0.8% |  | 0.47% |  | No | Fail | 391
93 |  | CZ16StandAloneRetailBaselineDuctLoss | 539.51 |  | 18.51 |  | 0.3 |  | 92.84 |  | 19.91 |  | 11.93 |  | 12.18 |  | 10.73 |  | 28.34 |  | 0 |  | 0 |  | 9.75 | [7 empty] | 404.5
94 | 66 | 66CZ16StandAloneRetail HVAC DuctLoss | 539.95 |  | 18.53 |  | 0.3 |  | 92.8 |  | 19.83 |  | 12.01 |  | 12.18 |  | 10.73 |  | 28.31 |  | 0 |  | 0 |  | 9.75 |  | -0.08% |  | 0.04% |  | No | Fail | 404.75
95 |  | CZ06StandAloneRetailBaselineDuctLoss | 512.27 |  | 18.4 |  | 0.13 |  | 75.82 |  | 4.37 |  | 20.24 |  | 12.11 |  | 10.73 |  | 19.7 |  | 0 |  | 0 |  | 8.67 | [7 empty] | 409.75
96 | 67 | 67CZ06StandAloneRetail HVAC DuctLoss | 513.1 |  | 18.43 |  | 0.13 |  | 75.87 |  | 4.33 |  | 20.37 |  | 12.11 |  | 10.73 |  | 19.67 |  | 0 |  | 0 |  | 8.67 |  | -0.16% |  | -0.07% |  | No | Fail | 408.25
97 |  | CZ15MediumOfficeBaseline | 265.68 |  | 10.3 |  | 0.03 |  | 37.83 |  | 0.65 |  | 12.96 |  | 5.78 |  | 14.5 |  | 1.88 |  | 0.04 |  | 0 |  | 2.03 | [7 empty] | 0
98 | 68 | 68CZ15MediumOffice HVACPVAV Design | 269.5 |  | 10.45 |  | 0.03 |  | 38.3 |  | 0.63 |  | 13.1 |  | 5.78 |  | 14.5 |  | 2.23 |  | 0.04 |  | 0 |  | 2.03 |  | -1.44% |  | -1.25% |  | No | Fail | 0
99 | 69 | 69CZ15MediumOffice HVACPVAV SATControl | 262.33 |  | 10.16 |  | 0.03 |  | 37.31 |  | 0.62 |  | 12.92 |  | 5.78 |  | 14.5 |  | 1.43 |  | 0.04 |  | 0 |  | 2.03 |  | 1.26% |  | 1.38% |  | No | Fail | 0
100 | 70 | 70CZ15MediumOffice HVACPVAV VAVControl | 266.27 |  | 10.34 |  | 0.03 |  | 37.94 |  | 0.64 |  | 13.08 |  | 5.78 |  | 14.5 |  | 1.87 |  | 0.04 |  | 0 |  | 2.03 |  | -0.22% |  | -0.29% |  | No | Fail | 0
101 | 71 | 71CZ15MediumOffice HVACPVAV EconomizerType | 266.29 |  | 10.34 |  | 0.03 |  | 37.95 |  | 0.65 |  | 13.08 |  | 5.78 |  | 14.5 |  | 1.87 |  | 0.04 |  | 0 |  | 2.03 |  | -0.23% |  | -0.31% |  | No | Fail | 0
102 |  | CZ16MediumOfficeBaseline | 193.83 |  | 7.09 |  | 0.12 |  | 36.57 |  | 9.66 |  | 2.53 |  | 5.78 |  | 14.5 |  | 1.25 |  | 0.12 |  | 0 |  | 2.73 | [7 empty] | 0
103 | 72 | 72CZ16MediumOffice HVACPVAV Design | 196.03 |  | 7.17 |  | 0.12 |  | 36.79 |  | 9.6 |  | 2.58 |  | 5.78 |  | 14.5 |  | 1.48 |  | 0.12 |  | 0 |  | 2.73 |  | -1.13% |  | -0.6% |  | No | Fail | 0
104 | 73 | 73CZ16MediumOffice HVACPVAV SATControl | 192.46 |  | 7.08 |  | 0.12 |  | 36.5 |  | 9.61 |  | 2.42 |  | 5.78 |  | 14.5 |  | 1.34 |  | 0.12 |  | 0 |  | 2.73 |  | 0.7% |  | 0.19% |  | No | Fail | 0
105 | 74 | 74CZ16MediumOffice HVACPVAV VAVControl | 193.96 |  | 7.14 |  | 0.12 |  | 36.25 |  | 9.17 |  | 2.7 |  | 5.78 |  | 14.5 |  | 1.24 |  | 0.12 |  | 0 |  | 2.73 |  | -0.07% |  | 0.89% |  | No | Fail
106 | 75 | 75CZ16MediumOffice HVACPVAV EconomizerType | 194.9 |  | 7.14 |  | 0.12 |  | 36.74 |  | 9.66 |  | 2.7 |  | 5.78 |  | 14.5 |  | 1.25 |  | 0.12 |  | 0 |  | 2.73 |  | -0.55% |  | -0.46% |  | No | Fail | 677.25
107 |  | CZ06MediumOfficeBaseline | 190.08 |  | 7.56 |  | 0.03 |  | 29.27 |  | 1.12 |  | 4.39 |  | 5.78 |  | 14.5 |  | 1.09 |  | 0.05 |  | 0 |  | 2.34 | [7 empty] | 740.25
108 | 76 | 76CZ06MediumOffice HVACPVAV Design | 192.22 |  | 7.64 |  | 0.03 |  | 29.53 |  | 1.11 |  | 4.46 |  | 5.78 |  | 14.5 |  | 1.29 |  | 0.05 |  | 0 |  | 2.34 |  | -1.13% |  | -0.91% |  | No | Fail | 623
109 | 77 | 77CZ06MediumOffice HVACPVAV SATControl | 188.44 |  | 7.5 |  | 0.03 |  | 29 |  | 1.08 |  | 4.06 |  | 5.78 |  | 14.5 |  | 1.19 |  | 0.05 |  | 0 |  | 2.34 |  | 0.86% |  | 0.91% |  | No | Fail | 822.5
110 | 78 | 78CZ06MediumOffice HVACPVAV VAVControl | 191.06 |  | 7.61 |  | 0.03 |  | 29.42 |  | 1.11 |  | 4.56 |  | 5.78 |  | 14.5 |  | 1.09 |  | 0.05 |  | 0 |  | 2.34 |  | -0.51% |  | -0.52% |  | No | Fail | 873.75
111 | 79 | 79CZ06MediumOffice HVACPVAV EconomizerType | 191.09 |  | 7.61 |  | 0.03 |  | 29.43 |  | 1.12 |  | 4.56 |  | 5.78 |  | 14.5 |  | 1.09 |  | 0.05 |  | 0 |  | 2.34 |  | -0.53% |  | -0.57% |  | No | Fail | 786.75
112 |  | CZ15LargeOfficeBaseline | 232.94 |  | 9.6 |  | 0.02 |  | 34.91 |  | 0.22 |  | 5.94 |  | 5.06 |  | 14.5 |  | 3.28 |  | 2.67 |  | 0 |  | 1.92 | [7 empty] | 245.75
113 | 80 | 80CZ15LargeOffice HVACVAV ChillerCOP | 227.66 |  | 9.41 |  | 0.02 |  | 34.24 |  | 0.22 |  | 5.32 |  | 5.06 |  | 14.5 |  | 3.28 |  | 2.64 |  | 0 |  | 1.92 |  | 2.27% |  | 1.91% |  | No | Fail | 277
114 | 81 | 81CZ15LargeOffice HVACVAV CHWdeltaT | 235.25 |  | 9.69 |  | 0.02 |  | 35.2 |  | 0.22 |  | 6.09 |  | 5.06 |  | 14.5 |  | 3.28 |  | 2.81 |  | 0 |  | 1.92 |  | -0.99% |  | -0.84% |  | No | Fail | 216.5
115 | 82 | 82CZ15LargeOffice HVACVAV CWSetpoint | 230.68 |  | 9.53 |  | 0.02 |  | 34.66 |  | 0.22 |  | 5.88 |  | 5.06 |  | 14.5 |  | 3.28 |  | 2.67 |  | 0 |  | 1.92 |  | 0.97% |  | 0.7% |  | No | Fail | 97.66
116 | 83 | 83CZ15LargeOffice HVACVAV TowerEff | 239.08 |  | 9.82 |  | 0.02 |  | 35.64 |  | 0.22 |  | 5.92 |  | 5.06 |  | 14.5 |  | 3.28 |  | 2.67 |  | 0 |  | 1.92 |  | -2.63% |  | -2.1% |  | No | Fail | 94.17
|  | CZ16LargeOfficeBaseline | 194.77 |  | 7.78 |  | 0.06 |  | 32.1 |  | 2.94 |  | 2.11 |  | 5.07 |  | 14.5 |  | 3.29 |  | 1.41 |  | 0 |  | 2.61
| 84 | 84CZ16LargeOffice HVACVAV ChillerCOP | 192.73 |  | 7.71 |  | 0.06 |  | 31.86 |  | 2.94 |  | 1.9 |  | 5.07 |  | 14.5 |  | 3.29 |  | 1.39 |  | 0 |  | 2.61 |  | 1.05% |  | 0.75% |  | No | Fail
| 85 | 85CZ16LargeOffice HVACVAV CHWdeltaT | 191.69 |  | 7.77 |  | 0.06 |  | 32.08 |  | 2.94 |  | 2.3 |  | 5.07 |  | 14.5 |  | 2.92 |  | 1.57 |  | 0 |  | 2.61 |  | 1.58% |  | 0.06% |  | No | Fail
| 86 | 86CZ16LargeOffice HVACVAV CWSetpoint | 194.32 |  | 7.75 |  | 0.06 |  | 31.98 |  | 2.94 |  | 1.83 |  | 5.07 |  | 14.5 |  | 3.29 |  | 1.41 |  | 0 |  | 2.61 |  | 0.23% |  | 0.36% |  | No | Fail
| 87 | 87CZ16LargeOffice HVACVAV TowerEff | 195.72 |  | 7.8 |  | 0.06 |  | 32.18 |  | 2.94 |  | 2.11 |  | 5.07 |  | 14.5 |  | 3.29 |  | 1.41 |  | 0 |  | 2.61 |  | -0.48% |  | -0.26% |  | No | Fail
|  | CZ06LargeOfficeBaseline | 196.14 |  | 8.09 |  | 0.03 |  | 30.15 |  | 0.32 |  | 3.03 |  | 5.06 |  | 14.5 |  | 2.52 |  | 1.83 |  | 0 |  | 2.23
| 88 | 88CZ06LargeOffice HVACVAV ChillerCOP | 193.23 |  | 7.99 |  | 0.03 |  | 29.81 |  | 0.32 |  | 2.72 |  | 5.06 |  | 14.5 |  | 2.52 |  | 1.81 |  | 0 |  | 2.23 |  | 1.48% |  | 1.15% |  | No | Fail
| 89 | 89CZ06LargeOffice HVACVAV CHWdeltaT | 197.99 |  | 8.17 |  | 0.03 |  | 30.43 |  | 0.33 |  | 3.17 |  | 5.06 |  | 14.5 |  | 2.52 |  | 1.94 |  | 0 |  | 2.23 |  | -0.94% |  | -0.93% |  | No | Fail
| 90 | 90CZ06LargeOffice HVACVAV CWSetpoint | 194.35 |  | 8.03 |  | 0.03 |  | 29.96 |  | 0.32 |  | 3.02 |  | 5.06 |  | 14.5 |  | 2.52 |  | 1.83 |  | 0 |  | 2.23 |  | 0.91% |  | 0.65% |  | No | Fail
| 91 | 91CZ06LargeOffice HVACVAV TowerEff | 199.69 |  | 8.19 |  | 0.03 |  | 30.5 |  | 0.32 |  | 3.03 |  | 5.06 |  | 14.5 |  | 2.52 |  | 1.83 |  | 0 |  | 2.23 |  | -1.81% |  | -1.15% |  | No | Fail
|  | CZ15StripMallBaselinePSZ | 450.07 |  | 15.99 |  | 0.05 |  | 59.72 |  | 5.16 |  | 24.27 |  | 14.17 |  | 6.21 |  | 9.92 |  | 0 |  | 0 |  | 0
| 92 | 92CZ15StripMall HVACPSZ DXCOP | 414.16 |  | 14.87 |  | 0.05 |  | 55.89 |  | 5.16 |  | 20.44 |  | 14.17 |  | 6.21 |  | 9.92 |  | 0 |  | 0 |  | 0 |  | 7.98% |  | 6.42% |  | No | Fail
| 93 | 93CZ15StripMall HVACPSZ HeatEff | 448.97 |  | 15.99 |  | 0.05 |  | 59.15 |  | 4.59 |  | 24.27 |  | 14.17 |  | 6.21 |  | 9.92 |  | 0 |  | 0 |  | 0 |  | 0.24% |  | 0.96% |  | No | Fail
| 94 | 94CZ15StripMall HVACPSZ EconomizerControl | 453.26 |  | 16.18 |  | 0.05 |  | 60.23 |  | 5.03 |  | 24.9 |  | 14.17 |  | 6.21 |  | 9.92 |  | 0 |  | 0 |  | 0 |  | -0.71% |  | -0.84% |  | No | Fail
|  | CZ16StripMallBaselinePSZ | 329.1 |  | 10.25 |  | 0.33 |  | 68.1 |  | 33.14 |  | 4.13 |  | 14.17 |  | 6.21 |  | 10.46 |  | 0 |  | 0 |  | 0
| 95 | 95CZ16StripMall HVACPSZ DXCOP | 320.81 |  | 10.05 |  | 0.33 |  | 67.44 |  | 33.14 |  | 3.48 |  | 14.17 |  | 6.21 |  | 10.46 |  | 0 |  | 0 |  | 0 |  | 2.52% |  | 0.96% |  | No | Fail
| 96 | 96CZ16StripMall HVACPSZ HeatEff | 322.39 |  | 10.25 |  | 0.29 |  | 64.41 |  | 29.45 |  | 4.13 |  | 14.17 |  | 6.21 |  | 10.46 |  | 0 |  | 0 |  | 0 |  | 2.04% |  | 5.41% |  | No | Fail
| 97 | 97CZ16StripMall HVACPSZ EconomizerControl | 335.34 |  | 10.5 |  | 0.33 |  | 68.9 |  | 33.06 |  | 5 |  | 14.17 |  | 6.21 |  | 10.46 |  | 0 |  | 0 |  | 0 |  | -1.9% |  | -1.18% |  | No | Fail
|  | CZ06StripMallBaselinePSZ | 297.6 |  | 10.39 |  | 0.08 |  | 43.89 |  | 8.45 |  | 6.37 |  | 14.17 |  | 6.21 |  | 8.69 |  | 0 |  | 0 |  | 0
| 98 | 98CZ06StripMall HVACPSZ DXCOP | 285.34 |  | 10.09 |  | 0.08 |  | 42.88 |  | 8.45 |  | 5.36 |  | 14.17 |  | 6.21 |  | 8.69 |  | 0 |  | 0 |  | 0 |  | 4.12% |  | 2.29% |  | No | Fail
| 99 | 99CZ06StripMall HVACPSZ HeatEff | 295.87 |  | 10.39 |  | 0.08 |  | 42.95 |  | 7.51 |  | 6.37 |  | 14.17 |  | 6.21 |  | 8.69 |  | 0 |  | 0 |  | 0 |  | 0.58% |  | 2.14% |  | No
| 100 | 100CZ06StripMall HVACPSZ EconomizerControl | 306.34 |  | 10.84 |  | 0.08 |  | 45.16 |  | 8.18 |  | 7.91 |  | 14.17 |  | 6.21 |  | 8.69 |  | 0 |  | 0 |  | 0 |  | -2.93% |  | -2.9% |  | No
|  | CZ15StripMallBaselinePTAC | 363.89 |  | 12.96 |  | 0 |  | 44.23 |  | 0.53 |  | 20.19 |  | 14.17 |  | 6.21 |  | 3.14 |  | 0 |  | 0 |  | 0
| 101 | 101CZ15StripMall HVACPTAC DXCOP | 334.09 |  | 12.03 |  | 0 |  | 41.04 |  | 0.53 |  | 17 |  | 14.17 |  | 6.21 |  | 3.14 |  | 0 |  | 0 |  | 0 |  | 8.19% |  | 7.21% |  | No | Fail
|  | CZ16StripMallBaselinePTAC | 244.22 |  | 9.6 |  | 0 |  | 32.77 |  | 4.19 |  | 6.49 |  | 14.17 |  | 6.21 |  | 1.71 |  | 0 |  | 0 |  | 0
| 103 | 102CZ16StripMall HVACPTAC DXCOP | 234.27 |  | 9.3 |  | 0 |  | 31.75 |  | 4.19 |  | 5.46 |  | 14.17 |  | 6.21 |  | 1.71 |  | 0 |  | 0 |  | 0 |  | 4.07% |  | 3.13% |  | No | Fail
|  | CZ06StripMallBaselinePTAC | 260.12 |  | 9.82 |  | 0 |  | 33.5 |  | 1.08 |  | 10.17 |  | 14.17 |  | 6.21 |  | 1.87 |  | 0 |  | 0 |  | 0
| 103 | 103CZ06StripMall HVACPTAC DXCOP | 245.36 |  | 9.35 |  | 0 |  | 31.9 |  | 1.08 |  | 8.57 |  | 14.17 |  | 6.21 |  | 1.87 |  | 0 |  | 0 |  | 0 |  | 5.68% |  | 4.8% |  | No | Fail
|  | CZ15StripMallBaselinePTAC | 363.89 |  | 12.96 |  | 0 |  | 44.23 |  | 0.53 |  | 20.19 |  | 14.17 |  | 6.21 |  | 3.14 |  | 0 |  | 0 |  | 0
| 104 | 104CZ15StripMall HVACPTAC vsFanCoil | 288.16 |  | 11.08 |  | 0.01 |  | 38.35 |  | 0.53 |  | 13.43 |  | 14.17 |  | 6.21 |  | 2.58 |  | 1.22 |  | 0 |  | 0 |  | 20.81% |  | 13.29% |  | No | Fail
|  | CZ16StripMallBaselinePTAC | 244.22 |  | 9.6 |  | 0 |  | 32.77 |  | 4.19 |  | 6.49 |  | 14.17 |  | 6.21 |  | 1.71 |  | 0 |  | 0 |  | 0
| 105 | 105CZ16StripMall HVACPTAC vsFanCoil | 221.38 |  | 8.43 |  | 0.03 |  | 32.18 |  | 3.4 |  | 5.77 |  | 14.17 |  | 6.21 |  | 2.01 |  | 0.6 |  | 0 |  | 0 |  | 9.35% |  | 1.81% |  | No | Fail
|  | CZ06StripMallBaselinePTAC | 260.12 |  | 9.82 |  | 0 |  | 33.5 |  | 1.08 |  | 10.17 |  | 14.17 |  | 6.21 |  | 1.87 |  | 0 |  | 0 |  | 0
| 106 | 106CZ06StripMall HVACPTAC vsFanCoil | 247.26 |  | 9.64 |  | 0.01 |  | 33.96 |  | 1.06 |  | 9.52 |  | 14.17 |  | 6.21 |  | 1.95 |  | 0.98 |  | 0 |  | 0 |  | 4.95% |  | -1.38% |  | No | Fail