### REFERENCE METHOD-

### RULESET IMPLEMENTATION TESTS

### For 2013 ACM

### (Draft Report)

## Table of Contents

I.	Introduction	3

II.	Overview	3

III.	Labeling of Baseline Tests	4

IV.	Rule set Implementation Tests	4

V.	Results Comparison	10

## Introduction

The Compliance Margin Tests in the Reference Method suite of tests verifies that the simulation engine produces results that are within an acceptable range. The tests in this section are intended to verify that the software correctly constructs the baseline model and applies rules of the 2013 Nonresidential ACM appropriately to the proposed and baseline models. Evaluation of the modeling assumptions and baseline building tests is qualitative.

## Overview

The test runs described in this section represent the Title-24 2013 Non-Residential ACM code compliance calculation and use the following Prototype Models- Small Office Building, Medium Office Building, Large Office Building, Warehouse Building and Small Hotel. For further details on the Prototype Models, refer to Section III of the Software Compliance Specification document. Each of the baseline test cases shall be created by modifying the Prototype Model as described in Section IV of this document. The modified Prototype Model shall form the proposed case for each test run. The baseline model shall be generated by compliance software as per the rules in the 2013 Nonresidential ACM. The baseline and proposed model files for each of test cases shall then be evaluated to verify that:

- The baseline building envelope constructions are correctly substituted for exterior opaque surfaces and fenestrations.

- Fenestration area in the baseline building is reduced in accordance with the 2013 Nonresidential ACM Manual, when the proposed design fenestration area is greater than 40% of the exterior wall.

- Skylight area in the baseline building is adjusted in accordance with the 2013 Nonresidential ACM Manual, when applicable.

- Default schedules of operation are applied for both the baseline building and the proposed design.

- The proposed and baseline cases use the same defaults or tailored inputs for internal loads as required by the 2013 Nonresidential ACM Manual.

- The baseline building lighting system is correctly specified and that exterior lighting is modeled.

- Receptacle loads, process loads is modeled according to the rules in the 2013 Nonresidential ACM Manual.

- The baseline building use the correct system types as prescribed in Table_ of the 2013 Nonresidential ACM Manual.

- An economizer (of the right type) is included in the baseline building if required.

- The primary and secondary baseline building systems are properly specified and sized.

- Fan brake horsepower is correctly specified for the baseline building.

- Prescribed modeling assumptions are applied for both the baseline building and the proposed design.

- Overhangs are modeled in the proposed design for Run 7 but not the baseline building.

- Unconditioned spaces are modeled.

- Other baseline building specifications and/or modeling assumptions are correctly applied.

As the software developer verifies the above and other conditions, the input and output files should be annotated with comments or other methods to demonstrate that the modeling rules specified in the 2013 Nonresidential ACM Manual are correctly applied. Software developers should use the output format spreadsheets, included in Appendix B, to report the results of these tests. These annotated files shall then be submitted to the Commission for further evaluation. Any errors discovered shall be corrected by making modifications to the software; the runs shall be repeated; and the new results shall be annotated for submittal to the Commission.

## Labeling of Baseline Tests

The Baseline Tests are labeled using the format:

Baseline Fenestration Test/Medium Office -CZ-15, Exterior Envelope Run 01

Run name number

Climate Zone

Prototype Model Type

Test Type

## Rule set Implementation Tests

The following tests shall be performed to verify that the compliance software correctly creates the baseline model and applies modeling rules as per the requirements of the Nonresidential ACM 2013. The proposed model shall be created by modifying the appropriate Prototype Model type. The Baseline Model for each test case shall be generated automatically by the complaince software.

The intent of each test run, characteristics of the proposed model and inputs to be verified in the baseline model are described below.

- Baseline Exterior Envelope Test/Small Office-CZ-6, Run01– This test will verify that the applicant software models the  wall, floor and  roof construction correctly in the baseline model and the envelope and fenestration performance requirements for the baseline are modelled as per the requirements of NACM 2013.

The proposed model is a small office building in climate zone 6 with the following envelope characteristics-

- Low sloped concrete roof with assembly U value of  0.065, Aged Solar Reflectance of 0.75 and Thermal emittance of 0.78.

- Wood-framed wall with assembly U value of 0.090

- Mass floor with asssembly U value of 0.15.

- Fixed window with U factor of 0.25, RSHGC of 0.20 and V.T of 0.45.

The following inputs in the baseline model file shall be verified and reported in the output form provided in Appendix B-

- Baseline roof, wall and floor construction assembly type

- Baseline roof, wall and floor overall U-value

- Baseline roof, wall and floor construction assembly layer inputs

- Baseline roof aged solar reflectance and thermal emittance.

- Window U value, SHGC and V.T

- Baseline Exterior Envelope Test/Small Office-CZ-15, Run02 – This test will verify that the applicant software models the  wall, floor, roof construction and fenestrations correctly and the envelope performance requirements for the baseline are modelled as per the NACM 2013.

The proposed model is a small office building in climate zone 15 with the following envelope characteristics-

- Steep sloped metal building roof with assembly U value of  0.055, Aged Solar Reflectance of 0.60 and Thermal emittance of 0.70.

- Metal- framed wall with assembly U value of 0.056

- Slab on grade floor with florr F factor of 0.70.

- Horizontal overhang of 2 feet on south facing windows and vertical fins of 2 feet on right and left of west facing windows.

The following inputs in the baseline model file shall be verified and reported in the output form-

- Baseline roof, wall and floor construction assembly type

- Baseline roof, wall and floor construction assembly layer inputs

- Baseline roof, wall overall U-value

- Baseline floor slab F-factor.

- Baseline roof aged solar reflectance and thermal emittance.

- Window overhangs for south and west windows.

- Baseline Exterior Envelope Test/Small Hotel-CZ-15, Run03 – This test will verify that the applicant software models the  wall, floor and  roof construction correctly in the baseline model and the envelope and fenestration performance requirements for the baseline are modelled as per the requirements of NACM 2013.

The proposed model is a small hotel building in climate zone 15 with the following characteristics-

- Low sloped Metal building Roof with assembly U value of  0.055, Aged Solar Reflectance of 0.60 and Thermal emittance of 0.70

- Metal- framed wall with assembly U value of 0.8

- Mass Floor with asssembly U value of 0.052.

- Fixed windows in the first floor with U factor of 0.25, RSHGC of 0.20 and V.T of 0.47.

- Opearble windows in guest room windows with U factor of 0.42, RSHGC of 0.18 and V.T of 0.35.

The following inputs in the baseline model file shall be verified and reported in the output form-

- Baseline roof, wall and floor construction assembly type

- Baseline roof, wall and floor construction assembly layer inputs

- Baseline roof, wall and floor U-value

- Baseline roof aged solar reflectance and thermal emittance.

- Window U value, SHGC and V.T

- Baseline Fenestration Test/Large Office-CZ-6, WWR Run04 - Run 04 tests whether the applicant software determines the window area of the baseline model as per the rules in NACM 2013.

The proposed model is the Large office building in climate zone six with an overall window to wall ratio (WWR) of 60% made of a continuous band of glass distributed evenly across all facades. For this run, the building is rotated 15 degrees to the east in azimuth.

The following inputs in the baseline model file shall be verified and reported in the output form-

- Baseline WWR

- Baseline Fenestration Test/Large Office-CZ-6, WWR Run05 - Run 05 tests whether the applicant software determines the window area of the baseline model as per the rules in NACM 2013.

The proposed model is the Large office building in climate zone six with overall building WWR-30% and 45% WWR in the western façade.

The following inputs in the baseline model file shall be verified and reported in the output form-

- Baseline WWR

- Baseline Fenestration Test/Large Office-CZ-6, WWR Run06 - Run 06 tests whether the applicant software determines the window area of the baseline model as per the rules in NACM 2013.

The proposed model is the Large office building in climate zone six with overall building WWR-46% and 50% WWR in the west, 40% in South, 45% in East and 50% in the North façade.

The following inputs in the baseline model file shall be verified and reported in the output form-

- Baseline WWR

- Baseline Skylight Test/Warehouse-CZ-6, Run07 – This tests verifies whether the applicant software models the baseline skylight as per the performance requirements for skylights in NACM 2013.

The proposed model is a Warehouse building in climate zone six with the following characteristics-

- Curb mounted glass Skylight  with U value 0.55 ,SHGC 0.20  and V.T 0.40.

The following inputs in the baseline model file shall be verified and reported in the output form-

- Skylight U value, SHGC and VT.

- Baseline Skylight Test/Warehouse-CZ-6, SRR Run08 – This test checks whether the applicant software determines the skylight area of the baseline model correctly. The proposed model is a Warehouse building in climate zone 6 with an overall Skylight to roof ratio (SRR) of 10%.

The following inputs in the baseline model file shall be verified and reported in the output form-

- Baseline SRR.

- Baseline Skylight Test/Warehouse-CZ-6, SRR Run09- This test checks whether the applicant software determines the skylight area of the baseline model correctly. The proposed model is a Warehouse building in climate zone 6 - Work in Progress

- Baseline Skylight Test/Warehouse-CZ-6, SRR Run10- This test checks whether the applicant software determines the skylight area of the baseline model correctly. The proposed model is a Warehouse building in climate zone 6 -Work in Progress

- Baseline Occupancy Test/Medium Office-CZ-6, Whole Building Method Run11- This test verifies whether the applicant software inserts the correct baseline inputs for schedules, occupant density, equipment power density, lighting power density, hot water load  and  ventilation rates using the whole building method and in accordance with NACM 2013. The proposed model is an office occupancy with:

- Occupant Density- 100 ft2/person

- Equipment Power Density- 1.34 W/ft2

- Lighting Power Density- 1.2 W/ft2

- Hot Water Load- 106 Btu/person

- Ventilation Rate- 0.15 cfm/ft2

The baseline model inputs shall be verified for-

- Schedules (verified shall include occupancy schedule, lighting schedule, receptacle schedule, hot water schedule, infiltration schedule and elevator schedule)

- Occupant Density

- Equipment Power Density

- Lighting Power Density

- Hot Water Load

- Ventilation Rate

- Baseline Occupancy Test/Large Office- CZ-6, Space by Space Method Run12- This test verifies whether the applicant software inserts the correct baseline inputs for schedules, occupant density, equipment power density, lighting power density, hot water load  and  ventilation rates in accordance with NACM 2013. This run tests the capability of the applicant software to model baseline inputs for multiple space types using the Space by Space method. The proposed model is the Large office building in climate zone six with the following characteristics-

- First Floor- Retail space occupancy- Occupant Density 30 ft2/person, EPD-1W/ft2, LPD-1W/ft2, Ventilation rate- 0.25 cfm/ft2, Hot Water Load- 120 Btuh/person.

- Second Floor- Medical occupancy- Occupant Density 100 ft2/person, EPD-1.5 W/ft2, LPD-1W/ft2, Ventilation rate- 0.15 cfm/ft2, Hot Water Load- 160 Btuh/person.

- Third to 12th Floor North, South, West and East zones -Offices occupancy- Occupant Density 150 ft2/person, EPD-1.5 W/ft2, LPD-0.75 W/ft2, Ventilation rate- 0.15 cfm/ft2, Hot Water Load- 120 Btuh/person.

- Third and Fifth Floor Core zones- Lobby occupancy- Occupant Density 100 ft2/person, EPD-0.5 W/ft2, LPD-1.5 W/ft2, Ventilation rate- 0.15 cfm/ft2.

- Fourth, Seventh, 10th and 12th Floor Core Zones- Conference occupancy- Occupant Density 100 ft2/person, EPD-1.0 W/ft2, LPD-1.2 W/ft2, Ventilation rate- 0.15 cfm/ft2, Hot Water Load- 60 Btuh/person.

- Sixth, Eighth Floor Core Zone- Restroom occupancy- Occupant Density 100 ft2/person, EPD-0.2 W/ft2, LPD-0.5 W/ft2, Ventilation rate- 0.15 cfm/ft2.

- Ninth and 11th Floor Core Zones- Corridor occupancy- Occupant Density 100 ft2/person, EPD-0.2 W/ft2, LPD-0.5 W/ft2, Ventilation rate- 0.15 cfm/ft2.

- Baseline Tailored Lighting Method/Large Office-CZ-6, Run13- This test verifies if the applicant software applies the requirements of the Tailored lighting Method appropriately. Proposed Model is a large office building in climate Zone 6. - Work in Progress

- Baseline Tailored Lighting Method/Large Office-CZ-6, Run13- This test verifies if the applicant software applies the requirements of the Tailored lighting Method appropriately. Proposed Model is a large office building in climate Zone 6. - Work in Progress

- Baseline Tailored Lighting Method/Large Office-CZ-6, Run13- This test verifies if the applicant software applies the requirements of the Tailored lighting Method appropriately. Proposed Model is a large office building in climate Zone 6. - Work in Progress

- Baseline Lighting Control Test/Small Office-CZ-6, PAF Run14- This test verifies if the applicant software models lighting power density and schedules for eligible Califonia Power adjustment factors as required by the NACM2013. The proposed model is a small office building (area=5500 sq ft) with demand responsive lighting controls.The model files shall be examined to verify whether adjustment factors are applied as per the requirements in NACM 2013.

- Baseline Lighting Control Test/Large Office-CZ-6, Daylightcontrol Run15- Work in Progress

- Baseline Ext. Light, SHW Test/Large Office-CZ-6, Run16- This test verifies if the NACM rules for exterior lighting is applied accurately for Tradable and Non-Tradable surface lighting power,  exterior lighting control and schedules.  This test also verifies if the Service hot Water systems are modelled correctly. The proposed building is a large office building in climate zone 6, with a hot water load of 106 Btuh/person.  Work in Progress

- Baseline HVAC Test/Small Office-CZ-6, System Type Run17- This test  checks  if the applicant software models the baseline HVAC system in accordance with the requirements of NACM 2013. The proposed model is a small office building in climate zone 6 with the following characteristics-

- DX cooling

- Cooling COP-3.84

- Gas Furnace Heating

- Thermal Efficiency – 80%

- Constant Volume Fan

The following baseline model inputs shall be verified-

- HVAC System Type

- Heating and Cooling Type

- Heating and Cooling Efficiency

- System Sizing

- Maximum and minimum supply air temperature

- Fan Control Method

- Cooling and heating efficiency curve

- Cooling, Heating and Fan Schedule

- Baseline HVAC Test/Medium Office-CZ-6, System Type Run18- This test  checks  if the applicant software models the baseline HVAC system in accordance with the requirements of NACM 2013. The proposed model is a medium office building in climate zone 6 with the following characteristics-

- Core, Mid and Top Bottom Zones (Cooling load= 110,000 Btuh)-Electric  Heat pump  and constant volume fan.

- All Perimeter zones- DX Cooling and Hot water Boiler with reheat  and variable volume fan.

- Cooling Efficiency-

- Heating Efficiency –

The following baseline model inputs shall be verified-

- HVAC System Type

- Heating and Cooling Type

- Heating and Cooling Efficiency

- System Sizing

- Maximum and minimum supply air temperature

- Sat Reset Control

- Economizer Type and limits

- Fan Power

- Fan Control Method

- Cooling and heating capacity adjustment curve

- Cooling and heating efficiency curve

- Cooling, Heating and Fan Schedule

- Terminal heat type and capacity.

- Boiler type and Number of boilers

- Boiler Heat loss, boiler minimum unloading ratio

- Boiler Performance Curve

- Hot water supply and return temperature

- Boiler pump type

- Pump motor power and efficiency.

- Pump part load curve.

- Baseline HVAC Test/Large Office-CZ-6, System Type Run19- This test  checks  if the applicant software models the baseline HVAC system in accordance with the requirements of NACM 2013. The proposed model is a Large office building in climate zone 6 with the following characteristics-

- Basement Zone is a computer room with cooling only variable air volume system.

- All other  zones have a Built-up VAV system.

- Cooling Efficiency-

- Heating Efficiency –

The following baseline model inputs shall be verified-

- HVAC System Type

- Heating and Cooling Type

- Heating and Cooling Efficiency

- System Sizing

- Maximum and minimum supply air temperature

- Sat Reset Control

- Economizer Type and limits

- Fan Power

- Fan Control Method

- Cooling, Heating and Fan Schedule

- Terminal heat type and capacity.

- Boiler type and Number of boilers

- Boiler Heat loss, boiler minimum unloading ratio

- Boiler Performance Curve

- Hot water supply and return temperature

- Boiler pump type

- Pump motor power and efficiency.

- Pump part load curve.

- Chiller Type and Number of chillers

- Chiller fuel, capacity and efficiency

- Chiller Minimum Unloading ratio

- Chiller cooling capacity and adjustment curves

- Chilled water supply and return air temperature

- Condenser Type

- Cooling Tower Fan control type and horse power

- Cooling Tower Set Point Control

- Pump Control Type, Motor Power, Efficiency and design flow rate

- Baseline HVAC Test/Warehouse-CZ-6, System Type Run20- This test  checks  if the applicant software models the baseline HVAC system in accordance with the requirements of NACM 2013. The proposed model is a Warehouse building in climate zone 6 with the following characteristics-

- Zones are served by a gas furnace heat only system.

- Heating Efficiency –

The following baseline model inputs shall be verified-

- HVAC System Type

- Heating and Cooling Type

- Heating and Cooling Efficiency

- System Sizing

- Maximum and minimum supply air temperature

- Sat Reset Control

- Economizer Type and limits

- Fan Power

- Fan Control Method

- Cooling, Heating and Fan Schedule

## Results Comparison

The applicant shall perform all tests specified in Section IV and report the outputs in the forms provided in Appendix B.