## Sheet1
|  | Run01 |  | Run02 |  | Run03 |  | Run04 | [7 empty] | Run05 | [7 empty] | Run06 | [19 empty] | Run07 |  | Run08 |  | Run09 |  | Run10 |  | Run11 |  | Run12 | [13 empty] | Run13 |  | Run14 |  | Run15 |  | Run16 |  | Run17 |  | Run18 |  | Run19 |  |  | Run20 | [5 empty] | Run21 | [5 empty] | Run22
|  | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model |  |  |  | Baseline model |  |  |  | Proposed Model |  |  |  | Baseline model |  |  |  | Proposed Model |  |  |  | Baseline model | [15 empty] | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | [6 empty] | Baseline Model | [6 empty] | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model | Proposed Model | Baseline model |  | Proposed Model |  | Baseline model |  |  |  | Proposed Model |  | Baseline model |  |  |  | Proposed Model | Baseline model
Building Type |  | Small Office | Small Office | Small Office | Small Office | Small Hotel | Small Hotel | Large Office |  |  |  | Large Office |  |  |  | Large Office |  |  |  | Large Office |  |  |  | Large Office |  |  |  | Large Office | [15 empty] | Warehouse | Warehouse | Warehouse | Warehouse | Warehouse | Warehouse | Warehouse | Warehouse | Medium Office | Medium Office | Large Office | [6 empty] | Large Office | [6 empty] | Large Office | Large Office | Large Office | Large Office | Large Office | Large Office | Small Office | Small Office | Large Office | Large Office | Large Office | Large Office | Small Office | Small Office |  | Medium Office |  | Medium Office |  |  |  | Large Office |  | Large Office |  |  |  | Warehouse | Warehouse
Climate Zone |  | CZ-6 | CZ-6 | CZ-15 | CZ-15 | CZ-15 | CZ-15 | CZ-6 |  |  |  | CZ-6 |  |  |  | CZ-6 |  |  |  | CZ-6 |  |  |  | CZ-6 |  |  |  | CZ-6 | [15 empty] | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | [6 empty] | CZ-6 | [6 empty] | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 |  | CZ-6 |  | CZ-6 |  |  |  | CZ-6 |  | CZ-6 |  |  |  | CZ-6 | CZ-6
Envelope Components
| Roof Construction Assembly Type | Concrete Roof | Wood Framed | Metal Building | Metal Building | Metal Building | Metal Building | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model | [15 empty] | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | [6 empty] | Same as Ref. Model | [6 empty] | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  | Same as Ref. Model |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  | Same as Ref. Model |  |  |  | Same as Ref. Model | Same as Ref. Model
| Roof Construction Assembly overall U value | 0.065 | 0.075 | 0.055 | 0.065 | 0.055 | 0.065
| Roof Construction Assembly layers | 1.Single Ply Roofing Membrane (R-0.15) 2.Protective Board (R-1.06) 3. Continuous Insulation 4. Concrete Topping (Density 120 lb/ft, R-0.11/inch) 5. Fire Proofing (R-0.88) | 1.Asphalt Roofing (R-0.44) 2.Building Paper (R-0.06) 3.Wood Sheathing (R-0.48) 4.Insulation/Framing Layer (R-10.74533) 5.Air Space (R-0.8, thickness 0.3 ft) 6.Gypsum Board (R-0.45 thickness 0.0417 ft) | 1.Metal Roofing (R-0) 2.Insulation (R-) | 1.Metal Roofing (R-0) 2.Insulation (R-12.47462) | 1.Metal Roofing (R-0) 2.Insulation (R-) | 1.Metal Roofing (R-0) 2.Insulation (R-12.47462)
| Roof Aged Solar Reflectance | 0.75 | 0.65 | 0.6 | 0.2 | 0.6 | 0.55
| Roof Thermal emittance | 0.78 | 0.75 | 0.7 | 0.75 | 0.7 | 0.75
| Exterior Wall Construction Assembly Type | Wood-Framed | Metal-Framed? | Metal-Framed | Metal-Framed | Metal- Framed | Metal-Framed
| Exterior Wall Construction Assembly overall U value | 0.095 | 0.11 | 0.056 | 0.062 | 0.8 | 0.105
| Exterior Wall Construction Assembly layers | 1. Stucco 7/8" (R-0.18) 2. Building Paper (R-0.06) 3. Insulation/Framing Layer (R-15, 2x4) 4. 1/2" Gypsum Board (R-0.45) | 1. Stucco 7/8" (R-0.18) 2. Building Paper (R-0.06) 3. Continuous Insulation (R-8) 4. Metal Framing, no Insulation (R-0.66) 5. 1/2" Gypsum Board (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Continuous Insulation (R-) 4. Metal Framing, no Insulation (R-0.66) 5. 1/2" Gypsum Board (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Continuous Insulation (R-14 or 12?) 4. Metal Framing, no Insulation (R-0.66) 5. 1/2" Gypsum Board (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Continuous Insulation (R-) 4. Metal Framing, no Insulation (R-) 5. 1/2" Gypsum Board (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Continuous Insulation (R-) 4. Metal Framing, no Insulation (R-) 5. 1/2" Gypsum Board (R-0.45)
| Above-grade Floor Construction Assembly Type | Concrete Raised Floor | Steel Joist Floor | Slab -on grade | Slab-on-grade | Mass Floor | Steel Joist Floor
| Above-grade Floor Construction Assembly overall U value | 0.052 | 0.071 | NA | NA | 0.052 | 0.071
| Floor F-factor, Area and Perimeter exposed | NA | NA | 0.70, 17869.56 ft2, 1567.125 ft | 0.73, 17869.56 ft2, 1567.125 ft | NA | NA
| Above-grade Floor Construction Assembly layers | 1. R-15 Continuous Insulation 2. LW Concrete 4" 3. Metal Deck (R-0) 4. 5/8" Wood Sheathing (R-0.65) 5. Carpet with pad (R-2.08) | 1. Continuous Insulation (R-4) 2. Insulation/Framing Layer (R-6.35) 3. Wood Sheathing 5/8" (R-0.65) 4. Carpet with pad (R-2) | NA | NA | 1. R-15 Continuous Insulation 2. LW Concrete 4" 3. Metal Deck (R-0) 4. 5/8" Wood Sheathing (R-0.65) 5. Carpet with pad (R-2.08) | 1. Continuous Insulation (R-4) 2. Insulation/Framing Layer (R-6.35) 3. Wood Sheathing 5/8" (R-0.65) 4. Carpet with pad (R-2)
| Window assembly U value | 0.25 | 0.36 | Same as Ref. Model | Same as Ref. Model | Fixed-0.26, Operable-0.42 | Fixed-0.36, Operable-0.46
| Window SHGC | 0.2 | 0.25 |  |  | Fixed-0.20, Operable-0.18 | Fixed-0.25, operable-0.22
| Window VT | 0.45 | 0.42 |  |  | Fixed-0.47, Operable-0.35 | Fixed-0.42, Operable-0.32
| Window-Wall Ratio | Same as ref. Model | Same as ref. Model |  |  | Same as ref. Model | Same as ref. Model | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%]
[8 empty] | Total | 124748.7703 | 64961.5987 | 52.07 | Total | 124748.7703 | 49903.1033 | 40 | Total | 124748.7703 | 37424.6311 | 30 | Total | 124748.7703 | 36177.8527 | 29.0006 | Total | 124748.7703 | 57384.4354 | 46 | Total | 124748.7703 | 54889.4579 | 44 | Total | 124748.7703 | 50806.7725 | 40.7273 | Total | 124748.7703 | 50077.7209 | 40.1429 | Total | 124748.7703 | 49935.0239 | 40.0285
[8 empty] | North | 37424.6096 | 19488.4904 | 52.07 | North | 37424.6096 | 14970.9848 | 40 | North | 37424.6096 | 9822.7342 | 26.2467 | North | 37424.6096 | 9822.7342 | 26.2467 | North | 37424.6096 | 18712.3048 | 50 | North | 37424.6096 | 18712.3048 | 50 | North | 37424.6096 | 17011.1865 | 45.4545 | North | 37424.6096 | 16707.4151 | 44.6429 | North | 37424.6096 | 16647.958 | 44.484
[8 empty] | East | 24949.7756 | 12992.3628 | 52.07 | East | 24949.7756 | 9980.6207 | 40 | East | 24949.7756 | 6551.7637 | 26.2598 | East | 24949.7756 | 6551.7637 | 26.2598 | East | 24949.7756 | 11227.399 | 45 | East | 24949.7756 | 11227.399 | 45 | East | 24949.7756 | 10206.7266 | 40.9091 | East | 24949.7756 | 10024.4635 | 40.1786 | East | 24949.7756 | 9988.7892 | 40.0356
[8 empty] | South | 37424.6096 | 19488.4904 | 52.07 | South | 37424.6096 | 14970.9848 | 40 | South | 37424.6096 | 9822.7342 | 26.2467 | South | 37424.6096 | 9822.7342 | 26.2467 | South | 37424.6096 | 14969.8438 | 40 | South | 37424.6096 | 14969.8438 | 40 | South | 37424.6096 | 13608.9492 | 36.3636 | South | 37424.6096 | 13365.9321 | 35.7143 | South | 37424.6096 | 13318.3664 | 35.5872
[8 empty] | West | 24949.7756 | 12992.3628 | 52.07 | West | 24949.7756 | 9980.6207 | 40 | West | 24949.7756 | 11227.399 | 45 | West | 24949.7756 | 9980.6207 | 40 | West | 24949.7756 | 12474.8878 | 50 | West | 24949.7756 | 9979.9102 | 40 | West | 24949.7756 | 9979.9102 | 40 | West | 24949.7756 | 9979.9102 | 40 | West | 24949.7756 | 9979.9102 | 40
| Window overhang |  |  | South Windows- 2 feet Horizontal overhang West Windows- 2 feet Vertical overhang | None |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model
| Skylight overall U value | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA | [15 empty] | 0.55 | 0.58 | [6 empty] | NA | NA | NA | [6 empty] | NA | [6 empty] | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA |  | NA |  | NA |  |  |  | NA |  | NA |  |  |  | NA | NA
| Skylight SHGC | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA | [15 empty] | 0.2 | 0.25 | [6 empty] | NA | NA | NA | [6 empty] | NA | [6 empty] | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA |  | NA |  | NA |  |  |  | NA |  | NA |  |  |  | NA | NA
| Skylight VT | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA | [15 empty] | 0.4 | 0.49 | [6 empty] | NA | NA | NA | [6 empty] | NA | [6 empty] | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA |  | NA |  | NA |  |  |  | NA |  | NA |  |  |  | NA | NA
| Skylight to Roof Ratio | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA | [15 empty] | Same as Ref. Model | Same as Ref. Model | 10% | [5 empty] | NA | NA | NA | [6 empty] | NA | [6 empty] | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA |  | NA |  | NA |  |  |  | NA |  | NA |  |  |  | NA | NA
Internal Load Components
| Occupancy Type | [50 empty] | Office | Office | Retail | Medical | Office | Conference Room | Corridor | Rest Room | Lobby | Retail | Medical | Office | Conference Room | Corridor | Rest Room | Lobby | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  | Same as Ref. Model |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  | Same as Ref. Model |  |  |  | Same as Ref. Model | Same as Ref. Model
| People Density | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model | [15 empty] | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | 100 ft2/person | 100 ft2/person | 33 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 67 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 33 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 67 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2
| Sensible Heat/person | [50 empty] | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 245 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 245 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant
| Latent Heat/person | [50 empty] | 206 Btu/occupant | 206 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 155 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 155 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant
| Equipment Power Density | [50 empty] | 1.34 W/ft2 | 1.34 W/ft2 | 1 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | 1 W/ft2 | 0.2 W/ft2 | 0.2 W/ft2 | 0.5 W/ft2 | 1 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | 1 W/ft2 | 0.2 W/ft2 | 0.2 W/ft2 | 0.5 W/ft2
| Lighting Power Density | [50 empty] | 1.2 W/ft2 | 0.8 W/ft2 | 1W/ft2 | 1 W/ft2 | 0.75 W/ft2 | 1.2 W/ft2 | 0.6 W/ft2 | 0.5 W/ft2 | 1.5 W/ft2 | 1.2 W/ft2 | 1.2 W/ft2 | 0.75 W/ft2 | 1.4 W/ft2 | 0.6 W/ft2 | 0.6 W/ft2 | 1.5 W/ft2 | [6 empty] | 0.9 W/ft2 * (1-0.05) | 0.9 W/ft2
| Ventilation Rate | [50 empty] | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.25 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.5 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.25 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.5 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model
| Hot-water Load | [50 empty] | 106 Btu/person | 106 Btu/person | 120 Btuh/person | 160 Btuh/person | 120 Btuh/person | 60 Btuh/person | 0 | 0 | NA | 120 Btuh/person | 160 Btuh/person | 120 Btuh/person | 60 Btuh/person | 0 | 0 | 60 Btuh/person
Infiltration rate (Work in Progress)
| Elevator Power | [50 empty] | 32 kW | 32kW | NA | NA | NA | NA | NA | NA | 244 kW | NA | NA | NA | NA | NA | NA | 244 kW
| Occupancy Schedule | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly
| Equipment Schedule | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly
| Lighting Schedule | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | [6 empty] | Office | Office
| Hot Water Schedule | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model
| Infiltration(Work in Progress) | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly
| Elevator | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | [12 empty] | NA | NA | [13 empty] | NA | NA
HVAC Components
| HVAC System Type | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model | [23 empty] | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | [6 empty] | Same as Ref. Model | [16 empty] | Same as Ref. Model | Same as Ref. Model | PSZ AC | PSZ AC (System 3) |  | PVAV with Reheat | VAV HP | PVAV with Reheat (System 5) |  | SZVAV HP (System 8) |  | Built-up VAV with Reheat | Variable Air Volume System | VAV with Reheat (System 6) |  | CRAH Unit (System 10) |  | PSZ, no cooling | Heating Ventilation (System 9)
| Heating Type | [78 empty] | Gas Furnace | Gas Furnace |  | Hot Water boiler with reheat | Heat Pump | Hot Water boiler with reheat |  | Heat Pump |  | Fossil Fuel | None | Hot Water boiler with reheat |  | None |  | Electric Heat pump | Gas Furnace
| Cooling Type | [78 empty] | DX | Direct Expansion (DX) |  | DX | Heat Pump | DX |  | Heat Pump |  | Chilled Water | Chilled Water | Chilled Water |  | Chilled Water |  | NA | NA
| Cooling Efficiency | [78 empty] | COP-3.84 | Input Based on Proposed System Size- | Final input based on sizing Run- | TBD | TBD | Input Based on Proposed System Size- | Final input based on sizing Run- | Input Based on Proposed System Size- | Final input based on sizing Run- | TBD | TBD | Input Based on Proposed System Size- | Final input based on sizing Run- | Input Based on Proposed System Size- | Final input based on sizing Run- | NA | NA
| Heating Efficiency | [78 empty] | 80% | Input Based on Proposed System Size- | Final input based on sizing Run- | TBD | TBD | Input Based on Proposed System Size- | Final input based on sizing Run- | Input Based on Proposed System Size- | Final input based on sizing Run- | TBD | TBD | Input Based on Proposed System Size- | Final input based on sizing Run- | Input Based on Proposed System Size- | Final input based on sizing Run- | TBD | Input Based on Proposed System Size- | Final input based on sizing Run-
| System Capacity | [78 empty] | Heating Capacity- Cooling Capacity- | Heating- 1.25 Cooling- 1.15 |  | Heating Capacity- Cooling Capacity- | Heating Capacity- Cooling Capacity-110,000 Btuh | Heating- 1.25 Cooling- 1.15 |  | Heating- 1.25 Cooling- 1.15 |  | Heating Capacity- Cooling Capacity- | Cooling Capacity- 650,000 Btuh | Heating- 1.25 Cooling- 1.15 |  | Heating- 1.25 Cooling- 1.15 |  | TBD | Heating- 1.25
| Supply Air Temperature | [78 empty] | Heating - 105F Cooling - 55F | Heating- 105F Cooling- 55F |  | TBD Cooling - 55F | TBD Cooling - 55F | Heating- 70F Cooling- 55F |  | Heating- (ACM not clear) Cooling- 55F |  | Heating- 70F Cooling- 55F | Heating- 80F Cooling- 60F | Heating- 70F Cooling- 55F |  | Heating- 80F Cooling- 60F |  | Heating- 100F Cooling- NA | Heating- 100F Cooling- NA
| SAT Reset Control | [78 empty] | Fixed | Heating- Fixed, Cooling- Fixed |  | Heating- Fixed, Cooling- TBD |  | Heating- Fixed Cooling- Reset by outside dry-bulb temperature. |  | Heating- Fixed Cooling- Reset by outside dry-bulb temperature. (not clear in ACM) |  | Heating- Cooling- |  | Heating- Fixed Cooling- Reset by outside dry-bulb temperature. |  | Heating- Fixed Cooling- Reset by outside dry-bulb temperature. (not clear in ACM) |  | NA | NA
| Economizer | [78 empty] | None |  | Final input based on sizing Run- | TBD | TBD |  | Final input based on sizing Run- |  | Final input based on sizing Run- | TBD | TBD |  | Final input based on sizing Run- |  | Final input based on sizing Run- | None | TBD
| Economizer Limits | [78 empty] | NA |  | Final input based on sizing Run- | TBD | TBD |  | Final input based on sizing Run- |  | Final input based on sizing Run- | TBD | TBD |  | Final input based on sizing Run- |  | Final input based on sizing Run- | None | TBD
| Fan Power | [81 empty] | TBD | TBD | TBD | Final input based on sizing Run- | TBD | Final input based on sizing Run- | TBD | TBD | TBD | Final input based on sizing Run- | TBD | Final input based on sizing Run- | TBD | TBD | Final input based on sizing Run-
| Fan Control Method | [78 empty] | Constant Volume | Constant Volume |  | Variable flow, VSD | Constant Volume | Variable flow, VSD |  | Variable flow, Two-speed drive |  | Variable-flow, VSD | Variable-flow, VSD | Variable-flow, variable speed drive |  | Variable-flow, variable speed drive |  | Constant Volume | Constant Volume
| DX Cooling Efficiency Adjustment Curve | [78 empty] | Default | Default |  | Default | Default | Default |  | Default |  | NA | NA | NA |  | NA |  | NA | NA
| Cooling Capacity Adjustment Curve | [78 empty] | Default | Default |  | Default | Default | Default |  | Default |  | NA | NA | NA |  | NA |  | NA | NA
| Heating (Furnace) Part-load Efficiency Curve | [78 empty] | Fixed | Fixed |  | NA |  | NA |  | NA |  | NA | NA | NA |  | NA |  | NA | Default
| Electric Heat Pump Heating Capacity Adjustment Curve | [78 empty] | NA | NA |  | NA | Default | NA |  | Default |  | NA | NA | NA |  | NA |  | Default | NA
| Electric Heat Pump Heating Efficiency Adjustment Curve | [78 empty] | NA | NA |  | NA | Default | NA |  | Default |  | NA | NA | NA |  | NA |  | Default | NA
| Fan Part-load Performance Curve | [78 empty] | NA | NA |  | TBD | TBD | Any Fan with VSD |  | (ACM not clear) |  |  |  | Any Fan with VSD |  | (ACM not clear) |  | NA | NA
| HVAC(Availability/Fan) Schedule | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  |  |  | Office | Office |  | Office | Office | Office |  | Office |  | Office | Office | Office |  | Office |  | Office | Office
| Cooling Schedule | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  |  |  | Office | Office |  | Office | Office | Office |  | Office |  | Office | Office | Office |  | NA |  | NA | NA
| Heating Schedule | [50 empty] | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  |  |  | Office | Office |  | Office | Office | Office |  | Office |  | Office | Office | Office |  | Office |  | Office | Office
| Terminal Heat Type | [78 empty] | NA | NA |  | Hot Water | NA | Hot Water |  | NA |  | Hot Water | NA | Hot Water |  | NA |  | NA | NA
| Terminal Heat Capacity | [78 empty] | NA | NA |  | TBD | NA | 1.25 |  | NA |  | TBD | NA | 1.25 |  | NA |  | NA | NA
| Reheat Delta T | [78 empty] | NA | NA |  | TBD | NA | NA |  | NA |  | TBD | NA | NA |  | NA |  | NA | NA
Boiler Components
| Number of boilers | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | 1 | NA | 1 |  | NA |  | 1 | NA | 1 |  | NA |  | NA | NA
| Boiler Capacity | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  |  | NA | 1.25 |  | NA |  |  | NA | 1.25 |  | NA |  | NA | NA
| Boiler Efficiency | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | TBD | NA | Input Based on Proposed System Size- | Final input based on sizing Run- | NA |  | TBD | NA | Input Based on Proposed System Size- | Final input based on sizing Run- | NA |  | NA | NA
| Boiler Type | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | Hot Water Boiler | NA | Hot Water Boiler |  | NA |  | Hot Water Boiler | NA | Hot Water Boiler |  | NA |  | NA | NA
| Boiler Heat Loss | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | 0% | NA | 0% |  | NA |  | 0% | NA | 0% |  | NA |  | NA | NA
| Boiler Performance Curve | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | Default Curve | NA | Default |  | NA |  | Default Curve | NA | Default |  | NA |  | NA | NA
| Boiler Min. Unloading Ratio | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | 25% | NA | 25% |  | NA |  | 25% | NA | 25% |  | NA |  | NA | NA
| Hot Water Supply Temperature | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | TBD | NA | 180F |  | NA |  | TBD | NA | 180F |  | NA |  | NA | NA
| Hot Water Return Temperature | [78 empty] | NA | NA |  | TBD | NA | 130F |  | NA |  | TBD | NA | 130F |  | NA |  | NA | NA
| Pump Control Type | [81 empty] | Fixed Speed Variable flow pump (Intermittent/CF) |  | Fixed Speed Variable Flow pump (Intermittent/CF) |  | NA |  | Fixed Speed Variable flow pump (Intermittent/CF) |  | Fixed Speed Variable Flow pump (Intermittent/CF) |  |  |  | NA | NA
| Pump Motor Power | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | TBD | NA | 19 W/gpm |  | NA |  | TBD | NA | 19 W/gpm |  | NA |  | NA | NA
| Pump Motor Efficiency | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | TBD | NA | TBD |  | NA |  | TBD | NA | TBD |  | NA |  | NA | NA
| Pump Part Load Curve | [81 empty] | Default Curve | NA | Default |  | NA |  | Default Curve | NA | Default |  | NA |  | NA | NA
Chiller Components
| Chiller Type | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | Centrifugal chiller | Scroll Chiller | Centrifugal Chiller |  | Scroll Chiller |  | NA | NA
| Number of Chillers | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | 2 | 1 | 2 |  | 1 |  | NA | NA
| Chiller Fuel | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | Electricity |  | Electricity |  |  |  | NA | NA
| Chiller Capacity | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | TBD | TBD | 1.15 |  | 1.15 |  | NA | NA
| Chiller Efficiency | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | TBD | TBD | TBD |  | TBD |  | NA | NA
| Chiller Min. Unloading Ratio | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | 10% | 25% | 10% |  | 25% |  | NA | NA
| Chiller Cooling Capacity Adjustment Curve | [83 empty] | NA |  |  |  | Default | Default | Default |  | Default |  | NA | NA
| Chiller Cooling Efficiency Adjustment Curve | [83 empty] | NA |  |  |  | Default | Default | Default |  | Default |  | NA | NA
| Chilled Water Supply Temperature | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | TBD | TBD | 44F |  | 44F |  | NA | NA
| Chilled Water ReturnTemperature | [83 empty] | NA |  |  |  | TBD | TBD | 56F |  | 56F |  | NA | NA
| Condensor Type | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | Water-cooled | Water-cooled | Water-cooled |  | Water-cooled |  | NA | NA
| Cooling tower Fan Control Type | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | TBD | TBD | Open Tower axial with two-speed fan |  | Open Tower axial with two-speed fan |  | NA | NA
| Cooling Tower Fan Horse Power | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA |  |  |  | TBD | TBD | TBD |  | TBD |  | NA | NA
| Cooling Tower Set Point Control | [78 empty] | NA | NA |  | NA |  | NA |  |  |  | 70F | 70F | 70F |  | 70F |  | NA | NA
| Chiller, Condenser Pump Control Type | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA | [5 empty] | Chilled-water pump- Variable Speed, Variable flow Condenser Water-Fixed Speed |  | Chilled-water pump- Variable Speed, Variable flow Condenser Water-Fixed Speed |  | NA | NA
| Chiller, Condenser Pump Motor Power | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA | [5 empty] | Chilled-water pump- 22W/gpm Condenser Water-19W/gpm |  | Chilled-water pump- 22W/gpm Condenser Water-19W/gpm |  | NA | NA
| Chiller, Condenser Pump Motor Efficiency | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA | [5 empty] | TBD |  | TBD |  | NA | NA
| Chiller, Condenser Pump Design Flow | NA | NA | NA | NA | NA | NA | [44 empty] | NA | NA | [26 empty] | NA | NA |  | NA |  | NA | [5 empty] | Chiller- 2 gpm/ton Condenser-2.4 gpm/ton |  | Chiller- 2 gpm/ton Condenser-2.4 gpm/ton |  | NA | NA
Service Hot Water
| Thermal Efficiency | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model | [23 empty] | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | [6 empty] | Same as Ref. Model | [6 empty] | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | 0.78 | 0.78 | Same as Ref. Model | Same as Ref. Model |  | Same as Ref. Model |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  | Same as Ref. Model |  |  |  | Same as Ref. Model | Same as Ref. Model
| Energy Factor | [76 empty] | TBD | 0.67-0.0019XV
| Hot Water Load/person | [76 empty] | 106 Btuh/person | 106 Btuh/person
| SHW Schedule | [76 empty] | Office | Office
Exterior Load
| Exterior LPD- Tradable Surface | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  |  |  | Same as Ref. Model | [23 empty] | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | [6 empty] | Same as Ref. Model | [6 empty] | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model | Same as Ref. Model |  |  | Same as Ref. Model | Same as Ref. Model |  | Same as Ref. Model |  | Same as Ref. Model |  |  |  | Same as Ref. Model |  | Same as Ref. Model |  |  |  | Same as Ref. Model | Same as Ref. Model
Exterior LPD- Non-tradable Surface
| Exterior lighting schedule | [77 empty] | Same as Proposed
Note on B77: Nambiar, Chitra: Sizing will be at either system or palnt level, not both.
Note on B82: Nambiar, Chitra: This input is not an option in E+ HVAc Template:Plant:Boiler object.

## Sheet2
m/ft | 0.3048
m²/ft² | 0.092903
Proposed | Total | North (315 to 45 deg) | East (45 to 135 deg) | South (135 to 225 deg) | West (225 to 315 deg)
Gross Wall Area [m2] | 11589.54 | 3476.86 | 2317.91 | 3476.86 | 2317.91
Window Opening Area [m2] | 6035.13 | 1810.54 | 1207.03 | 1810.54 | 1207.03
Window-Wall Ratio [%] | 52.07 | 52.07 | 52.07 | 52.07 | 52.07
Orientation | Gross Wall Area [ft2] | Window Opening Area [ft2] | Window-Wall Ratio [%]
Total | 124748.7703 | 64961.5987 | 52.07
North (315 to 45 deg) | 37424.6096 | 19488.4904 | 52.07
East (45 to 135 deg) | 124748.7703 | 12992.3628 | 52.07
South (135 to 225 deg) | 37424.6096 | 19488.4904 | 52.07
West (225 to 315 deg) | 124748.7703 | 12992.3628 | 52.07
| Total | North (315 to 45 deg) | East (45 to 135 deg) | South (135 to 225 deg) | West (225 to 315 deg)
Gross Wall Area [m2] | 11589.54 | 3476.86 | 2317.91 | 3476.86 | 2317.91
Window Opening Area [m2] | 4636.15 | 1390.85 | 927.23 | 1390.85 | 927.23
Window-Wall Ratio [%] | 40 | 40 | 40 | 40 | 40
Orientation | Gross Wall Area [ft2] | Window Opening Area [ft2] | Window-Wall Ratio [%]
Total | 124748.7703 | 49903.1033 | 40
North (315 to 45 deg) | 37424.6096 | 14970.9848 | 40
East (45 to 135 deg) | 24949.7756 | 9980.6207 | 40
South (135 to 225 deg) | 37424.6096 | 14970.9848 | 40
West (225 to 315 deg) | 24949.7756 | 9980.6207 | 40