## Whole Bldg New
2013 NACM | People | Sensible heat | Latent heat | Receptacle | Receptacle Inventory Coefficients |  |  | Hot water | Lighting | Ventilation | Gas Appl Load | Refrig Load | Schedule
| # per 1000 ft² | per person | per person | Load W/ft² | C | PDMisc | D | Btu/h per person | W/ft² | CFM/ft² | Btu/h-ft2 | W/ft2
Auditorium Building | 143 | 245 | 105 | 1 | 2 | 0.54813 | 0.779 | 60 | 1.5 | 1.07 | 0.04 | 0.03 | Assembly
Classroom Building | 40 | 246 | 171 | 1 | 2 | 0.18581 | 0.773 | 108 | 1.1 | 0.32 | 0.04 | 0.03 | School
Commercial and Industrial Storage Buildings | 5 | 268 | 403 | 0.43 | 2 | 0.18581 | 1 | 108 | 0.6 | 0.15 | 0 | 0.28 | Warehouse
Convention Center Building | 136 | 245 | 112 | 0.96 | 2 | 0.54813 | 0.779 | 57 | 1.2 | 1.02 | 0.04 | 0.03 | Assembly
Data Center Buildings (note 9) | 5 | 268 | 403 | note 9 | N/A | N/A | N/A | 108 | 0.8 | 0.15 | 0 | 0 | Data Center
Financial Institution Buildings | 10 | 250 | 250 | 1.5 | 2 | 0.7711 | 0.923 | 120 | 1.1 | 0.15 | 0.04 | 0.06 | Office
General Commercial Building/Industrial Work Buildings | 7 | 375 | 625 | 1 | 2 | 0.18581 | 1 | 120 | 1 | 0.15 | 0 | 0.28 | Light Manuf
Grocery Store Buildings | 29 | 252 | 225 | 0.91 | N/A | N/A | N/A | 113 | 1.5 | 0.22 | 0.03 | 0.14 | Retail
Library Building | 10 | 250 | 250 | 1.5 | 2 | 0.18581 | 0.779 | 120 | 1.3 | 0.15 | 0.04 | 0.03 | Office
Medical Building/Clinic Building | 10 | 250 | 213 | 1.18 | 2 | 0.76181 | 0.962 | 110 | 1.1 | 0.15 | 0.33 | 1.12 | Health
Office Building | 10 | 250 | 206 | 1.34 | 2 | 0.7711 | 0.923 | 106 | 0.8 | 0.15 | 0.04 | 0.06 | Office
Parking Garage Building | 10 | 250 | 200 | 0 | 2 | 0.54813 | 1 | 0 | 0.2 | 0.15 | 0 | 0 | Parking
Religious Facility Buildings | 136 | 245 | 112 | 0.96 | 2 | 0.54813 | 0.779 | 57 | 1.6 | 1.03 | 0.04 | 0.03 | Assembly
Restaurant Buildings | 45 | 274 | 334 | 0.79 | 2 | 0.92903 | 1 | 366 | 1.2 | 0.38 | 5.14 | 0.06 | Restaurant
School Building | 40 | 246 | 171 | 1 | 2 | 0.18581 | 0.773 | 108 | 1 | 0.32 | 0.04 | 0.03 | School
Theater Building | 130 | 268 | 403 | 0.54 | 2 | 0.54813 | 0.779 | 60 | 1.3 | 0.98 | 0.04 | 0.03 | Assembly
All other buildings | 10 | 250 | 200 | 1 | 2 | 0.54813 | 0.779 | 120 | 0.6 | 0.15 | 0.04 | 0.03 | Office
Note 9 - Receptacle Load shall be specified by the user.

## Space-by-Space New
2013 NACM Space Type | People | Sensible heat | Latent heat | Receptacle | Receptacle Inventory Coefficients |  |  | Hot water | Lighting | Ventilation | Process Load | Refrig Load | Schedule
| # per 1000 ft² | per person | per person | Load W/ft² | C | PDMisc | D | Btu/h per person | W/ft² | CFM/ft² | Btu/h-ft2 | W/ft2
Auditorium Area (Note 10) | 143 | 245 | 105 | 1 | 2 | 0.54813 | 1 | 60 | 1.5 | 1.07 | 0.04 | 0.03 | Assembly
Auto Repair Area | 10 | 275 | 475 | 1 | 2 | 0.54813 | 1 | 120 | 0.9 | 1.5 | 0.22 | 0.15 | Light Manuf
Bar, Cocktail Lounge and Casino Areas (Note 10) | 67 | 275 | 275 | 1 | 2 | 0.92903 | 1 | 120 | 1.1 | 0.5 | 5.14 | 0.06 | Restaurant
Beauty Salon Area | 10 | 250 | 200 | 2 | N/A | N/A | N/A | 120 | 1.7 | 0.4 | 0 | 0 | Retail
Classrooms, Lecture, Training, Vocational Areas | 50 | 245 | 155 | 1 | 2 | 0.14865 | 1 | 120 | 1.2 | 0.38 | 0.04 | 0.03 | School
Civic Meeting Place Area (Note 10) | 25 | 250 | 200 | 1.5 | 2 | 1.1148 | 1 | 120 | 1.3 | 0.19 | 0.09 | 2.6 | Assembly
Commercial and Industrial Storage Areas (conditioned or unconditioned) | 3 | 275 | 475 | 0.2 | 2 | 0.18581 | 1 | 120 | 0.6 | 0.15 | 0 | 0.28 | Warehouse
Commercial and Industrial Storage Areas (refrigerated) | 1 | 275 | 475 | 0.2 | 2 | 0.18581 | 1 | 0 | 0.7 | 0.15 | 0 | 0.28 | Warehouse
Computer Room (Note 11) | 3 | 275 | 475 | 0 | N/A | N/A | N/A | 120 | 0.8 | 0.15 | 0 | 0 | Data Center
Convention, Conference, Multipurpose and Meeting Center Areas (Note 10) | 67 | 245 | 155 | 1 | 2 | 0.54813 | 1 | 60 | 1.4 | 0.5 | 0.04 | 0.03 | Assembly
Corridors, Restrooms, Stairs, and Support Areas | 10 | 250 | 250 | 0.2 | 2 | 0.54813 | 1 | 0 | 0.6 | 0.15 | 0 | 0 | Office
Dining Area (Note 10) | 67 | 275 | 275 | 0.5 | 2 | 0.92903 | 1 | 385 | 1.1 | 0.5 | 5.14 | 0.06 | Restaurant
Dry Cleaning (Coin Operated) | 10 | 250 | 250 | 3 | 2 | 0.54813 | 1 | 120 | 0.9 | 0.3 | 0.22 | 0.15 | Light Manuf
Dry Cleaning (Full Service Commercial) | 10 | 250 | 250 | 3 | 2 | 0.54813 | 1 | 120 | 0.9 | 0.45 | 0.22 | 0.15 | Light Manuf
Electrical, Mechanical, Telephone Rooms | 3 | 250 | 250 | 0.2 | N/A | N/A | N/A | 0 | 0.7 | 0.15 | N/A | N/A | Warehouse
Exercise Center, Gymnasium Areas | 67 | 255 | 875 | 0.5 | 2 | 0.54813 | 1 | 120 | 1 | 0.5 | 0.04 | 0.03 | Retail
Exhibit, Museum Areas (Note 10) | 67 | 250 | 250 | 1.5 | 2 | 0.54813 | 1 | 60 | 2 | 0.5 | 0.04 | 0.03 | Assembly
Financial Transaction Area | 10 | 250 | 250 | 1.5 | 2 | 0.7711 | 1 | 120 | 1.2 | 0.15 | 0.04 | 0.06 | Office
General Commercial and Industrial Work Areas, High Bay | 10 | 275 | 475 | 1 | N/A | N/A | N/A | 120 | 1 | 0.15 | N/A | N/A | Light Manuf
General Commercial and Industrial Work Areas, Low Bay | 10 | 275 | 475 | 1 | N/A | N/A | N/A | 120 | 0.9 | 0.15 | N/A | N/A | Light Manuf
General Commercial and Industrial Work Areas, Precision | 10 | 250 | 200 | 1 | N/A | N/A | N/A | 120 | 1.2 | 0.15 | N/A | N/A | Light Manuf
Grocery Sales Areas (Note 10) | 33 | 250 | 200 | 1 | 2 | 0.47381 | 1 | 120 | 1.2 | 0.25 | 0.35 | 0.05 | Retail
High-Rise Residential Living Spaces (9) | 5 | 245 | 155 | 0.5 | 2 | 0.29729 | 1 | note 7 | 0.5 | 0.15 | 0.2 | 0.08 | High-Rise Residential
Hotel Function Area (Note 10) | 67 | 250 | 200 | 0.5 | 2 | 0.54813 | 1 | 60 | 1.5 | 0.5 | 0.04 | 0.03 | Hotel Function
Hotel/Motel Guest Room (9) | 5 | 245 | 155 | 0.5 | 2 | 0.29729 | 1 | 2800 | 0.5 | 0.15 | 0.2 | 0.08 | Residential w/ Setback
Housing, Public and Common Areas: Multi-family, Dormitory | 10 | 250 | 250 | 0.5 | 2 | 0.29729 | 1 | 120 | 1 | 0.15 | 0.2 | 0.08 | Residential w/o Setback
Housing, Public and Common Areas:, Senior Housing | 10 | 250 | 250 | 0.5 | 2 | 1.1148 | 1 | 120 | 1.5 | 0.15 | 0.33 | 0.08 | Residential w/o Setback
Kitchen, Food Preparation | 5 | 275 | 475 | 1.5 | 2 | 0.92903 | 1 | 385 | 1.6 | 0.15 | 5.14 | 0.06 | Restaurant
Laboratory, Scientific | 10 | 250 | 200 | 3.96 | 2 | 2.7871 | 1 | 120 | 1.4 | 0.38 | 3.72 | 0.06 | Lab
Laundry | 10 | 250 | 250 | 3 | 2 | 0.54813 | 1 | 385 | 0.9 | 0.15 | 0.22 | 0.15 | Light Manuf
Library, Reading Areas | 20 | 250 | 200 | 1.5 | 2 | 0.54813 | 1 | 120 | 1.2 | 0.15 | 0.04 | 0.03 | Office
Library, Stacks | 10 | 250 | 200 | 1.5 | 2 | 0.54813 | 1 | 120 | 1.5 | 0.15 | 0.04 | 0.03 | Office
Lobby, Hotel | 10 | 250 | 250 | 0.5 | 2 | 0.29729 | 1 | 120 | 1.1 | 0.15 | 0.2 | 0.08 | Assembly
Lobby, Main Entry | 10 | 250 | 250 | 0.5 | N/A | N/A | N/A | 60 | 1.5 | 0.15 | N/A | N/A | Assembly
Locker/Dressing Room | 20 | 255 | 475 | 0.5 | 2 | 0.54813 | 1 | 385 | 0.8 | 0.15 | N/A | N/A | Assembly
Lounge, Recreation (Note 10) | 67 | 275 | 275 | 1 | 2 | 0.54813 | 1 | 60 | 1.1 | 0.5 | 0.04 | 0.03 | Assembly
Malls and Atria (Note 10) | 33 | 250 | 250 | 0.5 | N/A | N/A | N/A | 120 | 1.2 | 0.25 | 0 | 0 | Retail
Medical and Clinical Care | 10 | 250 | 200 | 1.5 | 2 | 0.76181 | 1 | 160 | 1.2 | 0.15 | 0.33 | 1.12 | Health
Office (Greater than 250 square feet in floor area) | 10 | 250 | 200 | 1.5 | 2 | 0.7711 | 1 | 120 | 0.75 | 0.15 | 0.04 | 0.06 | Office
Office (250 square feet in floor area or less) | 10 | 250 | 200 | 1.5 | 2 | 0.7711 | 1 | 120 | 1 | 0.15 | 0.04 | 0.06 | Office
Parking Garage Building, Parking Area | 10 | 250 | 200 | 0 | N/A | N/A | N/A | 0 | 0.14 | 0.15 | 0 | 0 | Parking
Parking Garage Area Dedicated Ramps | 10 | 250 | 200 | 0 | N/A | N/A | N/A | 0 | 0.3 | 0.15 | 0 | 0 | Parking
Parking Garage Area Daylight Adaptation Zones | 10 | 250 | 200 | 0 | N/A | N/A | N/A | 0 | 0.6 | 0.15 | 0 | 0 | Parking
Police Station and Fire Station | 10 | 250 | 200 | 1.5 | 2 | 1.1148 | 1 | 120 | 0.9 | 0.15 | N/A | N/A | High-Rise Residential
Religious Worship Area (Note 10) | 143 | 245 | 105 | 0.5 | 2 | 0.54813 | 0.4 | 60 | 1.5 | 1.07 | 0.04 | 1.53 | Assembly
Retail Merchandise Sales, Wholesale Showroom (Note 10) | 33 | 250 | 200 | 1 | N/A | N/A | N/A | 120 | 1.2 | 0.25 | N/A | N/A | Retail
Sports Arena, Indoor Playing Area | 143 | 245 | 105 | 1 | 2 | 0.34374 | 1 | 60 | 2.3 | 1.07 | 0.03 | 0.14 | Assembly
Tenant Lease Space | 10 | 250 | 200 | 1.5 |  |  |  | 120 | 1 | 0.15 |  |  | Office
Theater, Motion Picture) (Note 10) | 143 | 245 | 105 | 0.5 | 2 | 0.54813 | 0.779 | 60 | 0.9 | 1.07 | 0.04 | 0.03 | Assembly
Theater, Performance) (Note 10) | 143 | 245 | 105 | 0.5 | 2 | 0.54813 | 1 | 60 | 1.4 | 1.07 | 0.04 | 0.03 | Assembly
Transportation Function (Note 10) | 33 | 250 | 250 | 0.5 | 2 | 0.54813 | 1 | 120 | 1.2 | 0.25 | 0.04 | 0.03 | Assembly
Videoconferencing Studio (Note S1) | 10 | 250 | 200 | 1.5 | N/A | N/A | N/A | 120 | 1.2 | 0.15 | 0 | 0 | Office
Waiting Area | 10 | 250 | 250 | 0.5 | 2 | 0.54813 | 1 | 120 | 1.1 | 0.15 | 0 | 0 | Office
All Others (including unleased tenant space in multi-tenant facilities) | 10 | 250 | 200 | 1 | N/A | N/A | N/A | 120 | 0.6 | 0.15 | 0 | 0 | Office
| [i] | From Benya, July 2006 Workshop, Changes to Lighting Power Density Values: Bringing Certain Values in Line with Standard 90.1, http://www.energy.ca.gov/title24/2008standards/documents/2006-07-12_workshop/MEASURE_BLD_02.PDF
Note 11: data center equipment shall be specified by the user as process load.
| Note 10. | For these occupancies, when the proposed design is required to have demand control ventilation by §121(c) 3 the ventilation rate is the minimum that would occur at any time during occupied hours. Additional ventilation
would be provided through demand controlled ventilation to maintain CO2 levels according to §120.1.
| Note 11. | For data centers the process load from the servers and UPS shall be as designed, with the baseline same as proposed.
| Note S1: | Videoconferencing studios may install up to an additional 1.5 W/ft2 for videoconferencing rooms that meet all requirements in section 140.6(c)2Gvii.