## Curve Fit Data
Appendix 5.7 Equipment Performance Curves (DRAFT)
Some details and explanatory notes will be added, and min and max inputs for curves will be added as well. All curve fit information will be moved
to this Appendix.
Building Descriptor | Curve | Type | Variables | Input Min and Max | a | b | c | d | e | f | g | h | i | j
Fan Part-Flow Power Curve | FAN-FPLR | AF or BI Riding the Curve | FPLR | 0.70, 1 | a: 0.1631; b: 1.5901; c: -0.8817; d: 0.1281
|  | AF or BI inlet vanes | FPLR | 0.50,1 | a: 0.9977; b: -0.659; c: 0.9547; d: -0.2936
|  | FC riding the curve | FPLR | 0.30,1 | a: 0.1224; b: 0.612; c: 0.5983; d: -0.3334
|  | FC with inlet vanes | FPLR | 0.30,1 | a: 0.3038; b: -0.7608; c: 2.2729; d: -0.8169
|  | Vane-axial with variable pitch blades | FPLR | 0.20,1 | a: 0.1639; b: -0.4016; c: 1.9909; d: -0.7541
|  | Any fan with VSD | FPLR | 0.20,1 | a: 0.0013; b: 0.147; c: 0.9506; d: -0.0998
|  | VSD with static pressure reset | FPLR | 0.20,1 | a: -0.0031; b: 0.0991; c: 1.0268; d: -0.1128
Cooling Capacity Adjustment Curve | COOL-CAP-FT | Air-Source (PTAC) | Twb, Todb |  | 1.1839 | -0.0081087 | 0.000211 | -0.0061435 | 1.6e-06 | -3e-06
|  | Air-Source (Other DX)) | Twb, Todb |  | 0.87403 | -0.0011416 | 0.0001711 | -0.002957 | 1.02e-05 | -5.92e-05
|  | Water-Source (Heat Pump) | Twb, Twt |  | -0.27804 | 0.024831 | -9.5e-06 | -0.0032731 | 7e-06 | -2.72e-05
|  | Water-Source (Other DX) | Twb, Twt |  | 0.94526 | -0.0094199 | 0.000227 | 0.0004805 | -4.5e-06 | -5.99e-05
|  | Fan Coils | Twb, Tdb |  | 0.50389 | -0.086918 | 0.0016847 | 0.03363 | 0.0002478 | -0.0010297
|  | Other Chilled Water | Twb, Tdb |  | 2.5883 | -0.23059 | 0.0038359 | 0.10258 | 0.0005984 | -0.0028721
| CAP-FFLOW | E+ only
| COIL-BF-FFLOW | PTAC | FPLR |  | a: -2.277; b: 5.2114; c: -1.9344
|  | HP | FPLR |  | a: -0.82816; b: 14.3179; c: -21.8894; d: 9.3997
|  | PSZ and other | FPLR |  | a: -0.25423; b: 1.2183; c: 0.035978
| COIL-BF-FT | PTAC | Twb,Tdb |  | -1.5714 | 0.046963 | 0.0003125 | -0.0065347 | 0.0001105 | -0.0003719
|  | HP | Twb,Tdb |  | -29.9391 | 0.87535 | -0.0057055 | 0.16145 | 0.0002907 | -0.0031523
|  | PSZ and other | Twb,Tdb |  | 1.066 | -0.000517 | 5.67e-05 | -0.012918 | -1.7e-06 | 0.0001503
| COIL-BF-FPLR | PTAC | PLR |  | a: 0; b: 1
|  | HP | PLR |  | a: 0; b: 1
|  | PSZ and other | PLR |  | a: 0; b: 1
| DX-EIR-FT | Water-Source (HP) | Twb, Twt |  | 2.028 | -0.042309 | 0.0003054 | 0.014967 | 2.44e-05 | -0.000164
|  | Water-Source (Other) |  |  | -1.8395 | 0.075136 | -0.0005686 | 0.004709 | 9.01e-05 | -0.0001218
|  | Air-Source (PTAC) |  |  | -0.65505 | 0.038891 | -0.0001925 | 0.0013046 | 0.0001352 | -0.0002247
|  | Air-Source (PSZ with SEER) | Twb,Todb |  | n/a | n/a | n/a | n/a | n/a | n/a
|  | Air-Source (Other) | Twb,Todb |  | -1.0639 | 0.030658 | -0.0001269 | 0.015421 | 4.97e-05 | -0.0002096
Direct-Expansion Part-Load Efficiency Adjustment Curve | DX-EIR-FPLR | Air-Source (SEER) | PLR |  | a: 0; b: 1
|  | All Other | PLR |  | a: see data map
| DX-EIR-FFLOW | E+ only |  |  | a: tbd; b: tbd; c: tbd
Direct-Expansion Part-Load Efficiency Adjustment Curve | DX-PLF-PLR | Air-Source (SEER) | PLR |  | a: 1; b: 0
|  | All others | PLR |  | a: see data map
Evaporative Cooling Performance Curves | EFF-FFLOW | Direct Evap Cooler | FPLR |  | a: 1.1833; b: -0.25753; c: 0.074245
|  | Indirect Evap Cooler | FPLR |  | a: 1.097; b: -0.16506; c: 0.068069
Furnace Fuel Heating Part Load Efficiency Curve | FURN-EFF-FPLR | Furnace | PLR = Qpartload/Qrated |  | a: 0.01861; b: 1.0942; c: -0.11282
Electric Heat Pump Heating Capacity Adjustment Curve | HP-CAP-FT | Air-cooled | Todb |  | a: 0.25367; b: 0.010435; c: 0.0001861; d: -1.5e-06
| HP-CAP-FT | Air-cooled | Todb |  | a: data map?
| HP-CAP-FT | Water-cooled | Tdb, Twt |  | a: 0.48865; b: -0.0067774; c: 0; d: 0.014082
Electric Heat Pump Heating Efficiency Adjustment Curve | HP-EIR-FT | Air-Cooled |  |  | a: 2.46; b: -0.062254; c: 0.00088; d: -4.6e-06
|  | Water-Cooled |  |  | a: 1.3876; b: 0.0060479; c: 0; d: -0.011585
| HP-EIR-FPLR | Air-Cooled, Water-Cooled | PLR |  | a: 0.085652; b: 0.93881; c: -0.18344; d: 0.15897
Liquid Desiccant Performance Curves | Desc-T-FTW | Temp leaving desicc | T,w |  | 11.5335 | 0.65867 | -0.001028 | 0.29504 | -0.00017 | -0.0008724
| Desc-W-FTW | w leaving desicc | T,w |  | 11.8994 | -0.26956 | 0.0044549 | 0.083053 | 0.0006974 | 0.0015879
| Desc-Gas-FTW | gas usage | T,w |  | 58745.8008 | -1134.49 | -3.6676 | 3874.5901 | -1.6963 | -13.0732
| Desc-kW-FTW | electric usage | T,w |  | 3.5179 | -0.0059317 | 0 | 0.0040401 | 0 | 0
Boiler Part-Load Performance Curve | Boiler-FPLR | (All) | PLR | 0,1 | a: 0.082597; b: 0.99676; c: -0.079361
Chiller Cooling Capacity Adjustment Curves | CH-CAP-FT | Air-Cooled Scroll |  |  | 0.40071 | 0.018615 | 7.199e-05 | 0.001773 | -2.014e-05 | -8.273e-05
|  | Air-Cooled Recip |  |  | 0.57617 | 0.020631 | 7.769e-05 | -0.0035118 | 3.12e-06 | -7.865e-05
|  | Air-Cooled Screw |  |  | -0.094649 | 0.038341 | -9.205e-05 | 0.0037801 | -1.375e-05 | -0.00015464
|  | Air-Cooled Centrifugal |  |  | N/A | N/A | N/A | N/A | N/A | N/A
| CH-CAP-FT | Water-Cooled |  |  | 0.36131 | 0.018555 | 3.011e-05 | 0.00093592 | -1.518e-05 | -5.481e-05
|  | Water-Cooled Recip |  |  | 0.58531 | 0.015396 | 7.296e-05 | -0.0021246 | -7.15e-06 | -4.597e-05
|  | Water-Cooled Screw |  |  | 0.3327 | 0.0072912 | -0.00049938 | 0.01599 | -0.00028254 | 0.00052346
|  | Water-Cooled Centrifugal |  |  | -0.29862 | 0.029961 | -0.00080125 | 0.017363 | -0.00032606 | 0.00063139
| CH-EIR-FT | Air-Cooled |  |  | 0.99007 | -0.0058414 | 0.00016454 | -0.0066114 | 0.00016808 | -0.00022501
[5 empty] | 0.66534 | -0.013838 | 0.00014736 | 0.0071281 | 4.571e-05 | -0.00010326
[5 empty] | 0.13546 | 0.022929 | -0.00016107 | -0.002354 | 0.00012991 | -0.00018685
[5 empty] | N/A | N/A | N/A | N/A | N/A | N/A
| CH-EIR-FT | Water-Cooled |  |  | 1.0012 | -0.01027 | 0.00016703 | -0.0012814 | 0.00014613 | -0.00021959
[5 empty] | 0.4614 | -0.0088216 | 8.223e-05 | 0.0092661 | 5.722e-05 | -0.00011594
[5 empty] | 0.66625 | 0.00068584 | 0.00028498 | -0.0034168 | 0.00025484 | -0.00048195
[5 empty] | 0.51777 | -0.0040036 | 2.028e-05 | 0.0069879 | 8.29e-05 | -0.00015467
| CH-EIR-FPLR | Air-Cooled |  |  | a: 0.063691; b: 0.58489; c: 0.3528
[5 empty] | 0.11444 | 0.54593 | 0.3423
[5 empty] | 0.036487 | 0.73474 | 0.21995
[5 empty] | N/A | N/A | N/A
| CH-EIR-FPLR | Water-Cooled |  |  | a: 0.04412; b: 0.64037; c: 0.31956
[5 empty] | 0.081441 | 0.41927 | 0.4994
[5 empty] | 0.33019 | 0.23554 | 0.46071
[5 empty] | 0.17149 | 0.5882 | 0.23737
| CH-EIR-FPLR | Variable-Speed |  |  | TBD | TBD | TBD | TBD | TBD | TBD
Fuel and Steam Chiller Cooling Efficiency Adjustment Curves | FIR-FPLR | Single Stage Absorption |  |  | a: 0.098585; b: 0.58385; c: 0.56066; d: -0.24309
|  | Double Stage Absorption |  |  | a: 0.013994; b: 1.2404; c: -0.91488; d: 0.66044
|  | Direct-Fired Absorption |  |  | a: 0.13551; b: 0.61798; c: 0.24651; d: 0
|  | Engine-Driven, % Spd <= Min |  |  | a: 0.3802; b: 2.3609; c: 0; d: 0
|  | Engine-Driven, % Spd>Min % < 60% |  |  | a: 1.1434; b: 0.022889; c: 0; d: 0
|  | Engine-Driven, % Spd > 60% |  |  | a: 1.3886; b: -0.38861; c: 0; d: 0
| FIR-FT | Single Stage Absorption | CHWT, CWT |  | 0.65227 | 0 | 0 | -0.000545 | 5.5e-05 | 0
|  | Double Stage Absorption |  |  | 1.6587 | 0 | 0 | -0.29 | 0.00025 | 0
|  | Direct-Fired Absorption |  |  | 4.4287 | -0.13299 | 0.0012533 | 0.86174 | -0.0070892 | 0.0010251
|  | Engine-Driven, % Spd <= Min |  |  | 1.0881 | 0.014106 | 0 | -0.0083391 | 0 | 0
|  | Engine-Driven, % Spd>Min % < 60% |  |  | 1.2362 | 0.016892 | 0 | -0.011524 | 0 | 0
|  | Engine-Driven, % Spd > 60% |  |  | 1.2362 | 0.016892 | 0 | -0.011524 | 0 | 0
| FIR-FT1 | FIR(CHWST)
| FIR-FT2 | FIR(CWT)
Cooling Tower Capacity Adjustment Curves | TWR-CAP | details to be determined |  |  | a: TBD; b: TBD; c: TBD
Cooling Tower Power Adjustment Curve | TWR-FAN-FPLR | All | FPLR |  | a: 0.33163; b: -0.88568; c: 0.60557; d: 0.94848
Pump Part Load Curve | CIRC-PUMP-FPLR | All pumps | PLR |  | a: 0.0015303; b: 0.0052081; c: 1.1086; d: -0.11636

## Data Maps
Performance Maps Section
Some performance data is expressed not as a curve fit but as a performance map. The software can generate curve fits from this performance
data. The exact type of curve (polynomial, exponential) is left to the software developer, but the curve fit should have a high degree of accuracy
(R^2> 0.95 (exact metric to be determined), and curves that are normalized should produce an output of 1 +/- 0.005 with an input of 1.
Direct-Expansion Part-Load Efficiency Curves for Equipment without SEER Ratings
| EIR(PLR) | [6 empty] | PLF(PLR)
| PLR | EIR WSHP | EIR WS | EIR PTAC | EIR AS | EIR E+ |  | PLF WSHP | PLF WS | PLF PTAC | PLF AS | PLF E+
| 0 | 0.125 | 0.20123 | 0.125 | 0.20123 | 0 |  | 0 | 0 | 0 | 0 | 0.85
| 0.1 | 0.2125 | 0.21649 | 0.2125 | 0.21649 | 0.11561 |  | 0.47059 | 0.46191 | 0.47059 | 0.46191 | 0.865
| 0.2 | 0.3 | 0.26404 | 0.3 | 0.26404 | 0.22727 |  | 0.66667 | 0.75745 | 0.66667 | 0.75745 | 0.88
| 0.3 | 0.3875 | 0.33716 | 0.3875 | 0.33716 | 0.3352 |  | 0.77419 | 0.8898 | 0.77419 | 0.8898 | 0.895
| 0.4 | 0.475 | 0.42911 | 0.475 | 0.42911 | 0.43956 |  | 0.84211 | 0.93216 | 0.84211 | 0.93216 | 0.91
| 0.5 | 0.5625 | 0.53318 | 0.5625 | 0.53318 | 0.54054 |  | 0.88889 | 0.93777 | 0.88889 | 0.93777 | 0.925
| 0.6 | 0.65 | 0.64265 | 0.65 | 0.64265 | 0.6383 |  | 0.92308 | 0.93364 | 0.92308 | 0.93364 | 0.94
| 0.7 | 0.7375 | 0.75079 | 0.7375 | 0.75079 | 0.73298 |  | 0.94915 | 0.93236 | 0.94915 | 0.93236 | 0.955
| 0.8 | 0.825 | 0.85087 | 0.825 | 0.85087 | 0.82474 |  | 0.9697 | 0.94021 | 0.9697 | 0.94021 | 0.97
| 0.9 | 0.9125 | 0.93619 | 0.9125 | 0.93619 | 0.91371 |  | 0.9863 | 0.96135 | 0.9863 | 0.96135 | 0.985
| 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1
| For Air-Cooled DX with SEER Ratings, use EIR=PLR instead | [6 empty] | For Air-Cooled DX with SEER Ratings, use PLF=1 instead
| of the data map. | [6 empty] | of the data map.
Abbreviations:
WSHP - Water-Source Heat Pump
WS - Water-Source (Other)
PTAC - Packaged Terminal Air Conditioner
AS - Air-Source (Other)
Direct-Expansion Cooling Efficiency Curve for equipment with SEER Ratings
User Inputs: SEER, EER
| EWB | ODB | COOL-EIR-FT
| 67 | 95 | 1
| 57 | 82 | formula TBD
| 57 | 95 | formula TBD
| 57 | 110 | formula TBD
| 67 | 82 | EER/SEER
| 67 | 110 | formula TBD
| 77 | 82 | formula TBD
| 77 | 95 | formula TBD
| 77 | 110 | formula TBD
| Heat Pump Efficiency Adjustment Curve |  |  |  |  | Electric Heat Pump Heating Capacity Adjustment Curve
| User Inputs: COP17, COP47 |  |  |  |  | User Inputs: CAP17, CAP47
The two user inputs for these curves are Coefficient of Performance (COP) or Heating Capacity at 17F and 47F.
| Temp | EIR-FT |  |  |  | Temp | CAP-FT
| 67 | 0.856 |  |  |  | 67 | 1.337 | [5 empty] | = | (67,1.337)
| 57 | 0.919 |  |  |  | 57 | 1.175
| 47 | 1 |  |  |  | 47 | 1
| 17 | COP47/COP17 |  |  |  | 17 | CAP17/CAP47
| 7 | 1.266x COP47/COP17 |  |  |  | 7 | 0.702xCAP17/CAP47
| -13 | 3.428 |  |  |  | -13 | 0.153