## Prototype Model
Prototype Name | I | II | III | IV | IV |  |  | VIII | III | II
Prototype Description | Small Office Building (02000CZ-OffSml) | Medium Office Building ((0300CZ-OffMed)) | Large Office Building (0400CZ-OffLrg) | Retail Medium (0500CZ-RetlMed) | Stand-alone Retail DuctLoss Baseline | Strip Mall-PSZ System (1000CZ-RetlStrp) | Strip Mall-PTAC System (1000CZ-RetlStrp) | Strip Mall- Fan Coil System (1000CZ-RetlStrp) | Large Office Building (0400CZ-OffLrg-CRAH) | Medium Office Building ((0300CZ-OffMed-LabwExhPVAV))
Vintage | New Construction | New Construction | New Construction | New Construction | Same as Stand-alone Retail | New Construction | New Construction | New Construction | Same As Off Lrg | Same As Off Med
Location | CZ-6/15/16 | CZ-6/16 | CZ-7/6/16 | CZ-6/7/15 |  | CZ-6/15 | CZ-6/15 | CZ-6/15/16
Fuel Type | gas, electricity | gas, electricity | gas, electricity | gas, electricity |  | gas, electricity | Same as Strip Mall- PSZ System | Same as Strip Mall- PSZ System
Total Floor Area (sq feet) | 5502 (90.8 ft x 60.5ft) | 53600 (163.8 ft x 109.2 ft) | 498,600 (240 ft x 160 ft) | 24695 (178 ft x 139 ft) |  | 22,500 ft² (300 ft x 75 ft)
Building shape
Aspect Ratio | 1.5 | 1.5 | 1.5 | 1.28 |  | 4
Number of Floors | 1 | 3 | 13 (Including basement) | 1 |  | 1
Window Fraction (Window-to-Wall Ratio) | 24.4% for South and 19.8% for the other three orientations (Window Dimensions: 6.0 ft x 5.0 ft punch windows for all façades) | 33% (Window Dimensions: 163.8 ft x 4.29 ft on the long side of facade 109.2 ft x 4.29 ft on the short side of the façade) | 40% of above-grade gross walls 37.5% of gross walls (including the below-grade walls) | 7.1% (Window Dimensions: 82.136 ft x 5 ft, 9.843 ft x 8.563 ft and 82.136 ft x 5 on the street facing facade) |  | 10.5% (Window Dimensions: 24 windows, 7 ft x 5 ft each and 12 doors, 6 ft x 7 ft each, on the street facing façade with south WWR 26%)
Window Locations | evenly distributed along four façades | evenly distributed along four façades | evenly distributed along four façades | Windows only on the street facing façade (25.4% WWR) |  | Windows only on the street facing façade
Shading Geometry | none | none | none | none |  | none
Azimuth | non-directional | non-directional | non-directional | non-directional |  | non-directional
Thermal Zoning | Perimeter zone depth: 16.4 ft. Four perimeter zones, one core zone and an attic zone. Percentages of floor area: Perimeter 70%, Core 30% | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 40%, Core 60% | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 33%, Core 67% | Five thermal zones Refer StandAloneRetailArea for details |  | 10 thermal zones (from left to right): LGStore1 (Type 1), SMStore1 (Type 1), SMStore2 (Type 2), SMStore3 (Type 3), SMStore4 (Type 2), LGStore2 (Type 3), SMStore5 (Type 3), SMStore6 (Type 3), SMStore7 (Type 3), and SMStore8 (Type 3). Refer StripMallArea for details
Floor to floor height (feet) | 10.7 | 13 | 13, Basement - 8 | 20 |  | 17
Floor to ceiling height (feet) | 10 | 9 (4 ft above-ceiling plenum) | 9 | 20 (Core retail, Front Entry) 15 (Point of Sale, Front Retail, Back Space) |  | 17
Glazing sill height (feet) | 3 (top of the window is 8 ft high with 5 ft high glass) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass) | 3 ft | 3.74 ft (top of the window is 8.73 ft high with 5 ft high glass) |  | 3.0 ft (top of the window is 8 ft high)
Exterior walls
Construction | Metal Framed Wall | Metal Framed Wall | Metal Framed Wall | Metal Framed Wall |  | Metal Framed Wall
Construction Assembly Layers | Refer MetalFrameWall | Refer MetalFrameWall | Refer MetalFrameWall | Refer MetalFrameWall |  | Refer MetalFrameWall
Refer BasementWall
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | 0.062 | 0.062 | Exterior Wall U: 0.062 | 0.062 |  | 0.062
Dimensions | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio
Tilts and orientations | Vertical | Vertical | Vertical | Vertical | Vertical
Roof
Construction | Attic Roof with wood joist | Roof | Roof | Roof | NACM Roof. Note: For duct loss baseline, the insulation layer is modelled at the drop ceiling. See details below | NACM Roof
Construction Assembly Layers | Refer NACM_AtticRfWood | Refer Roof | Refer Roof | Refer Roof | Refer T24NRRoofInsAboveDeck | Refer Roof
U-factor (Btu / h * ft2 * °F) | 0.049 | 0.034 | 0.034 | 0.034 | Refer T24NRRoofInsAboveDeck | 0.034
Aged Solar Reflectance Aged Thermal Emittance | 0.2 0.85 | 0.08 0.75 | 0.08 0.75 | 0.08 0.75 |  | 0.08 0.75
Tilts and orientations | Hipped roof: 10.76 ft attic ridge height, 2 ft overhang-soffit | Horizontal | Horizontal | Horizontal | Horizontal | Horizontal
Window |  |  |  |  | Same as Stand-alone Retail
Glass-Type and frame | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. |  | Fixed vertical window with U-value and SHGC as specified.
U-factor (Btu / h * ft2 * °F) | 0.36 | 0.36 | 0.36 | 0.36 |  | 0.36
SHGC | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.25
Visible transmittance | 0.42 | 0.42 | 0.42 | 0.42 |  | 0.42
Operable area | 0 | 0 | 0 | 0 |  | 0
Skylight | NA | NA | NA
Dimensions |  |  |  | Skylight to Roof Ratio- 2.07 % Core Retail, Refer Skylight Layout for details |  | Skylight to Roof Ratio- 0.85 %
Glass-Type and frame |  |  |  | Glass, curb mounted skylight with U-value and SHGC as specified. |  | Glass, curb mounted skylight with U-value and SHGC as specified.
U-factor (Btu / h * ft2 * °F) |  |  |  | 0.58 |  | 0.58
SHGC |  |  |  | 0.25 |  | 0.25
Visible transmittance |  |  |  | 0.49 |  | 0.49
Foundation
Foundation Type | NACM Slab Floor F-factor method | Slab Floor F-factor method | Slab Floor F-factor method | Slab Floor F-factor method |  | NACM Slab Floor F-factor method
Construction | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation |  | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation
F factor (Btu / h * ft2 * °F) | F factor= 0.72 | 0.72 | 0.72 | F factor= 0.72 |  | F factor= 0.72
Thermal properties for basement walls | NA | NA | Refer BasementWall for detailed description | NA |  | NA
Interior Surfaces
Construction | 2x4 uninsulated Stud Wall | Uninsulated Stud Wall Interior Walls, Concrete with carpet for interior floor slabs, 3/4 in Acoustic celing tile for Drop ceiling | Uninsulated Stud Wall Interior Walls, Concrete with carpet for interior floor slabs, 3/4 in Acoustic celing tile for Drop ceiling | Uninsulated Stud Wall Interior Walls, Concrete with carpet for interior floor slabs, 3/4 in Acoustic celing tile for Drop ceiling | 2x4 uninsulated Stud Wall for Interior Walls & 3/4 in Acoustic celing tile for Drop ceiling. Note: For duct loss baseline the drop ceiling is modelled with a layer of insulation. See details below | Uninsulated Stud Wall Interior Walls, Concrete with carpet for interior floor slabs, 3/4 in Acoustic celing tile for Drop ceiling
Construction Assembly Layers | NACM Interior wall Drop Ceiling | Interior wall Interior Floor slab Drop Ceiling | Interior wall Interior Floor slab Drop Ceiling | Interior wall | NACM Interior wall Drop Ceiling2 | Interior wall
Internal Mass | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
Infiltration | Peak: 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) | 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) | 0.0448 cfm/sf of above grade exterior wall surface area | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Peak: 0.2318 cfm/sf of exterior wall surface area for BackSpace Plenum, Point of Sale Plenum and Front Retail Plenum (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | 0.0448 cfm/sf of above grade exterior wall surface area
HVAC System Type |  |  |  |  | Same as Stand-alone Retail
System Type | Packaged single zone air conditioning unit | Packaged VAV with hot-water reheat with one system per floor serving all zones in the floor | VAV with hot-water reheat with one system per floor serving all zones in the floor | Idirectly Conditioned Front_entry, Packaged single zone air conditioning unit for other zones. |  | Packaged single zone (One PSZ per zone) | Packaged Terminal Air Conditioner (One PTAC per zone) | 4 pipe fan coil system (One FPFC per zone with central boiler and chiller) | VAV with hot-water reheat with one system per floor serving all zones in the floor. Core Top space is a Computer Room served by a CRAH system. | Packaged VAV with hot-water reheat with one system per floor serving all zones in the floor. Core Mid is a Lab served by PVAV and an Exhaust system.
Heating type | Gas furnace inside the packaged air conditioning unit | Gas condensing boiler | Gas condensing boiler | Unconditioned for front_entry. Gas furnace inside the packaged air conditioning unit for all others. |  | Gas furnace | Electric heating | Heating hot water | Gas condensing boiler. No heating in CRAH | Gas condensing boiler
Cooling type | Packaged air conditioning unit | Direct Expansion | Water cooled Centrifugal chillers (2) | No cooling for front_entry. Packaged air conditioning unit for all others |  | Single speed DX cooling | Single speed DX cooling | Chilled water system | Water cooled Centrifugal chillers (2) | Direct Expansion
Distribution and terminal units | Single zone constant air volume distribution. | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. Zone control type: minimum supply air at 20% of the zone maximum air flow rate. | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. Zone control type: minimum supply air at 20% of the zone maximum air flow rate. | Constant air volume air distribution 4 single-zone roof top units serving thermal zones back_space, point_of_sale, core_retail, and front_retail. |  | Single zone Constant air volume distribution | Constant Air Volume distribution | 4 pipe fan coil unit | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. Zone control type: minimum supply air at 30% of the zone maximum air flow rate. | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. Zone control type: minimum supply air at 20% of the zone maximum air flow rate in all zones except Core mid. 40% min flow rate in Core Mid
HVAC Sizing
Cooling | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues |  | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues
Heating | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues |  | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues
HVAC Efficiency
Cooling | EER-10.8 | EER-11.00, IEER-12.1 (Bottom VAV, Mid and Top VAV). Note: EER, COP includes fan heat | 0.560 kw/ton, 0.5 IPLV | EER-11.20, IEER- 12.9, SEER-13.6. Indirect Heating and Cooling for front_entry) Note: EER, COP includes fan heat |  | EER-11.20, IEER-12.9, SEER- 13.6 Note: EER, COP includes fan heat | EER-11.20, IEER-12.9, SEER- 13.6 Note: EER, COP includes fan heat | Chiller COP-6.1 DOAS EER:10.0 | 0.560 kw/ton, 0.5 IPLV | EER-11.00 , IEER-12.4 Note: EER, COP includes fan heat
Heating | 82% | 80% | 80% | 82% |  | 82% | NA | 80% | 80% | 80%
HVAC Control
Thermostat Setpoint | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating |  | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating
Thermostat Setback | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating |  | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating
Design Supply air temperature | Maximum 95F, Minimum 55F | Cooling 55F Heating 95 F | Cooling 55F Heating 95 F | Cooling 55F Heating 95 F |  | Cooling 55F Heating 95 F | Cooling 55F Heating 95 F | Maximum 122°F, Minimum 55°F | Cooling 55F Heating 95 F | Cooling 55F Heating 95 F
Supply air temperature reset | NA | SAT reset by warmest zone airflow first (Reset Supply high: 60 F, reset supply low: 55F) | SAT reset by warmest zone airflow first (Reset Supply high: 60 F, reset supply low: 55F) | No SAT Control |  | No SAT Control | No SAT Control | No SAT Control | SAT reset by warmest zone airflow first (Reset Supply high: 60 F, reset supply low: 55F) | SAT reset by warmest zone airflow first (Reset Supply high: 60 F, reset supply low: 55F)
Zone control |  | DDC at zone level and Dual Max Reheat control | DDC at zone level and Dual Max Reheat control | CO2 sensor |  |  |  |  | DDC at zone level and Dual Max Reheat control | DDC at zone level and Dual Max Reheat control
Chilled water supply temperatures | NA | NA | 44°F | NA |  | NA | NA | 44°F | 44°F | NA
Chilled water return temperatures | NA | NA | 64°F | NA |  | NA | NA |  | 64°F | NA
Chilled water supply temperature reset | NA | NA | Fixed | NA |  | NA | NA | Reset (44°F-54°F ) based on outdoor air temperature | Fixed | NA
Condenser Type | NA | NA | Water-cooled, no reset | NA |  | NA | NA | Water cooled, no reset | Water-cooled, no reset | NA
Hot water supply temperatures | NA | 180°F | 180°F | NA |  | NA | NA | 180°F | 180°F | 180°F
Hot water supply temperature reset | NA | Fixed | Fixed | NA |  | NA | NA | Reset (150°F-180°F ) based on outdoor air temperature | Fixed | Fixed
Economizers | No economizer | Differential Dry bulb economizer (Integrated), 80 F High DB lockout | Differential Dry bulb economizer (Integrated), 80 F High DB lockout | Differential Dry bulb economizer (Integrated), 80F high DB lockout |  | Differential Dry bulb economizer (Integrated), 80F high DB lockout | No economizer | No economizer | Differential Dry bulb economizer (Integrated), 80 F High DB lockout | Differential Dry bulb economizer (Integrated), 80 F High DB lockout
Ventilation | 0.15 cfm/ft2 | Max of 15 cfm/person, 0.15 cfm/ft2, | Max of 15 cfm/person, 0.15 cfm/ft2, | Point of Sale & Core and Front Retail -0.2 cfm/ft2; Backspace, Front Entry-0.15 cfm/ft2 |  | Max of 15 cfm/person or 0.20 cfm/ft2 | DOAS system for ventilation. CO2 sensors. Max of 15 cfm/person or 0.20 cfm/ft2 | DOAS with Max of 15 cfm/person or 0.20 cfm/ft2 | Max of 15 cfm/person, 0.15 cfm/ft2, | Max of 15 cfm/person, 0.15 cfm/ft2,
Supply Fan
Fan type | CAV | Variable Volume | Constant volume for Basement, Variable Volume for all others | Constant Volume for all Conditioned zones |  | OnOff | OnOff | OnOff | Constant volume for Basement, Variable Volume for all others | Variable Volume
Supply Fan Total Efficiency (%) | 55%, 50% | 65% | 65% (for all VAV fans) | 60% (all fans) |  | 60% | 60% | DOAS fan 62% 60% for all other fans. | 65% (for all VAV fans) | 60% Exhaust Fan, 65% -VAV and Lab VAV fans.
Fan Motor Efficiency | 85.5% | 95% | 95% | 90% (all fans) |  | 90% | 95% | DOAS fan 89.5% 95.0% for all other fans | 95% | 95% for all VAV fans. Exhaust Fan 90%
Supply Fan Pressure Rise | 2.5 ftinH2O | 4 inch H2O | 4 inH2O | 2.5in H2O (all fans) |  | 2.50 inH2O | 1.50 inH2O | DOAS fan 3.5 in H2O 2.50 inH2O for other fans | 4 inH2O | 4.0 in H20 for all VAV. 0.5 for Exhaust Fan
Pump | [9 empty] | Same as Off-Med
Pump Type | NA | HW: Constant Speed | HW: Constant Speed variable flow, Cooling Tower:Constant Speed, CHW: Variable Primary | NA |  | NA | NA | Variable speed pumps for condenser water, chilled water and heating hot water systems | HW: Constant Speed variable flow, Cooling Tower:Constant Speed, CHW: Variable Primary
Rated Pump Head | NA | HW: 50 ft H20 | HW: 40 ft H20 Cooling Tower: 40 ft H20 Chiller Pumps: 60 ft H20 | NA |  | NA | NA | HW- 60 ftH2O CHW- 30 ftH2O CW- 45 ftH2O | HW: 40 ft H20 Cooling Tower: 40 ft H20 Chiller Pumps: 60 ft H20
Pump Motor Power per Unit Flow |  | HW: 19 W/gpm | HW: 15 W/gpm, CW: 17.4 W/gpm, ChW Primary: 17.5 W/gpm | NA |  |  |  | Hw: 19 W/gpm | HW: 15 W/gpm, CW: 17.4 W/gpm, ChW Primary: 17.5 W/gpm
Pump Efficiency | NA | Motor efficiency- HW: 0.9 | 0.9 | NA |  | NA | NA | Motor efficiency: 0.9 | 0.9
Cooling Tower | [8 empty] | Same As Off Lrg
Cooling Tower Type | NA | NA | open cooling tower with variable speed fan | NA |  | NA | NA | open cooling tower with two speed fan
Tower range | NA | NA | 10F delta T | NA |  | NA | NA | 10F (Design CW supply temp. 85F, CW return temp 95F)
Service Water Heating
SWH type | Storage Tank | Storage Tank | Storage Tank | Tank |  | Tank | Same as Strip Mall- PSZ System | Same as Strip Mall- PSZ System
Fuel type | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | Natural Gas
Efficiency | 80% | EF: 0.637, Recovery Eff: 0.780 | TE: 80% | EF: 0.637, Recovery Eff: 0.780 |  | EF: 0.637, Recovery Eff: 0.780
Water temperature setpoint | 135°F | 135°F | 135 °F | 135°F |  | 135°F
Water Heater Max Capacity (Btuh) | 6655 Btuh | 24,949 Btuh | 231,958 Btuh | 32,328 Btuh |  | 34,888 Btuh
Lighting Load
Lighting power density (W/ft2) | 0.75 W/ft2 | 0.75 W/ft2 | 0.75 W/ft2 | Point of sale, Retail-1.2 W/ft2,, Lobby-0.95 W/ft2, Backspace-0.6 W/ft2 |  | 1.2 W/ft2 |  |  |  | Core Mid: 1.4 W/ft2 All other spaces:0.75 W/ft2
Daylighting Controls | NA | Continuous dimming in Primary Daylit areas in Perimeter zones | Continuous dimming in Primary and Secondary Daylit zone in Perimeter zones | Continuous Dimming in Skylit area in Core Retail and in Primary Daylit in Front Entry, Front Retail, Point of Sale |  | Continuous Dimming in Skylit, Primary and Secondary Daylit areas in all zones. |  |  |  | Continuous dimming in Primary Daylit zone in Perimeter zones
Plug load
Electric power density (W/ft2) | 1.5 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | Point of sale, Retail-1.0 W/ft2, Backspace-0.2 W/ft2, Front entry: 0.5 W/ft2 |  | 1 W/ft2 |  |  | Core Top: 20.0 W/ft2 All other spaces: 1.5 W/ft2 | Core Mid: 2.0 W/ft2 All other spaces: 1.5 W/ft2 Hood Dominated Process exhaust in Core mid zone
Occupancy
Average people | 100- ft2/person | 200 ft2/person | 200 ft2/person | Point of sale, Retail - 60 ft2/person, Back Space- 997 ft2/person, Front Entry - 30 ft2/person |  | 60 ft2/person |  |  | Core Top: 60 ft2/person All other spaces: 200 ft2/person | 200 ft2/person
Elevator
Quantity | NA | NA | NA | NA |  | NA |  |  | NA | NA
Motor type
Peak Motor Power (W/elevator)
Heat Gain to Building
Peak Fan/lights Power (W/elevator)
Motor and fan/lights Schedules
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail
Note on F28: Nambiar, Chitra AEC: Not been updated

## Zonelvl
LARGE OFFICE
Baseline Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2
| Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
WWR20 Case Daylighting | Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
WWR60 Case Daylighting | Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
STAND ALONE RETAIL
Name | Area [ft2] | Conditioned
BACK_SPACE | 4089 | Yes
CORE_RETAIL | 17227 | Yes
POINT_OF_SALE | 1623 | Yes
FRONT_RETAIL | 1623 | Yes
FRONT_ENTRY | 129 | Yes
Conditioned Total | 24692
Unconditioned Total | 0
Baseline Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2 | SRR3.04 Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2
| Core_Retail | NA | NA | 16742.62 | UnderSkylight | NA | 0.97 |  | 550 lux |  |  | Core_Retail | NA | NA | 16934.71 | UnderSkylight | NA | 0.97 |  | 550 lux
| Point_Of_Sale | 718.07 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux |  |  | Point_Of_Sale | 717.0473 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux
| Front_Retial | 718.07 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux |  |  | Front_Retial | 717.0473 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux
| Front_Entry | 114.3 | NA | NA | In Prim. Daylit Zn | NA | 0.88 |  | 550 lux |  |  | Front_Entry | 85.9294 | NA | NA | In Prim. Daylit Zn | NA | 0.88 |  | 550 lux
Baseline Skylight Layout | [10 empty] | TestCase Skylight Layout
STRIP MALL
Name | Area [ft2] | Conditioned
LGSTORE1 | 3750.0388 | Yes
SMSTORE1 | 1874.9656 | Yes
SMSTORE2 | 1874.9656 | Yes
SMSTORE3 | 1874.9656 | Yes
SMSTORE4 | 1874.9656 | Yes
LGSTORE2 | 3750.0388 | Yes
SMSTORE5 | 1874.9656 | Yes
SMSTORE6 | 1874.9656 | Yes
SMSTORE7 | 1874.9656 | Yes
SMSTORE8 | 1874.9656 | Yes
Total | 18749.7632
Conditioned Total | 18749.7632
Unconditioned Total | 0
Skylight Layout

## ConstructionAssembly
Name | Layers | Overall UFactor All Climate Zones | Overall CFactor All Climate Zones | Overall FFactor All Climate Zones | Material Name | Thickness (in) | Conductivity (Btu/h*ft*F) | Density (lb/ft³) | Specific Heat (Btu/lb*F) | Rvalue (ft2*F*hr/Btu)
MetalFrameWall |  | 0.062 | NA | NA | Stucco - 7/8 in | 0.875 | 0.405 | 115.866 | 0.20063 | 0.18
Outside Layer | Stucco - 7/8 in |  |  |  | Building Paper - 1/16 in | 0.06 | 0.1667 | 70 | 0.3 | 0.03
Layer 2 | Building Paper - 1/16 in |  |  |  | Expanded Polystyrene - EPS - 3 1/3 in | 3.3 | 0.02 | 1.2 | 0.27 | 13.96
Layer 3 | Expanded Polystyrene - EPS - 3 1/3 in |  |  |  | Gypsum Board - 1/2 in | 0.5 | 0.092 | 40 | 0.27 | 0.45
Layer 4 | Air - Metal Wall Framing - 16 or 24 in OC |  |  |  | Composite Wood Frame 24 in OC depth 11.25 in R-30 |  |  |  |  | 30
Layer 5 | Gypsum Board - 1/2 in |  |  |  | Metal Standing Seam - 1/16 in | 0.0625 | 0.333 | 488.22 | 0.12
Roof |  | 0.034 | NA | NA | Expanded Polystyrene - EPS - 6 7/8 in | 6.9 | 0.02 | 1.2 | 0.27 | 28.63
Outside Layer | Metal Standing Seam - 1/16 in |  |  |  | Expanded Polystyrene - EPS - 1 1/2 in | 1.5 | 0.02 | 1 | 0.27 | 6.25
Layer 2 | Expanded Polystyrene - EPS - 6 7/8 in |  |  |  | Carpet - 3/4 in | 0.75 | 0.0263 | 18 | 0.33 | 2.38
BasementWall |  | NA | 1.14 | NA | Acoustic Tile - 3/4 in | 0.75 | 0.0333 | 18 | 0.19 | 1.89
Layer 2 | Concrete - Solid Grout - 115 lb/ft3 - 8 in |  |  |  | Concrete - Solid Grout - 115 lb/ft3 - 8 in | 8 | 0.433 | 115 | 0.2 | 1.538
Interior wall |  | 0.344 | NA | NA | Stud Wall | 5.5 | 0.705 | 0.08 | 0.24 | 0.65
Outside Layer | Gypsum Board - 1/2 in |  |  |  | Expanded Polystyrene - EPS - 2 in | 2 | 0.02 | 1 | 0.27 | 8.33
Layer 2 | Stud Wall |  |  |  | Concrete - 140 lb/ft3 - 4 in | 4 | 1.128 | 139.78 | 0.22 | 0.3
Layer 3 | Gypsum Board - 1/2 in |  |  |  | Plywood - 1/2 in | 0.5 | 0.0667 | 30 | 0.45 | 0.63
Interior Floor slab |  | 0.238 | NA | NA | Asphalt shingles - 1/4 in | 0.3 | 0.0467 | 69.89 | 0.3 | 0.45
Outside Layer | Concrete - 140 lb/ft3 - 4 in |  |  |  | Air - Metal Wall Framing - 16 or 24 in OC | 5.5 | 0.705 | 0.08 | 0.24 | 0.65
Layer 2 | Carpet - 3/4 in |  |  |  | Compliance Insulation-5 | 0.8 | 0.013 | 1 | 0.27 | 5
Drop Ceiling |  | 0.292 | NA | NA | Expanded Polystyrene - EPS - 4 1/16 in | 4.05 | 0.02 | 1 | 0.27 | 16.88
Outside Layer | Acoustic Tile- 3/4 in. |  |  |  | Compliance Insulation - R5 |  |  |  |  | 5
Floor Slab |  | NA | NA | 0.72 | Compliance insulation R9.83 |  |  |  |  | 9.83
HeavyMassWall |  | 0.063 | NA | NA | Compliance insulation R19.63 |  |  |  |  | 19.63
Outside Layer | Stucco - 7/8 in |  |  |  | Compliance insulation R24.86 |  |  |  |  | 24.86
Layer 2 | Building Paper - 1/16 in |  |  |  | Outside Air Film | ** All construction assembley Ufactors in this tab include air films ** |  |  |  | Rvalue (ft2*F*hr/Btu)
Layer 3 | Expanded Polystyrene - EPS - 3 1/3 in |  |  |  | Exterior Wall |  |  |  |  | 0.17
Layer 4 | Concrete - 140 lb/ft3 - 4 in |  |  |  | Roof |  |  |  |  | 0.17
Layer 6 | Gypsum Board - 1/2 in |  |  |  | Exterior Floor |  |  |  |  | 0.17
WoodRoof |  | 0.034 | NA | NA | Underground Wall |  |  |  |  | NA
Outside Layer | Asphalt shingles - 1/4 in |  |  |  | Underground Floor |  |  |  |  | NA
Layer 2 | Building Paper - 1/16 in |  |  |  | Interior Wall |  |  |  |  | 0.68
Layer 3 | Plywood - 1/2 in |  |  |  | Ceiling |  |  |  |  | 0.92
Layer 4 | Composite Wood Frame 24 in OC R-30 cavity insulation |  |  |  | Interior Floor |  |  |  |  | 0.61
Layer 5 | Gypsum Board - 1/2 in |  |  |  | Inside Air Film | ** All construction assembley Ufactors in this tab include air films ** |  |  |  | Rvalue (ft2*F*hr/Btu)
MetalFrameWallTest |  | 0.042 | NA | NA | Exterior Wall |  |  |  |  | 0.68
Outside Layer | Stucco - 7/8 in |  |  |  | Roof |  |  |  |  | 0.61
Layer 2 | Building Paper - 1/16 in |  |  |  | Exterior Floor |  |  |  |  | NA
Layer 3 | Expanded Polystyrene - EPS - 4 1/16 in |  |  |  | Underground Wall |  |  |  |  | NA
Layer 4 | Compliance Insulation-5 |  |  |  | Underground Floor |  |  |  |  | NA
Layer 5 | Air - Metal Wall Framing - 16 or 24 in OC |  |  |  | Interior Wall |  |  |  |  | NA
Layer 6 | Gypsum Board - 1/2 in |  |  |  | Ceiling |  |  |  |  | NA
Floor Slab Test |  | NA | NA | 0.46 | Interior Floor |  |  |  |  | NA
RoofTest |  | 0.028 | NA | NA | Exterior Floor |  |  |  |  | 0.92
Outside Layer | Metal Standing Seam - 1/16 in |  |  |  | Underground Wall |  |  |  |  | 0.68
Layer 2 | Expanded Polystyrene - EPS - 6 7/8 in |  |  |  | Underground Floor |  |  |  |  | 0.92
Layer 3 | Expanded Polystyrene - EPS - 1 1/2 in |  |  |  | Interior Floor |  |  |  |  | 0.92
NACM_AtticRfWood |  | 0.049 | NA | NA
Outside Layer | Metal Standing Seam - 1/16 in
Layer 2 | Compliance insulation R19.63
NACM_AtticRfWood_0.39 |  | 0.039 | NA | NA
Outside Layer | Metal Standing Seam - 1/16 in
Layer 2 | Compliance insulation R24.86
Attic_Floor |  | 0.039 | NA | NA
Outside Layer | Compliance Insulation R9.83
Layer 2 | Plywood - 5/8 in
Layer 3 | Carpet - 3/4 in

## Test Criteria
|  | 01 | 02 | 03 | 07 | 08 | 09 | 60 | 61 | 62 | 66 (To Be Completed) | 67 (To Be Completed) |  | 15 | 16 (VOID - Removed) | 17 | 18 | 19 | 20 | 21 (VOID - Removed) | 22 | 23 | 24 | 32 | 33 | 34 | 35 | 72 | 73 | 75 | 76 | 77 | 79 |  | 25 | 42 | 43 | 44 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 |  | 92 | 93 | 94 | 98 | 99 | 100 | 102 | 103 | 104 | 106 |  | 110 | 112 | 113 | 115 |  | 118 | 119 | 120 | 121 | 123 | 124 |  | 116 | 118 | 120 | 121 | 123 | 124 | 110 | 113 | 126 | 127 | 128 | 130 | 132 | 133 | 135 | 136 | 137 | 139 | 141 | 142 | 143 | 145
Test Run Name | Stand Alone Retail 0500 RetlMed | 0500115--RetlMed-EnvelopeRoofInsulation | 0500215--RetlMed-EnvelopeWallInsulation | 0500315--RetlMed-EnvelopeHeavy | 0500706--RetlMed-EnvelopeRoofInsulation | 0500806--RetlMed-EnvelopeWallInsulation | 0500906--RetlMed-EnvelopeHeavy | 0506007--RetlMed-Daylighting SRRBaseHighVT | 0506107--RetlMed-Daylighting SRR4.67 | 05062 07--RetlMed-Daylighting SRR4.67HighVT | 0566 (To Be Completed)16--RetlMed-HVAC DuctLoss | 0567 (To Be Completed)06--RetlMed-HVAC DuctLoss | Medium Office 0300 OffMed | 0301516-OffMed-FloorSlabInsulation | 03016 (VOID - Removed)16-OffMed-Envelope Infiltration | 0301716-OffMed-GlazingWindowU | 0301816-OffMed-GlazingWindowSHGC | 0301916-OffMed-GlazingWindowUSHGC | 0302006-OffMed-FloorSlabInsulation | 03021 (VOID - Removed)06-OffMed-Envelope Infiltration | 0302206-OffMed-GlazingWindowU | 0302306-OffMed-GlazingWindowSHGC | 0302406-OffMed-GlazingWindowUSHGC | 0303216-OffMed-LightingLowLPD | 0303316-OffMed-LightingHighLPD | 0303406-OffMed-LightingLowLPD | 0303506-OffMed-LightingHighLPD | 0307216-OffMed-HVACPVAV Design | 0307316-OffMed-HVACPVAV SATControl | 0307516-OffMed-HVACPVAV EconomizerType | 0307606-OffMed-HVACPVAV Design | 0307706-OffMed-HVACPVAV SATControl | 0307906-OffMed-HVACPVAV EconomizerType | Large Office | 0402507-OffLrg-WWR20 | 0404207-OffLrg-Cont.DimHighVT | 0404307-OffLrg-StepDim | 0404407-OffLrg-StepDimHighVT | 048115--OffLrg-HVACChWDeltaT | 048215--OffLrg-HVACVAV CWSetpoint | 048315--OffLrg-HVACTowerEff | 0408416--OffLrg-HVACChillerCOP | 0408516--OffLrg-HVACChWDeltaT | 048616--OffLrg-HVACVAV CWSetpoint | 048716--OffLrg-HVACTowerEff | 0408806--OffLrg-HVACChillerCOP | 0408906--OffLrg-HVACChWDeltaT | 049006--OffLrg-HVACVAV CWSetpoint | 049106--OffLrg-HVACTowerEff | Strip Mall 1000 RetlStrp | 1009215--RetlStrp-HVACPSZ DXCOP | 1009315--RetlStrp-HVACPSZ HeatEff | 1009415--RetlStrp-HVACPSZ EconomizerControl | 1009806--RetlStrp-HVACPSZ DXCOP | 1009906--RetlStrp-HVACPSZ HeatEff | 10010006--RetlStrp-HVACPSZ EconomizerControl | 10010216--RetlStrp-HVACPTAC DXCOP | 10010306--RetlStrp-HVACPTAC DXCOP | 10010416--RetlStrp-FPFC | 100106 06--RetlStrp-FPFC | Simple Geometry Small Office 02000 OffSml-SG | 0211015-OffSml-SG-EnvRoofInsulation | 0211206-OffSml-SG-EnvRoofInsulation | 0211315-OffSml-SG-EnvWallInsulation | 0211506-OffSml-SG-EnvWallInsulation | Simple Geometry Medium Office 03000 OffMed-SG | 0311816-OffMed-SG-WWR40 | 0311916-OffMed-SG-WWR20 | 0312006-OffMed-SG-WWR40 | 0312106-OffMed-SG-WWR20 | 0312316-OffMed-SG-WinUSHGC | 0312406-OffMed-SG-WinUSHGC | Simple Geometry Medium Retail 05000 RetlMed-SG | 0511615RetlMed-SG-SRR5 | 0511806RetlMed-SG-SRR5 | 0512016RetlMed-SG-SRR1 | 0512106RetlMed-SG-SRR1 | 0512316RetlMed-SG-SkyUSHGC | 0512406RetlMed-SG-SkyUSHGC | 0511015RetlMed-SG-EnvRoofInsulation | 0511315RetlMed-SG-EnvWallInsulation | 0312616-OffMed-Plenum | 0312706-OffMed-Plenum | 0512815-RetlMed-SZVAV | 0513006-RetlMed-SZVAV | 0413216-OffLrg-CRAC | 0413306-OffLrg-CRAC | 0313516-OffMed-LabExhDOAS | 0313606-OffMed-LabExhDOAS | 1013715--RetlStrp-EvapCooler | 1013906--RetlStrp-EvapCooler | 0314116-OffMed-FanPwrBox | 0314206-OffMed-FanPwrBox | 1014315--RetlStrp-WSHP | 1014506--RetlStrp-WSHP
Baseline |  | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500015-RetlMed-Baseline | 0500006-RetlMed-Baseline | 0500006-RetlMed-Baseline | 0500006-RetlMed-Baseline | 0500007-RetlMed-Baseline | 0500007-RetlMed-Baseline | 0500007-RetlMed-Baseline | 0500016-RetlMed-Baseline | 0500006-RetlMed-Baseline |  | 0300016-OffMed-Baseline | 0300016-OffMed-Baseline | 0300016-OffMed-Baseline | 0300016-OffMed-Baseline | 0300016-OffMed-Baseline | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline | 0300016-OffMed-Baseline | 0300016-OffMed-Baseline | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline | 03000-OffMed-Baseline | 03000-OffMed-Baseline | 0300016-OffMed-Baseline | 03000-OffMed-Baseline | 0300006-OffMed-Baseline | 0300006-OffMed-Baseline |  | 0400007-OffLrg-Baseline | 0400007-OffLrg-Baseline | 0400007-OffLrg-Baseline | 0400007-OffLrg-Baseline | 0400015-OffLrg-Baseline | 0400015-OffLrg-Baseline | 0400015-OffLrg-Baseline | 0400016-OffLrg-Baseline | 0400016-OffLrg-Baseline | 0400016-OffLrg-Baseline | 0400016-OffLrg-Baseline | 0400006-OffLrg-Baseline | 0400006-OffLrg-Baseline | 0400006-OffLrg-Baseline | 0400006-OffLrg-Baseline |  | 1000015-RetlStrp-BaselinePSZ | 1000015-RetlStrp-BaselinePSZ | 1000015-RetlStrp-BaselinePSZ | 1000006-RetlStrp-BaselinePSZ | 1000006-RetlStrp-BaselinePSZ | 1000006-RetlStrp-BaselinePSZ | 1000016-RetlStrp-BaselinePTAC | 1000006-RetlStrp-BaselinePTAC | 1000016-RetlStrp-BaselinePTAC | 1000006-RetlStrp-BaselinePTAC |  | 0200015-OffSml-SG-Baserun | 0200006-OffSml-SG-Baserun | 0200015-OffSml-SG-Baserun | 0200006-OffSml-SG-Baserun |  | 0300016-OffMed-SG-Baseline | 0300016-OffMed-SG-Baseline | 0300006-OffMed-SG-Baseline | 0300006-OffMed-SG-Baseline | 0300016-OffMed-SG-Baseline | 0300006-OffMed-SG-Baseline |  | 0500015RetlMed-SG-Baseline | 0500006RetlMed-SG-Baseline | 0500016RetlMed-SG-Baseline | 0500006RetlMed-SG-Baseline | 0500016RetlMed-SG-Baseline | 0500006RetlMed-SG-Baseline | 0500015RetlMed-SG-Baseline | 0500015RetlMed-SG-Baseline | 0300016-OffMed-Baseline | 0300006-OffMed-Baseline | 0500015-RetlMed-Baseline | 0500006-RetlMed-Baseline | 0400016-OffLrg-CRAH | 0400006-OffLrg-CRAH | 0316-OffMed-LabwExhPVAV | 0306-OffMed-LabwExhPVAV | 1000015-RetlStrp-BaselinePSZ | 1000006-RetlStrp-BaselinePSZ | 0300016-OffMed-Baseline | 0300006-OffMed-Baseline | 1000015-RetlStrp-BaselinePTAC | 1000006-RetlStrp-BaselinePTAC
Prototype Description |  | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Change Roof and Wall construction asssembly to Wood Framed Roof and Heavy Mass wall. Roof and Wall assembly overall U value of test case= Baseline construction assembly U value | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Change Roof and Wall construction asssembly to Wood Framed Roof and Heavy Mass wall. Roof and Wall assembly overall U value of test case= Baseline construction assembly U value | Increase Visible Transmittance of skylights by 20% compared to baseline case | Increase skylight area such that overall SRR fraction is 0.0467. | Increase skylight area such that overall SRR fraction is 0.0467 and visible transmittance of skylights by 20% compared to baseline case. | Increase ductloss in the zones served by Pacakaged Single Zone systems to 14%. The baseline for this test is a modified version of Stand-Alone Retail prototype. See details below | Increase ductloss in the zones served by Pacakaged Single Zone systems to 14%. The baseline for this test is a modified version of Stand-Alone Retail prototype. See details below |  | Change Floor slab F factor of permiter zones in the bottom floor to 0.46 | Increase Exterior Wall Infiltration by 10% compared to baseline case | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case | Change Floor slab F factor of permiter zones in the bottom floor to 0.46 | Increase Exterior Wall Infiltration by 10% compared to baseline case | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case | Decrease LPD by 20% compared to baseline case | Increase LPD by 20% compared to baseline case | Decrease LPD by 20% compared to baseline case | Increase LPD by 20% compared to baseline case | Change static pressure and motor efficiency of all VAV fans. See details below | Change supply air temperature reset based on Outside air. See details below | Change Economizer Type to Fixed Dry bulb with 70 F high limit | Change static pressure and motor efficiency of all VAV fans. See details below | Change supply air temperature reset based on Outside air. See details below | Change Economizer Type to Fixed Dry bulb with 70 F high limit |  | Reduce window area such that overall window to wall ratio is 20% | Increase Visible Transmittance of windows by 20% compared to baseline case | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20% | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 80 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 25 gpm/hp | Change Chiller COP See below for details | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 80 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 80 gpm/hp | Change Chiller COP See below for details | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 80 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 25 gpm/hp |  | Increase efficiency of DX coil | Increase efficiency of the Heating coil to 90% | Change Economizer from Integrated as in baseline to NonIntegrated. See below for details | Increase efficiency of DX coil | Increase efficiency of the Heating coil to 90% | Change Economizer from Integrated as in baseline to NonIntegrated. See below for details | Increase efficiency of DX coil | Increase efficiency of DX coil | Comparison of PTAC system with Fan Coil System with DOAS. For details on Fan Coil system, refer StripMall FanCoil | Comparison of PTAC system with Fan Coil System with DOAS. For details on Fan Coil system, refer StripMall FanCoil |  | Decrease overall U value of Roof by 20% compared to baserun case | Decrease overall U value of Roof by 20% compared to baserun case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case |  | Change WWR from 33% to 40% | Change WWR from 33% to 20% | Change WWR from 33% to 40% | Change WWR from 33% to 20% | Decrease U value & SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case |  | Change SRR to 5% | Change SRR to 5% | Change SRR to 1% | Change SRR to 1% | Decrease U value of skylights by 20% compared to baseline case | Decrease U value of skylights by 20% compared to baseline case | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Impact of heat gain distribution to plenum zones. In this test case, the HVAC return is via plenum zone. | Impact of heat gain distribution to plenum zones. In this test case, the HVAC return is via plenum zone. | Building is served by Single Zone VAV systems | Building is served by Single Zone VAV systems | Top Core space modelled as a Computer room with Process load of 20 W/ft2. This space is served by a CRAC unit and is compared against a similar model served by a CRAH unit | Top Core space modelled as a Computer room with Process load of 20 W/ft2. This space is served by a CRAC unit and is compared against a similar model served by a CRAH unit | Core Mid space of Medium Office building is modelled as a Lab space. This space is served by PTAC with DOAS and has an exhaust system. This case is compared against the OffMed-LabExh run which is similar to the test case but is served by a PVAV system instead of PTAC with DOAS | Core Mid space of Medium Office building is modelled as a Lab space. This space is served by PTAC with DOAS and has an exhaust system. This case is compared against the OffMed-LabExh run which is similar to the test case but is served by a PVAV system instead of PTAC with DOAS | Building is served by Direct and Indirect Evaporative Coolers. | Building is served by Direct and Indirect Evaporative Coolers. | All zones in Mid floor is served by VAV with series fan powered boxes. All zones in top floor is served by VAV with parallel fan powered boxes. | All zones in Mid floor is served by VAV with series fan powered boxes. All zones in top floor is served by VAV with parallel fan powered boxes. | Building is served by WSHP for heating and cooling and DOAS for ventilation | Building is served by WSHP for heating and cooling and DOAS for ventilation
Location |  | CZ15 | CZ15 | CZ15 | CZ06 | CZ06 | CZ06 | CZ07 | CZ07 | CZ07 | CZ16 | CZ06 | CZ000 | CZ16 | CZ16 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ06 | CZ06 | CZ16 | CZ16 | CZ06 | CZ06 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ000 | CZ07 | CZ07 | CZ07 | CZ07 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ06 | CZ000 | CZ15 | CZ15 | CZ15 | CZ06 | CZ06 | CZ06 | CZ16 | CZ06 | CZ16 | CZ06 | CZ000 | CZ15 | CZ06 | CZ15 | CZ06 | CZ00 | CZ16 | CZ16 | CZ06 | CZ06 | CZ16 | CZ06 | CZ000 | CZ15 | CZ06 | CZ16 | CZ06 | CZ16 | CZ06 | CZ15 | CZ15 | CZ16 | CZ06 | CZ15 | CZ06 | CZ16 | CZ06 | CZ16 | CZ06 | CZ15 | CZ06 | CZ16 | CZ06 | CZ15 | CZ06
Fuel Type |  | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail Ductloss Baseline | Refer StandAloneRetail Ductloss Baseline |  | Refer MediumOffice | Refer MediumOffice | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer MediumOffice | Refer MediumOffice | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office |  | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office |  | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC |  | Small Office | Small Office | Small Office | Small Office | [5 empty] | Refer Medium Office | Refer Medium Office | [7 empty] | Refer StandAloneRetail | Refer StandAloneRetail | Same as OffMed-Baseline except HVAC return air is via the plenum zone | Same as OffMed-Baseline except HVAC return air is via the plenum zone | Same as RetlMed-Baseline | Same as RetlMed-Baseline | Same As Off Lrg CRAH | Same As Off Lrg CRAH | Same As Off Med-LabwExhPVAV | Same As Off Med-LabwExhPVAV | Same as RetlStrip-BaselinePSZ | Same as RetlStrip-BaselinePSZ | Same as OffMed-Baseline | Same as OffMed-Baseline | Same as RetlStrp-BaselinePTAC | Same as RetlStrp-BaselinePTAC
Total Floor Area (sq feet)
Building shape
Aspect Ratio
Number of Floors
Window Fraction (Window-to-Wall Ratio) | [34 empty] | 25: 20% of above-grade gross wall | [17 empty] | 40% | 20% | 40% | 20%
Window Locations | [34 empty] | 25: Refer Large Office
Shading Geometry
Azimuth
Thermal Zoning
Floor to floor height (feet)
Floor to ceiling height (feet)
Glazing sill height (feet)
Exterior walls
Construction |  |  |  | HeavyMass Wall |  |  | HeavyMass Wall
Construction Assembly Layers |  |  | Refer MetalFrameWallTest | Refer HeavyMassWall |  | Refer MetalFrameWallTest | Refer HeavyMassWall | [73 empty] | Refer MetalFrameWallTest
U-factor (Btu / h * ft2 * °F) |  |  | 0.042 | 0.063 |  | 0.042 | 0.063 | [56 empty] | Small Office | Small Office | [15 empty] | 0.042
Roof |  |  |  | Wood Framed Roof |  |  | Wood Framed Roof
Construction |  |  |  | Refer WoodRoof |  |  | Refer WoodRoof
Construction Assembly Layers |  | Refer RoofTest |  |  | Refer RoofTest | [56 empty] | 0.039 Btu / h * ft2 * °F Refer NACM_AtticRfWood_0.39 for details | 0.039 Btu / h * ft2 * °F Refer NACM_AtticRfWood_0.39 for details | [16 empty] | Refer RoofTest
U-factor (Btu / h * ft2 * °F) |  | 0.028 |  | 0.034 | 0.028 |  | 0.034 | [54 empty] | Small Office | Small Office | [16 empty] | 0.028
Aged Solar Reflectance Aged Thermal Emittance |  | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | [72 empty] | Refer StandAloneRetail
Dimensions
Tilts and orientations
Window
Dimensions
Glass-Type and frame
U-factor (Btu / h * ft2 * °F) | [15 empty] | 0.29 |  | 0.29 |  |  | 0.29 |  | 0.29 | [47 empty] | 0.29 | 0.29
SHGC | [15 empty] | Refer Medium Office | 0.2 | 0.2 |  |  | Refer Medium Office | 0.2 | 0.2 | [47 empty] | 0.2 | 0.2
Visible transmittance | [16 empty] | Refer Medium Office | Refer Medium Office |  |  |  | Refer Medium Office | Refer Medium Office | [11 empty] | 42: 0.504; 44: 0.504 | [21 empty] | Refer Medium Office | Refer Medium Office
Operable area | [34 empty] | 42: Refer Large Office; 44: Refer Large Office
Skylight | [9 empty] | Skylight to Roof Ratio- 0.0467 Core Retail, Refer Skylight Layout for details
Dimensions | [8 empty] | Skylight to Roof Ratio- 0.0467 Core Retail, Refer Skylight Layout for details
Glass-Type and frame | [8 empty] | Refer StandAloneRetail
U-factor (Btu / h * ft2 * °F) | [77 empty] | 0.464 | 0.464
SHGC
Visible transmittance | [7 empty] | 0.588 |  | 0.588
Foundation | [7 empty] | Refer StandAloneRetail |  | Refer StandAloneRetail
Foundation Type
Construction | [13 empty] | Fully Insulated unheated slab on grade with R-5 insulation |  |  |  |  | Fully Insulated unheated slab on grade with R-5 insulation
F factor (Btu / h * ft2 * °F) | [13 empty] | F factor= 0.46 |  |  |  |  | F factor= 0.46
Thermal properties for basement walls | [13 empty] | Refer MediumOffice |  |  |  |  | Refer MediumOffice
Interior Surfaces
Construction
Construction Assembly Layers
Dimensions
Air Barrier System | [14 empty] | Refer MediumOffice |  |  |  |  | Refer MediumOffice
Infiltration
HVAC System Type
System Type | [58 empty] | 4 pipe fan coil system (One FPFC per zone with central boiler and chiller) | 4 pipe fan coil system (One FPFC per zone with central boiler and chiller) | [23 empty] | Single Zone VAV (one SZVAVAC per zone) | Single Zone VAV (one SZVAVAC per zone) |  |  | Core Mid is served by PTAC with DOAS and Exhaust system. | Core Mid is served by PTAC with DOAS and Exhaust system. | Evaporative Coolers (One PSZ per zone). LG Store 1, LG Store 2, Sm Store 1, SM Store 2, and SM Store 3 are served by Direct Evap Coolers. Rest of the zones are served by Indirect Evap Coolers. | Evaporative Coolers (One PSZ per zone). LG Store 1, LG Store 2, Sm Store 1, SM Store 2, and SM Store 3 are served by Direct Evap Coolers. Rest of the zones are served by Indirect Evap Coolers. | Packaged VAV with hot-water reheat and parallel fan powered boxes with one system per floor serving all zones in the floor | Packaged VAV with hot-water reheat and parallel fan powered boxes with one system per floor serving all zones in the floor | Water Source Heat pump (One per zone) | Water Source Heat pump (One per zone)
Heating type | [10 empty] | 3 single-zone roof top units serving thermal zones back_space, point_of_sale, and front_retail with Duct loss - 14% of design flow rate. | 3 single-zone roof top units serving thermal zones back_space, point_of_sale, and front_retail with Duct loss - 14% of design flow rate. | [46 empty] | Heating hot water | Heating hot water | [23 empty] | Gas Furnace | Gas Furnace |  |  | Gas furnace inside the packaged air conditioning unit | Gas furnace inside the packaged air conditioning unit | Gas Furnance | Gas Furnance | Gas furnace inside the packaged air conditioning unit | Gas furnace inside the packaged air conditioning unit | Heat Pump | Heat Pump
Cooling type | [10 empty] | Refer StandAloneRetail Ductloss Baseline | Refer StandAloneRetail Ductloss Baseline | [46 empty] | Chilled water system | Chilled water system | [23 empty] | Direct Expansion | Direct Expansion |  |  | Packaged air conditioning unit | Packaged air conditioning unit | Direct Expansion and Evap cooling | Direct Expansion and Evap cooling | Direct Expansion | Direct Expansion | Direct Expansion | Direct Expansion
Distribution and terminal units | [58 empty] | 4 pipe fan coil unit | 4 pipe fan coil unit | [23 empty] | Variable Air Volume distribution | Variable Air Volume distribution |  |  | PTAC and DOAS serving Core Mid space has constant volume fans | PTAC and DOAS serving Core Mid space has constant volume fans | Constant Air Volume distribution | Constant Air Volume distribution | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. All zones in top floor is served by VAV with parallel fan powered boxes. | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. All zones in top floor is served by VAV with parallel fan powered boxes. | Constant Air Volume distribution | Constant Air Volume distribution
HVAC Sizing
Cooling | [58 empty] | Refer SizingValues | Refer SizingValues | [23 empty] | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues
Heating | [58 empty] | Refer SizingValues | Refer SizingValues | [23 empty] | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues
HVAC Efficiency
Cooling | [34 empty] | 84: 0.464 kW/ton, 0.35 IPLV; 88: 0.464 kW/ton, 0.35 IPLV |  | EER-13, IEER-14.4 |  |  | EER-13, IEER-14.4 |  |  | EER-13, IEER-14.4 | EER-13, IEER-14.4 | 0.590 kw/ton, 0.4 IPLV | 0.590 kw/ton, 0.4 IPLV | [23 empty] | EER-11.20, IEER-12.9, SEER- 13.6 Note: EER, COP includes fan heat | EER-11.20, IEER-12.9, SEER- 13.6 Note: EER, COP includes fan heat | CRAC EER-11.20, IEER-12.9 | CRAC EER-11.20, IEER-12.9 | PTAC EER: 11.2, DOAS EER :9.8 Note: EER, COP includes fan heat | PTAC EER: 11.2, DOAS EER :9.8 Note: EER, COP includes fan heat | EER-11.20 / COP-3.28 DOAS EER:10.0 Note: EER, COP includes fan heat | EER-11.20 / COP-3.28 DOAS EER:10.0 Note: EER, COP includes fan heat |  |  | DOAS- 11.2 EER, 12.9-IEER. WSHP EER-13.5 Note: EER includes fan heat | DOAS- 11.2 EER, 12.9-IEER. WSHP EER-13.5 Note: EER includes fan heat
Heating | [34 empty] | 84: Refer Large Office; 88: Refer Large Office |  | Refer StripMall PTAC | 90% |  | Refer StripMall PTAC | 90% |  | Refer StripMall PTAC | Refer StripMall PTAC | 80% | 80% | [23 empty] | 82% | 82% |  |  | 80% | 80% | Boiler efficiency:80% | Boiler efficiency:80% |  |  | 82% | 82%
HVAC Control | [51 empty] | Refer StripMall PSZ |  |  | Refer StripMall PSZ | [34 empty] | Same as RetlStrip-BaselinePSZ | Same as RetlStrip-BaselinePSZ | Same as OffMed-Baseline | Same as OffMed-Baseline
Thermostat Setpoint | [58 empty] | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | [23 empty] | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | Same As Off Lrg CRAH | Same As Off Lrg CRAH
Thermostat Setback | [58 empty] | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | [23 empty] | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating
Design Supply air temperature | [34 empty] | 81: 56 F | [9 empty] | Cooling 55F Heating 95 F | Cooling 55F Heating 95 F | [23 empty] | Cooling 55F Heating 95 F | Cooling 55F Heating 95 F
Supply air temperature reset | [28 empty] | Reset by Outdoor Air. Supply 65F @ OAT 45F Supply 50F @ OAT 60F |  |  | Reset by Outdoor Air. Supply 65F @ OAT 45F Supply 50F @ OAT 60F |  |  | 81: Refer Large Office | [9 empty] | No SAT Control | No SAT Control | [23 empty] | No SAT Control | No SAT Control |  |  | No SAT control for DOAS | No SAT control for DOAS
Chilled water supply temperatures | [28 empty] | Refer Medium Office |  |  | Refer Medium Office |  |  | 82: Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature; 85: 52 F, Delta T 12 F; 86: Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature; 89: 52 F, Delta T 12 F; 90: Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature | [9 empty] | 44°F | 44°F | [23 empty] | NA | NA
Chilled water return temperatures | [34 empty] | 82: Refer Large Office; 86: Refer Large Office; 90: Refer Large Office | [9 empty] | 64 F | 64 F | [23 empty] | NA | NA
Chilled water supply temperature reset | [34 empty] | 85: Refer Large Office; 89: Refer Large Office | [9 empty] | Fixed reset | Fixed reset | [23 empty] | NA | NA
Condenser Type | [29 empty] | Integrated Fixed Dry bulb -70F high limit |  |  | Integrated Fixed Dry bulb -70F high limit | [25 empty] | Water cooled, no reset | Water cooled, no reset | [23 empty] | NA | NA | [8 empty] | Watersource | Watersource
Hot water supply temperatures | [29 empty] | Refer Medium Office |  |  | Refer Medium Office | [25 empty] | 180°F | 180°F | [23 empty] | NA | NA
Hot water supply temperature reset | [58 empty] | Fixed reset | Fixed reset | [23 empty] | NA | NA
Economizers | [52 empty] | Non-Integrated Economizer (Diff. DB) Economizer max limit set to 55 F(cooling supply temperature) |  |  | Non-Integrated Economizer (Diff. DB) Economizer max limit set to 55 F(cooling supply temperature) |  |  | No economizer | No economizer | [23 empty] | Differential Dry bulb economizer (Integrated) | Differential Dry bulb economizer (Integrated)
Ventilation | [52 empty] | Refer StripMall PSZ |  |  | Refer StripMall PSZ |  |  | DOAS with Max of 15 cfm/person or 0.15 cfm/ft2 | DOAS with Max of 15 cfm/person or 0.15 cfm/ft2 | [23 empty] | Point of Sale & Core and Front Retail -0.2 cfm/ft2; Backspace, Front Entry-0.15 cfm/ft2 | Point of Sale & Core and Front Retail -0.2 cfm/ft2; Backspace, Front Entry-0.15 cfm/ft2 |  |  | DOAS with 0.15 cfm/ft3 | DOAS with 0.15 cfm/ft3 |  |  |  |  | DOAS with 0.15 cfm/ft3 | DOAS with 0.15 cfm/ft3
Fan
Fan type | [58 empty] | OnOff | OnOff | [23 empty] | Variable Volume for all Conditioned zones | Variable Volume for all Conditioned zones | [8 empty] | Constant Volume | Constant Volume
Supply Fan Total Efficiency (%) | [58 empty] | 60% | 60% | [23 empty] | 56.25% (all fans) | 56.25% (all fans) | [8 empty] | 60% | 60%
Fan Motor Efficiency | [27 empty] | 98% |  |  | 98% | [27 empty] | 95% | 95% | [23 empty] | 86.5% (all fans) | 86.5% (all fans) | [8 empty] | 95% | 95%
Supply Fan Pressure Rise | [27 empty] | 3 in H2O |  |  | 3 in H2O | [27 empty] | 1.5 in H2O | 1.5 in H2O | [23 empty] | 2.5in H2O (all fans) | 2.5in H2O (all fans) | [8 empty] | 1.5 in H2O | 1.5 in H2O
Pump | [27 empty] | Refer Medium Office |  |  | Refer Medium Office | [56 empty] | Same as Off-Med LabwExhPVAV | Same as Off-Med LabwExhPVAV
Pump Type | [58 empty] | Variable speed pumps for condenser water, chilled water and heating hot water systems | Variable speed pumps for condenser water, chilled water and heating hot water systems | [23 empty] | NA | NA | [8 empty] | Constant Speed Pumps for Cooling Tower and Boiler | Constant Speed Pumps for Cooling Tower and Boiler
Rated Pump Head | [58 empty] | HW- 40 ftH2O CHW- 30.0 ftH2O CW- 40 ftH2O | HW- 40 ftH2O CHW- 30.0 ftH2O CW- 40 ftH2O | [23 empty] | NA | NA | [8 empty] | HW- 40.0 ftH2O CW- 40.0 ftH2O | HW- 40.0 ftH2O CW- 40.0 ftH2O
Pump Motor Power per Unit Flow | [58 empty] | Hw, CW: 12 W/gpm, CHW: 9 W/gpm | Hw, CW: 12 W/gpm, CHW: 9 W/gpm | [23 empty] | NA | NA | [8 empty] | HW: 12 W/gpm CW: 12 W/gpm | HW: 12 W/gpm CW: 12 W/gpm
Pump Efficiency | [58 empty] | Motor efficiency: 0.9 | Motor efficiency: 0.9 | [23 empty] | NA | NA | [8 empty] | Motor efficiency: 0.9 | Motor efficiency: 0.9
Cooling Tower
Cooling Tower Type | [58 empty] | open cooling tower with variable speed fan | open cooling tower with variable speed fan | [23 empty] | NA | NA | [8 empty] | Open Tower | Open Tower
Tower range | [34 empty] | 83: 80 gpm/hp; 87: 80 gpm/hp; 91: 80 gpm/hp | [9 empty] | 10F (Design CW supply temp. 85F, CW return temp 95F) | 10F (Design CW supply temp. 85F, CW return temp 95F) | [23 empty] | NA | NA | [8 empty] | 10F (Design CW supply temp. 85F, CW return temp 95F) | 10F (Design CW supply temp. 85F, CW return temp 95F)
Service Water Heating | [58 empty] | Same as RetlStrip-BaselinePTAC | Same as RetlStrip-BaselinePTAC | [23 empty] | Same as RetlMed-Baseline | Same as RetlMed-Baseline | [8 empty] | Same as RetlStrip-BaselinePTAC | Same as RetlStrip-BaselinePTAC
SWH type
Fuel type
Thermal efficiency (%)
Water temperature setpoint
Water Heater Max Capacity (Btuh)
Lighting Load
Lighting power density (W/ft2) | [23 empty] | 0.6 | 0.9 | 0.6 W/ft2 | 0.9 W/ft2
Schedule | [23 empty] | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | bar: 25; 44
Daylighting Controls | [8 empty] | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . | [24 empty] | 25: Refer LargeOfficeDaylight for details; 43: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 44: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.
Plug load | [8 empty] | Refer StandAloneDaylight for more details | Refer StandAloneDaylight for more details | [24 empty] | 25: Refer Large Office; 43: Refer Large Office; 44: Refer Large Office
Electric power density (W/ft2) | [8 empty] | Refer Stand Alone Retail | Refer Stand Alone Retail
Schedule
Occupancy
Average people
Schedule | [85 empty] | Large Office Building Schedule | Large Office Building Schedule | Medium Office Building Schedule | Medium Office Building Schedule
| 05-RetlMed | EnvelopeRoofInsulation | EnvelopeWallInsulation | EnvelopeHeavy | EnvelopeRoofInsulation | EnvelopeWallInsulation | EnvelopeHeavy | Daylighting SRRBaseHighVT | Daylighting SRR4.67 | Daylighting SRR4.67HighVT | HVAC DuctLoss | HVAC DuctLoss | 03-OffMed | FloorSlabInsulation | Envelope Infiltration | GlazingWindowU | GlazingWindowSHGC | GlazingWindowUSHGC | FloorSlabInsulation | Envelope Infiltration | GlazingWindowU | GlazingWindowSHGC | GlazingWindowUSHGC | [6 empty] | HVACPVAV EconomizerType |  | HVACPVAV SATControl | HVACPVAV EconomizerType | 04-OffLrg | WWR20 | Cont.DimHighVT | StepDim | StepDimHighVT | HVACChWDeltaT | HVACVAV CWSetpoint | HVACTowerEff | HVACChillerCOP | HVACChWDeltaT | HVACVAV CWSetpoint | HVACTowerEff | HVACChillerCOP | HVACChWDeltaT | HVACVAV CWSetpoint | HVACTowerEff | 10-RetlStrp | HVACPSZ DXCOP | HVACPSZ HeatEff | HVACPSZ EconomizerControl | HVACPSZ DXCOP | HVACPSZ HeatEff | HVACPSZ EconomizerControl | HVACPTAC DXCOP | HVACPTAC DXCOP | FPFC | FPFC | 02-OffSml-SG | EnvRoofInsulation | EnvRoofInsulation | EnvWallInsulation | EnvWallInsulation | 03-OffMed-SG | WWR40 | WWR20 | WWR40 | WWR20 | WinUSHGC | WinUSHGC | 05-RetlMed-SG | SRR5 | SRR5 | SRR1 | SRR1 | SkyUSHGC | SkyUSHGC | EnvRoofInsulation | EnvWallInsulation | Plenum | Plenum | SZVAV | SZVAV | CRAC | CRAC | LabExhDOAS | LabExhDOAS | EvapCooler | EvapCooler | FanPwrBox | FanPwrBox | WSHP | WSHP
| 000 | 15 | 15 | 15 | 06 | 06 | 06 | 07 | 07 | 07 | 16 | 06 | 000 | 16 | 16 | 16 | 16 | 16 | 06 | 06 | 06 | 06 | 06 | [6 empty] | 16 |  | 06 | 06 | 000 | 07 | 07 | 07 | 07 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 06 | 06 | 06 | 06 | 000 | 15 | 15 | 15 | 06 | 06 | 06 | 16 | 06 | 16 | 06 | 000 | 15 | 06 | 15 | 06 | 00 | 16 | 16 | 06 | 06 | 16 | 06 | 000 | 15 | 06 | 16 | 06 | 16 | 06 | 15 | 15 | 16 | 06 | 15 | 06 | 16 | 06 | 16 | 06 | 15 | 06 | 16 | 06 | 15 | 06
|  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | LightingLowLPD | LightingHighLPD | LightingLowLPD | LightingHighLPD | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline |  | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePTAC | -BaselinePTAC | -BaselinePTAC | -BaselinePTAC |  | -Baserun | -Baserun | -Baserun | -Baserun |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -CRAH | -CRAH | -LabwExhPVAV | -LabwExhPVAV | -BaselinePSZ | -BaselinePSZ | -Baseline | -Baseline | -BaselinePTAC | -BaselinePTAC
[24 empty] | 16 | 16 | 06 | 06 | HVACPVAV Design | HVACPVAV SATControl |  | HVACPVAV Design
[24 empty] | -Baseline | -Baseline | -Baseline | -Baseline | 16 | 16 | 16 | 06

## Sizing Values
Sizing Values | C:\Users\chitran\Documents\CBECC-Com 2016 Projects v1\Sizing Value
Object |  | Characteristics | Units | 0300006-OffMed-SG-Baseline | 0300016-OffMed-SG-Baseline | 0500015-RetlMed-SG-Baseline | 0500006-RetlMed-SG-Baseline | 0400006-OffLrg-CRAH_NDL | 0400016-OffLrg-CRAH_NDL | 0413306-OffLrg-CRAC_NDL | 0413216-OffLrg-CRAC_NDL | 1000015-RetlStrp-BaselinePSZ_NDL | 1000006-RetlStrp-BaselinePSZ_NDL | 1013715-RetlStrp-EvapCooler_NDL | 1013906-RetlStrp-EvapCooler_NDL | 1000015-RetlStrp-BaselinePTAC_NDL | 1000006-RetlStrp-BaselinePTAC_NDL | 1010515-RetlStrp-FPFC_NDL | 1010606-RetlStrp-FPFC_NDL | 1014315-RetlStrp-WSHP_NDL | 1014506-RetlStrp-WSHP_NDL | 0400006-OffLrg-Baserun_NDL | 0400016-OffLrg-Baserun_NDL | 0300006-OffMed-Baseline_NDL | 0300016-OffMed-Baseline_NDL | 0313516-OffMed-LabwExhDOAS_NDL | 0313606-OffMed-LabwExhDOAS_NDL | 0314716-OffMed-LabwExhPVAV_NDL | 0314806-OffMed-LabwExhPVAV_NDL | 0500015-RetlMed-Baseline_NDL | 0500006-RetlMed-Baseline_NDL
Exclude |  |  |  | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | End
Building |  | Climate Zone | none | 6 | 16 | 15 | 6 | 6 | 16 | 6 | 16 | 15 | 6 | 15 | 6 | 15 | 6 | 15 | 6 | 15 | 6 | 6 | 16 | 6 | 16 | 16 | 6 | 16 | 6 | 15 | 6
Building |  | Weather Station | none | TORRANCE_722955 | BLUE-CANYON_725845 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | TORRANCE_722955 | BLUE-CANYON_725845 | TORRANCE_722955 | BLUE-CANYON_725845 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | TORRANCE_722955 | BLUE-CANYON_725845 | TORRANCE_722955 | BLUE-CANYON_725845 | BLUE-CANYON_725845 | TORRANCE_722955 | BLUE-CANYON_725845 | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955
Building |  | Zip Code | none | 90505 | 95715 | 92262 | 90505 | 90505 | 95715 | 90505 | 95715 | 92262 | 90505 | 92262 | 90505 | 92262 | 90505 | 92262 | 90505 | 92262 | 90505 | 90505 | 95715 | 90505 | 95715 | 95715 | 90505 | 95715 | 90505 | 92262 | 90505
Chilled Water Loop
Chiller 1 | 7 | Rated Capacity | Btu/h | NA | NA | NA | NA | 9429060 | 10154700 | 9499900 | 10225500 | NA | NA | NA | NA | NA | NA | 1910000 | 1350000 | NA | NA | 8226710 | 8988130 | NA | NA | NA | NA | NA | NA | NA | NA
Chiller 2 | 7 | Rated Capacity | Btu/h | NA | NA | NA | NA | 9429060 | 10154700 | 9499900 | 10225500 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 8226710 | 8988130 | NA | NA | NA | NA | NA | NA | NA | NA
Chiller 1 Pump | 7 | Flow Capacity | gpm | NA | NA | NA | NA | 942.548 | 1015.08 | 949.629 | 1022.16 | NA | NA | NA | NA | NA | NA | 190.516 | 134.949 | NA | NA | 822.359 | 898.472 | NA | NA | NA | NA | NA | NA | NA | NA
Chiller 1 Pump | 14 | Min Flow Rate | gpm | NA | NA | NA | NA | 282.764 | 304.524 | 284.889 | 306.648 | NA | NA | NA | NA | NA | NA | 57.1548 | 40.4846 | NA | NA | 246.708 | 269.542 | NA | NA | NA | NA | NA | NA | NA | NA
Chiller 2 Pump | 7 | Flow Capacity | gpm | NA | NA | NA | NA | 942.548 | 1015.08 | 949.629 | 1022.16 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 822.359 | 898.472 | NA | NA | NA | NA | NA | NA | NA | NA
Chiller 2 Pump | 14 | Min Flow Rate | gpm | NA | NA | NA | NA | 282.764 | 304.524 | 284.889 | 306.648 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 246.708 | 269.542 | NA | NA | NA | NA | NA | NA | NA | NA
Condenser Water Loop
Cooling Tower | 5 | Rated Capacity | Btu/h | NA | NA | NA | NA | 21995100 | 23687700 | 22160400 | 23853000 | NA | NA | NA | NA | NA | NA | 2230000 | 1580000 | 1030000 | 1030000 | 19190400 | 20966600 | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower Pump | 7 | Flow Capacity | gpm | NA | NA | NA | NA | 4397.36 | 4735.75 | 4430.39 | 4768.78 | NA | NA | NA | NA | NA | NA | 444.957 | 315.178 | 205.201 | 205.201 | 3836.63 | 4191.72 | NA | NA | NA | NA | NA | NA | NA | NA
Cooling Tower Pump | 9 | Electric Power | kW | NA | NA | NA | NA | 52.568 | 56.6133 | 52.9629 | 57.0082 | NA | NA | NA | NA | NA | NA | 5.3192 | 3.7678 | 2.4531 | 2.4531 | 45.8648 | 50.1098 | NA | NA | NA | NA | NA | NA | NA | NA
Hot Water Loop
Boiler 1 | 7 | Rated Capacity | Btu/h | 1210490 | 1371880 | NA | NA | 6677880 | 7332770 | 6677880 | 7332770 | NA | NA | NA | NA | NA | NA | 1480000 | 984960 | 1190000 | 1190000 | 7329620 | 8082520 | 1250840 | 1533280 | 1951830 | 1764970 | 2795440 | 2608580 | NA | NA
Boiler Pump | 7 | Flow Capacity | gpm | 60.5013 | 68.5681 | NA | NA | 333 | 366 | 333 | 366 | NA | NA | NA | NA | NA | NA | 73.8439 | 49.2293 | 237.148 | 237.148 | 366 | 403 | 62.5181 | 76.635 | 97.5544 | 88.2148 | 139.719 | 130.379 | NA | NA
Boiler Pump | 9 | Electric Power | kW | 0.90408 | 1.0246 | NA | NA | 3.9808 | 4.3753 | 3.9808 | 4.3753 | NA | NA | NA | NA | NA | NA | 0.88277 | 0.58851 | 2.835 | 2.835 | 4.3753 | 4.8177 | 0.93421 | 1.1452 | 1.4578 | 1.3182 | 2.0878 | 1.9483 | NA | NA
Cooling Coils
CoreZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim1ZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim2ZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim3ZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim4ZnCoolingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
BasementCoilCooling | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 1265648.125 | 1380707.125 | 1265648.125 | 1380707.125 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1265648.125 | 1380707.125 | NA | NA | NA | NA | NA | NA | NA | NA
BottomVAVCoilCooling | 7 | Gross Capacity/Net Capacity | Btu/h | 536277.625 | 536277.625 | NA | NA | 1265648.125 | 1380707.125 | 1265648.125 | 1380707.125 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1265648.125 | 1380707.125 | 504732.188 | 504732.188 | 504732.188 | 504732.188 | 504732.188 | 504732.188 | NA | NA
MidVAVCoilCooling | 7 | Gross Capacity/Net Capacity | Btu/h | 536277.625 | 643533.188 | NA | NA | 1265648.125 | 1380707 | 1265648.125 | 1380707 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1265648.125 | 1380707 | 536277.938 | 682535.563 | 278315.938 | 218676.828 | 278315.938 | 218676.828 | NA | NA
HiVAVCoilCooling | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 1265648.125 | 1380707 | 1265648.125 | 1380707 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1265648.125 | 1380707 | NA | NA | NA | NA | NA | NA | NA | NA
TopVAVCoilCooling | 7 | Gross Capacity/Net Capacity | Btu/h | 536277.625 | 643533.188 | NA | NA | 399432 | 469920 | 399432 | 469920 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1265648.125 | 1407779.625 | 589905.75 | 682535.563 | 682535.563 | 589905.75 | 682535.563 | 589905.75 | NA | NA
CRAH Cooling | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 3270916.75 | 3270916.75 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
CRAC Cooling | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | 3270916.75 | 3270916.75 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Core Mid DOAS Cooling | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 714600 | 714600 | NA | NA | NA | NA
Core Mid PTAC Cooling | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 317601.156 | 317601.156 | NA | NA | NA | NA
BackSpaceZn_CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | 184009.516 | 122673 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 122673.594 | 122673.594
PointOfSaleZn_CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | 73048.508 | 48699 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 67529.352 | 48699.055
FrontRetailZn_CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | 73048.508 | 48699 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 67529.188 | 48698.938
CoreRetailZn_CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | 775233.063 | 516822 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 516822.125 | 516822.125
LG Store 1 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 146250 | 112500 | 146250 | 112500 | 156000 | 112500 | 158823.531 | 112500 | 112500 | 112500 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
LG Store 2 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 146250 | 112500 | 146250 | 112500 | 156000 | 112500 | 158823.531 | 112500 | 112500 | 112500 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 1 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 73125 | 56250 | 73125 | 56250 | 78000 | 56250 | 79411.766 | 56250 | 56250 | 56250 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 2 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 73125 | 56250 | 73125 | 56250 | 78000 | 56250 | 79411.766 | 56250 | 56250 | 56250 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 3 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 73125 | 56250 | 73125 | 56250 | 78000 | 56250 | 79411.766 | 56250 | 56250 | 56250 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 4 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 73125 | 56250 | 73125 | 56250 | 78000 | 56250 | 79411.766 | 56250 | 56250 | 56250 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 5 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 73125 | 56250 | 73125 | 56250 | 78000 | 56250 | 79411.766 | 56250 | 56250 | 56250 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 6 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 73125 | 56250 | 73125 | 56250 | 78000 | 56250 | 79411.766 | 56250 | 56250 | 56250 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 7 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 73125 | 56250 | 73125 | 56250 | 78000 | 56250 | 79411.766 | 56250 | 56250 | 56250 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 8 Zn CoolingCoil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 73125 | 56250 | 73125 | 56250 | 83571.43 | 56250 | 79411.766 | 56250 | 56250 | 56250 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
DOAS Cooling Coil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 936000 | 675000 | 952941.188 | 675000 | 675000 | 675000 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Lab VAV Cooling Coil | 6 | Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 714602.25 | 714602.25 | NA | NA
Heating Coils
CoreZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim1ZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim2ZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim3ZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim4ZnHeatingCoil | 7 | Rated Capacity (Net or Gross depending on system configuration) | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
BasementCoilHeating | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 1385125.375 | 1511045.875 | 1385125.375 | 1511045.875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1385125.375 | 1511045.875 | NA | NA | NA | NA | NA | NA | NA | NA
CoilHeating-BasementReheat | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 288567.781 | 314801.219 | 288567.781 | 314801.219 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 288567.781 | 314801.219 | NA | NA | NA | NA | NA | NA | NA | NA
BottomVAVCoilHeating | 7 | Gross Capacity | Btu/h | 97817.039 | 97817.039 | NA | NA | 230854.219 | 251840.984 | 230854.219 | 251840.984 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 230854.219 | 251840.984 | 97817.102 | 97817.102 | 97817.102 | 97817.102 | 97817.102 | 97817.102 | NA | NA
CoreBottomReheatCoil | 7 | Gross Capacity | Btu/h | 181032.578 | 181032.578 | NA | NA | 512716.188 | 559326.813 | 512716.188 | 559326.813 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 512716.188 | 559326.813 | 181032.672 | 181032.672 | 181032.672 | 181032.672 | 181032.672 | 181032.672 | NA | NA
PerimeterBottom1ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.098 | 38163.098 | NA | NA | 63457.656 | 69226.531 | 63457.656 | 69226.531 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63457.656 | 69226.531 | 38163.152 | 38163.152 | 38163.152 | 38163.152 | 38163.152 | 38163.152 | NA | NA
PerimeterBottom2ReheatCoil | 7 | Gross Capacity | Btu/h | 24160.592 | 24160.592 | NA | NA | 40893.895 | 44611.527 | 40893.895 | 44611.527 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 40893.895 | 44611.527 | 24160.631 | 24160.631 | 24160.631 | 24160.631 | 24160.631 | 24160.631 | NA | NA
PerimeterBottom3ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.098 | 38163.098 | NA | NA | 63458.074 | 69226.992 | 63458.074 | 69226.992 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63458.074 | 69226.992 | 38163.152 | 38163.152 | 38163.152 | 38163.152 | 38163.152 | 38163.152 | NA | NA
PerimeterBottom4ReheatCoil | 7 | Gross Capacity | Btu/h | 24158.883 | 24158.883 | NA | NA | 40893.613 | 44611.215 | 40893.613 | 44611.215 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 40893.613 | 44611.215 | 24158.859 | 24158.859 | 24158.859 | 24158.859 | 24158.859 | 24158.859 | NA | NA
MidVAVCoilHeating | 7 | Gross Capacity | Btu/h | 97817.039 | 117380.453 | NA | NA | 230854.25 | 251840.969 | 230854.25 | 251840.969 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 230854.25 | 251840.969 | 97817.102 | 136943.938 | 55841.313 | 39886.656 | 55841.313 | 39886.656 | NA | NA
CoreMidReheatCoil | 7 | Gross Capacity | Btu/h | 181032.578 | 217239.109 | NA | NA | 512716.188 | 559326.75 | 512716.188 | 559326.75 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 512716.188 | 559326.75 | 181032.672 | 253445.719 | NA | NA | 814646.563 | 814646.563 | NA | NA
Core Mid PTAC Heating | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterMid1ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.098 | 45795.719 | NA | NA | 63457.656 | 69226.531 | 63457.656 | 69226.531 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63457.656 | 69226.531 | 38163.152 | 53428.414 | 53428.414 | 38163.152 | 53428.414 | 38163.152 | NA | NA
PerimeterMid2ReheatCoil | 7 | Gross Capacity | Btu/h | 24160.592 | 28992.711 | NA | NA | 40893.895 | 44611.527 | 40893.895 | 44611.527 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 40893.895 | 44611.527 | 24160.631 | 33824.883 | 33824.883 | 24160.631 | 33824.883 | 24160.631 | NA | NA
PerimeterMid3ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.098 | 45795.719 | NA | NA | 63458.074 | 69226.992 | 63458.074 | 69226.992 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63458.074 | 69226.992 | 38163.152 | 53428.414 | 53428.414 | 38163.152 | 53428.414 | 38163.152 | NA | NA
PerimeterMid4ReheatCoil | 7 | Gross Capacity | Btu/h | 24158.883 | 28990.658 | NA | NA | 40893.613 | 44611.215 | 40893.613 | 44611.215 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 40893.613 | 44611.215 | 24158.859 | 33822.402 | 33822.402 | 24158.859 | 33822.402 | 24158.859 | NA | NA
HiVAVCoilHeating | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 230854.25 | 251840.969 | 230854.25 | 251840.969 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 230854.25 | 251840.969 | NA | NA | NA | NA | NA | NA | NA | NA
CoreHiReheatCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 512716.188 | 559326.75 | 512716.188 | 559326.75 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 512716.188 | 559326.75 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHi1ReheatCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 63457.656 | 69226.531 | 63457.656 | 69226.531 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63457.656 | 69226.531 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHi2ReheatCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 40893.895 | 44611.527 | 40893.895 | 44611.527 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 40893.895 | 44611.527 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHi3ReheatCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 63458.074 | 69226.992 | 63458.074 | 69226.992 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63458.074 | 69226.992 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHi4ReheatCoil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | 40893.613 | 44611.215 | 40893.613 | 44611.215 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 40893.613 | 44611.215 | NA | NA | NA | NA | NA | NA | NA | NA
TopVAVCoilHeating | 7 | Gross Capacity | Btu/h | 97817.039 | 117380.453 | NA | NA | 72856.398 | 91070.5 | 72856.398 | 91070.5 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 230854.219 | 272827.719 | 107598.813 | 136943.938 | 136943.938 | 107598.813 | 136943.938 | 107598.813 | NA | NA
CoreTopReheatCoil | 7 | Gross Capacity | Btu/h | 181032.578 | 217239.109 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 512716.188 | 605937.313 | 199135.938 | 253445.719 | 253445.719 | 199135.938 | 253445.719 | 199135.938 | NA | NA
PerimeterTop1ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.098 | 45795.719 | NA | NA | 69226.531 | 86533.164 | 69226.531 | 86533.164 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63457.656 | 74995.406 | 41979.465 | 53428.414 | 53428.414 | 41979.465 | 53428.414 | 41979.465 | NA | NA
PerimeterTop2ReheatCoil | 7 | Gross Capacity | Btu/h | 24160.592 | 28992.711 | NA | NA | 44611.527 | 55764.406 | 44611.527 | 55764.406 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 40893.895 | 48329.148 | 26576.695 | 33824.883 | 33824.883 | 26576.695 | 33824.883 | 26576.695 | NA | NA
PerimeterTop3ReheatCoil | 7 | Gross Capacity | Btu/h | 38163.098 | 45795.719 | NA | NA | 69226.992 | 86533.734 | 69226.992 | 86533.734 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 63458.074 | 74995.906 | 41979.465 | 53428.414 | 53428.414 | 41979.465 | 53428.414 | 41979.465 | NA | NA
PerimeterTop4ReheatCoil | 7 | Gross Capacity | Btu/h | 24158.883 | 28990.658 | NA | NA | 44611.215 | 55764.016 | 44611.215 | 55764.016 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 40893.613 | 48328.816 | 26574.746 | 33822.402 | 33822.402 | 26574.746 | 33822.402 | 26574.746 | NA | NA
BackSpaceZn_HeatingCoil | 7 | Gross Capacity | Btu/h | NA | NA | 134253.344 | 89502.227 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 89502.656 | 89502.656
PointOfSaleZn_HeatingCoil | 7 | Gross Capacity | Btu/h | NA | NA | 53296.191 | 35530.793 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 46190.078 | 35530.832
FrontRetailZn_HeatingCoil | 7 | Gross Capacity | Btu/h | NA | NA | 53296.191 | 35530.793 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 46189.965 | 35530.746
CoreRetailZn_HeatingCoil | 7 | Gross Capacity | Btu/h | NA | NA | 565610.063 | 377073.344 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 377073.438 | 377073.438
LG Store 1 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 106704.008 | 82080 | 106704.008 | 82080 | 106704.008 | 82080 | 123120.008 | 82080 | 118124.992 | 118124.992 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
LG Store 2 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 106704.008 | 82080 | 106704.008 | 82080 | 106704.008 | 82080 | 123120.008 | 82080 | 118124.992 | 118124.992 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 1 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 53352.004 | 41040 | 53352.004 | 41040 | 53352.004 | 41040 | 61560.004 | 41040 | 59062.496 | 59062.496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 2 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 53352.004 | 41040 | 53352.004 | 41040 | 53352.004 | 41040 | 61560.004 | 41040 | 59062.496 | 59062.496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 3 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 53352.004 | 41040 | 53352.004 | 41040 | 53352.004 | 41040 | 61560.004 | 41040 | 59062.496 | 59062.496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 4 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 53352.004 | 41040 | 53352.004 | 41040 | 53352.004 | 41040 | 61560.004 | 41040 | 59062.496 | 59062.496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 5 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 53352.004 | 41040 | 53352.004 | 41040 | 53352.004 | 41040 | 61560.004 | 41040 | 59062.496 | 59062.496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 6 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 53352.004 | 41040 | 53352.004 | 41040 | 53352.004 | 41040 | 61560.004 | 41040 | 59062.496 | 59062.496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 7 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 53352.004 | 41040 | 53352.004 | 41040 | 53352.004 | 41040 | 61560.004 | 41040 | 59062.496 | 59062.496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 8 Zn HeatingCoil | 7 | Gross Capacity/Net Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 53352.004 | 41040 | 53352.004 | 41040 | 53352.004 | 41040 | 61560.004 | 41040 | 59062.496 | 59062.496 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Core Mid DOAS Heating Coil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 521372.188 | 521372.188 | NA | NA | NA | NA
Lab Heating Coil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 231721.813 | 231721.813 | 782060.688 | 782060.688 | NA | NA
DOAS Heating Coil | 7 | Gross Capacity | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 640224 | 492480.031 | 738720.063 | 492480.031 | 492480.031 | 492480.031 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Fans
CoreZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim1ZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim2ZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim3ZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim4ZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Basement CAVFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | 42188.27 | 46023.57 | 42188.27 | 46023.57 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 42188.27 | 46023.57 | NA | NA | NA | NA | NA | NA | NA | NA
Bottom VAVFan | 6 | Flow Capacity (max air flow rate) | CFM | 17875.92 | 17875.92 | NA | NA | 42188.27 | 46023.57 | 42188.27 | 46023.57 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 42188.27 | 46023.57 | 17875.932 | 17875.932 | 17875.932 | 17875.932 | 17875.932 | 17875.932 | NA | NA
Mid VAVFan | 6 | Flow Capacity (max air flow rate) | CFM | 17875.92 | 21451.105 | NA | NA | 42188.273 | 46023.566 | 42188.273 | 46023.566 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 42188.273 | 46023.566 | 17875.932 | 25026.305 | 10204.918 | 7289.228 | 10204.918 | 7289.228 | NA | NA
Hi VAVFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | 42188.273 | 46023.566 | 42188.273 | 46023.566 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 42188.273 | 46023.566 | NA | NA | NA | NA | NA | NA | NA | NA
Top VAVFan | 6 | Flow Capacity (max air flow rate) | CFM | 17875.92 | 21451.105 | NA | NA | 13314.4 | 16643 | 13314.4 | 16643 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 42188.27 | 49858.863 | 19663.525 | 25026.305 | 25026.305 | 19663.525 | 25026.305 | 19663.525 | NA | NA
CRAH Fan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | 109030.555 | 109030.555 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
CRAC Fan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 109030.555 | 109030.555 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Lab Exhaust Fan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 23820.074 | 23820.074 | 23820.074 | 23820.074 | NA | NA
Lab Fan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 10586.705 | 10586.705 | 23820.074 | 23820.074 | NA | NA
Core Mid DOAS Fan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 23820 | 23820 | NA | NA | NA | NA
Core Mid PTAC Fan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
BackSpaceZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | 6133.65 | 4089.1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 4089.12 | 4089.12
PointOfSaleZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | 2434.95 | 1623.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2110.292 | 1623.302
FrontRetailZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | 2434.95 | 1623.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2110.287 | 1623.298
CoreRetailZnSupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | 25841.102 | 17227.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 17227.404 | 17227.404
LG Store 1 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 4875 | 3750 | 4875 | 3750 | 4875 | 3750 | 5625 | 3750 | 3750 | 3750 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
LG Store 2 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 4875 | 3750 | 4875 | 3750 | 4875 | 3750 | 5625 | 3750 | 3750 | 3750 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 1 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 2 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 3 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 4 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 5 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 6 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 7 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 8 Zn SupplyFan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
DOAS Fan | 6 | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 29250 | 22500 | 33750 | 22500 | 22500 | 22500 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Terminal Units
CoreZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim1ZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim2ZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim3ZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Perim4ZnSupplyFan | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
TerminalUnit-Basement | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 42188.27 | 46023.57 | 42188.27 | 46023.57 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 42188.27 | 46023.57 | NA | NA | NA | NA | NA | NA | NA | NA
CoreBottomZn TU | 6 | Primary Air Flow (max air flow rate) | CFM | 10586.7 | 10586.7 | NA | NA | 29983.402 | 32709.168 | 29983.402 | 32709.168 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 29983.402 | 32709.168 | 10586.705 | 10586.705 | 10586.705 | 10586.705 | 10586.705 | 10586.705 | NA | NA
PerimeterBottomZn1 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2231.76 | NA | NA | 3710.974 | 4048.335 | 3710.974 | 4048.335 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3710.974 | 4048.335 | 2231.763 | 2231.763 | 2231.763 | 2231.763 | 2231.763 | 2231.763 | NA | NA
PerimeterBottomZn2 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.9 | 1412.9 | NA | NA | 2391.456 | 2608.861 | 2391.456 | 2608.861 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2391.456 | 2608.861 | 1412.902 | 1412.902 | 1412.902 | 1412.902 | 1412.902 | 1412.902 | NA | NA
PerimeterBottomZn3 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2231.76 | NA | NA | 3710.998 | 4048.362 | 3710.998 | 4048.362 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3710.998 | 4048.362 | 2231.763 | 2231.763 | 2231.763 | 2231.763 | 2231.763 | 2231.763 | NA | NA
PerimeterBottomZn4 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.8 | 1412.8 | NA | NA | 2391.439 | 2608.843 | 2391.439 | 2608.843 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2391.439 | 2608.843 | 1412.799 | 1412.799 | 1412.799 | 1412.799 | 1412.799 | 1412.799 | NA | NA
CoreMidZn TU | 6 | Primary Air Flow (max air flow rate) | CFM | 10586.7 | 12704.041 | NA | NA | 29983.402 | 32709.166 | 29983.402 | 32709.166 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 29983.402 | 32709.166 | 10586.705 | 14821.387 | NA | NA | 23820.074 | 23820.074 | NA | NA
PerimeterMidZn1 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2678.112 | NA | NA | 3710.974 | 4048.335 | 3710.974 | 4048.335 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3710.974 | 4048.335 | 2231.763 | 3124.469 | 3124.469 | 2231.763 | 3124.469 | 2231.763 | NA | NA
PerimeterMidZn2 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.9 | 1695.48 | NA | NA | 2391.456 | 2608.861 | 2391.456 | 2608.861 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2391.456 | 2608.861 | 1412.902 | 1978.063 | 1978.063 | 1412.902 | 1978.063 | 1412.902 | NA | NA
PerimeterMidZn3 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2678.112 | NA | NA | 3710.998 | 4048.362 | 3710.998 | 4048.362 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3710.998 | 4048.362 | 2231.763 | 3124.469 | 3124.469 | 2231.763 | 3124.469 | 2231.763 | NA | NA
PerimeterMidZn4 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.8 | 1695.36 | NA | NA | 2391.439 | 2608.843 | 2391.439 | 2608.843 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2391.439 | 2608.843 | 1412.799 | 1977.918 | 1977.918 | 1412.799 | 1977.918 | 1412.799 | NA | NA
CoreHiZn TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 29983.402 | 32709.166 | 29983.402 | 32709.166 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 29983.402 | 32709.166 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHiZn1 TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 3710.974 | 4048.335 | 3710.974 | 4048.335 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3710.974 | 4048.335 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHiZn2 TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 2391.456 | 2608.861 | 2391.456 | 2608.861 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2391.456 | 2608.861 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHiZn3 TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 3710.998 | 4048.362 | 3710.998 | 4048.362 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3710.998 | 4048.362 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHiZn4 TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | 2391.439 | 2608.843 | 2391.439 | 2608.843 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2391.439 | 2608.843 | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterTopZn1 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2678.112 | NA | NA | 4048.335 | 5060.419 | 4048.335 | 5060.419 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3710.974 | 4385.696 | 2454.939 | 3124.469 | 3124.469 | 2454.939 | 3124.469 | 2454.939 | NA | NA
PerimeterTopZn2 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.9 | 1695.48 | NA | NA | 2608.861 | 3261.076 | 2608.861 | 3261.076 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2391.456 | 2826.266 | 1554.193 | 1978.063 | 1978.063 | 1554.193 | 1978.063 | 1554.193 | NA | NA
PerimeterTopZn3 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2678.112 | NA | NA | 4048.362 | 5060.452 | 4048.362 | 5060.452 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3710.998 | 4385.725 | 2454.939 | 3124.469 | 3124.469 | 2454.939 | 3124.469 | 2454.939 | NA | NA
PerimeterTopZn4 TU | 6 | Primary Air Flow (max air flow rate) | CFM | 1412.8 | 1695.36 | NA | NA | 2608.843 | 3261.053 | 2608.843 | 3261.053 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2391.439 | 2826.246 | 1554.079 | 1977.918 | 1977.918 | 1554.079 | 1977.918 | 1554.079 | NA | NA
CoreTopZn TU | 6 | Primary Air Flow (max air flow rate) | CFM | 10586.7 | 12704.041 | NA | NA | 109030.555 | 109030.555 | 109030.555 | 109030.555 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 29983.402 | 35434.93 | 11645.376 | 14821.387 | 14821.387 | 11645.376 | 14821.387 | 11645.376 | NA | NA
Core Mid DOAS TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 23820 | 23820 | NA | NA | NA | NA
BackSpaceSys_TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | 6133.65 | 4089.1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 4089.12 | 4089.12
PointOfSaleSys_TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | 2434.95 | 1623.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2110.292 | 1623.302
FrontRetailSys_TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | 2434.95 | 1623.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2110.287 | 1623.298
CoreRetailSys_TU | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | 25841.102 | 17227.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 17227.404 | 17227.404
LG Store 1 Sys TU 1 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 4875 | 3750 | 4875 | 3750 | 4875 | 3750 | 5625 | 3750 | 3750 | 3750 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
LG Store 2 Sys TU 2 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 4875 | 3750 | 4875 | 3750 | 4875 | 3750 | 5625 | 3750 | 3750 | 3750 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 1 Sys TU 3 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 2 Sys TU 4 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 3 Sys TU 5 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 4 Sys TU 6 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 5 Sys TU 7 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 6 Sys TU 8 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 7 Sys TU 9 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SM Store 8 Sys TU 10 | 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 2437.5 | 1875 | 2437.5 | 1875 | 2437.5 | 1875 | 2812.5 | 1875 | 1875 | 1875 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA