## All Tests-ORIGINAL (hidden)
|  | Run01 |  |  | Run02 |  |  | Run03 |  |  | Run04 |  |  | Run05 | [11 empty] | Run0X - NOT IN ACM | [11 empty] | Run06 | [19 empty] | Run07 |  |  | Run08 |  |  | Run9 |  |  | Run10 | [9 empty] | Run11 | [13 empty] | Run12 |  |  | Run13 |  |  | Run14 |  |  | Run15 |  |  | Run16 |  |  | Run17 |  |  | Run18 |  |  | Run19 - VAV reheat system with CRAC Unit | [7 empty] | Run20 - Large Office Building with CRAH | [7 empty] | Run21 - Warehouse with Heating and Vent Only |  |  |  | Run22 - Hotel with FPFC |  |  |  | Run23 - Medium Office with Window Alteration
|  | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model |  |  |  | Proposed Model |  |  |  | Baseline model |  |  |  | User Model |  |  |  | Proposed Model |  |  |  | Baseline model |  |  |  | User Model |  |  |  | Proposed Model |  |  |  | Baseline Model | [11 empty] | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | [6 empty] | Proposed Model | [6 empty] | Baseline Model | [6 empty] | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model |  | Proposed Model |  | Baseline model |  |  |  | User Model |  | Proposed Model |  | Baseline model |  |  |  | User Model | Proposed Model | Baseline model |  | User Model | Proposed Model | Baseline model |  | User Model | Proposed Model | Baseline model
Building Type |  | Small Office |  |  | Small Office |  | Small Office | Small Hotel |  | Small Hotel | Medium Office |  | Medium Office | Large Office | [11 empty] | Large Office | [11 empty] | Large Office | [19 empty] | Warehouse |  |  | Warehouse | Warehouse | Warehouse | Warehouse | Warehouse | Warehouse | Medium Office | Medium Office | Medium Office | Large Office | [20 empty] | Medium Office |  |  | Medium Office | Medium Office | Medium Office | Small Office | Small Office | Small Office | Warehouse | Warehouse | Warehouse | Retail | Retail | Retail | Large Office | Large Office | Large Office | Small Office | Small Office | Small Office | Medium Office, North-facing zone on second floor is a Computer Room | [7 empty] | Large Office (Core Zones on bottom two floors are a data center) | [7 empty] | Warehouse |  |  |  | Hotel |  |  |  | Medium Office
Climate Zone |  | CZ-6 |  |  | CZ-15 |  | CZ-15 | CZ-15 |  | CZ-15 | CZ-6 |  | CZ-6 | CZ-6 | [11 empty] | CZ-6 | [11 empty] | CZ-6 | [19 empty] | CZ-6 |  |  | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | [20 empty] | CZ-6 |  |  | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | [7 empty] | CZ-6 | [7 empty] | CZ-6 |  |  |  | CZ-12 |  |  |  | CZ-6
Envelope Components
| Roof Construction Assembly Type | Wood-Framed and Other Roof | Wood-Framed and Other Roof | Metal Building | Metal Building | Metal Building | Metal Building | Metal Building | Metal Building | Metal Building | Metal Building | None | None | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case | [11 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | [6 empty] | Not part of Test Case | [6 empty] | Not part of Test Case | [6 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case |  | Not part of Test Case |  |  |  | Not part of Test Case |  | Not part of Test Case |  | Not part of Test Case |  |  |  | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Metal Building Roof | Metal Building Roof | Metal Building Roof
| Roof Construction Assembly overall U value | 0.051 | 0.051 | 0.075 | 0.061 | 0.061 | 0.039 | 0.055 | 0.055 | 0.065 | 0.085 | None | None | [122 empty] | 0.065 | 0.065 | 0.082
| Roof Construction Assembly layers | 1.Asphalt roll roofing - 1/4 in. (R-0.15) 2.Hardboard - HDF - 50 lb/ft3 - 3/4 in. (R-1.03) 3. Polyisocyanurate - aged - unfaced - 3 in. (R-18.18) | 1.Asphalt roll roofing - 1/4 in. (R-0.15) 2.Hardboard - HDF - 50 lb/ft3 - 3/4 in. (R-1.03) 3. Polyisocyanurate - aged - unfaced - 2 in. (R-18.18) | 1.Metal Standing Seam - 1/16 in. R - 0.00 2. Expanded Polystyrene - EPS - 1 1/2 in. R - 6.25 3. Expanded Polystyrene - EPS - 1 1/2 in. R - 6.25 4. Metal Framing R - 0.00 | 1. Roof Gravel - 1/2 in. R - 0.10 2. Expanded Polystyrene - EPS - 3 1/2 in. R - 14.58 3. Plywood (1/2 in.) R - 0.63 4. Metal Deck R - 0.00 5. Metal Framing R - 0.00 6. Air Layer (4 in. or more) R - 0.92 | 1. Roof Gravel - 1/2 in. R - 0.10 2. Expanded Polystyrene - EPS - 3 1/2 in. R - 14.58 3. Plywood (1/2 in.) R - 0.63 4. Metal Deck R - 0.00 5. Metal Framing R - 0.00 6. Air Layer (4 in. or more) R - 0.92 | 1.Metal Standing Seam - 1/16 in. R - 0.00 2. Expanded Polystyrene - EPS - 5 19/20 in. R - 24.79 3. Metal Framing R - 0.00 | 1.Metal Roofing (R-0) 2.Insulation entirely above deck (R-15.75) 3. Plywood (1/2 in.) - R-0.63 4. Metal Deck - R-0 5. Air Layer (4 in. or more) - R-0.92 | 1.Metal Roofing (R-0) 2.Insulation entirely above deck (R-15.75) 3. Plywood (1/2 in.) - R-0.63 4. Metal Deck - R-0 5. Air Layer (4 in. or more) - R-0.92 | 1.Metal Standing Seam - 1/16 in. R - 0.00 2. Expanded Polystyrene - EPS - 3 1/2 in. R - 14.58 3. Metal Framing R - 0.00 | 1.Metal Roofing (R-0) 2.Expanded Polystyrene - EPS - 2 2/5 in. (R-10.0) 3. Plywood (1/2 in.) - R-0.63 4. Metal Deck - R-0 5. Air Layer (4 in. or more) - R-0.92 | None | None | [122 empty] | Metal Deck - R-0.0 Expanded Polystyrene - EPS - 3 1/2 in. (R-14.58) | Metal Deck - R-0.0 Expanded Polystyrene - EPS - 3 1/2 in. (R-14.58) | Metal Deck - R-0.0 Expanded Polystyrene - EPS - 2 3/4in.. (R-11.44)
| Roof Aged Solar Reflectance | 0.75 | 0.75 | 0.63 | 0.6 | 0.6 | 0.2 | 0.6 | 0.6 | 0.55 | 0.6 | None | None | [122 empty] | 0.1 | 0.1 | 0.1
| Roof Thermal emittance | 0.78 | 0.78 | 0.85 | 0.7 | 0.7 | 0.85 | 0.7 | 0.7 | 0.85 | 0.7 | None | None | [122 empty] | 0.8 | 0.8 | 0.8
| Exterior Wall Construction Assembly Type | Wood-Framed | Wood-Framed | Metal-Framed | Metal-Framed | Metal-Framed | Metal-Framed | Metal- Framed | Metal- Framed | Metal-Framed | Metal- Framed | None | None | [122 empty] | Wood-Framed Wall | Wood-Framed Wall | Wood-Framed Wall
| Exterior Wall Construction Assembly overall U value | 0.095 | 0.095 | 0.098 | 0.056 | 0.056 | 0.062 | 0.082 | 0.082 | 0.105 | 0.137 | None | None | [122 empty] | 0.11 | 0.11 | 0.11
| Exterior Wall Construction Assembly layers | 1. Stucco 7/8" (R-0.18) 2. Building Paper - 1/16 in. (R-0.06) 3. Insulation/Framing Layer (R-15, 2x4) 4. Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" (R-0.18) 2. Building Paper - 1/16 in. (R-0.06) 3. Insulation/Framing Layer (R-15, 2x4) 4.Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" (R-0.18) 2. Building Paper - 1/16 in. (R-0.06) 3. Expanded Polystyrene - EPS - 1 7/8 in. (R-8) 4. Metal Wall Framing - 16 or 24 in. OC (R-0.65) 5. Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" (R-0.18) 2. Building Paper (R-0.06) 3. Continuous Insulation (R-) 4. Metal Wall Framing - 16 or 24 in. OC (R-0.65) 5.Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Continuous Insulation (R-) 4. Metal Wall Framing, 16 or 24 in. OC (R-0.65) 5. Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Expanded Polystyrene - EPS - 3 1/3 in. (R-14) 4. Metal Wall Framing - 16 or 24 in. OC (R-0.65) 5.Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Expanded Polystyrene - EPS - 2 2/5 in. (R-10) 4. Metal Wall Framing - 16 or 24 in. OC (R-0.65) 5. Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Expanded Polystyrene - EPS - 2 2/5 in. (R-10) 4. Metal Wall Framing - 16 or 24 in. OC (R-0.65) 5. Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Expanded Polystyrene - EPS - 1 3/4 in. (R-7.29) 4. Metal Wall Framing - 16 or 24 in. OC (R-0.65) 5.Gypsum Board - 1/2 in. (R-0.45) | 1. Stucco 7/8" 2. Building Paper (R-0.06) 3. Continuous Insulation (R-5) 4. Metal Wall Framing - 16 or 24 in. OC (R-0.65) 5. 1/2" Gypsum Board (R-0.45) | None | None | [122 empty] | Wood-Framed Wall with R-11 | Wood-Framed Wall with R-11 | Wood-Framed Wall with R-11
| Above-grade Floor Construction Assembly Type | Concrete Raised Floor | Concrete Raised Floor | Steel Joist Floor | Slab -on grade | Slab -on grade | Slab-on-grade | Mass Floor | Mass Floor | Steel Joist Floor | Mass Floor | None | None | [122 empty] | n/a | n/a | n/a
| Above-grade Floor Construction Assembly overall U value | 0.052 | 0.052 | 0.071 | NA | NA | NA | 0.052 | 0.052 | 0.071 | 0.052 | None | None | [122 empty] | n/a | n/a | n/a
| Floor F-factor, Area and Perimeter exposed | NA | NA | NA | 0.70, 17869.56 ft2, 1567.125 ft | 0.70, 17869.56 ft2, 1567.125 ft | 0.73, 17869.56 ft2, 1567.125 ft | NA | NA | NA | NA | None | None | [122 empty] | 0.73 | 0.73 | 0.73
| Above-grade Floor Construction Assembly layers | 1. Polyisocyanurate - aged - facers - 1 1/2 in. (R-15) 2. Concrete - 80 lb/ft3 - 4 in. (R-1.09) 3. Metal Deck (R-0) 4. OSB - Oriented Strand Board - 5/8 in. (R-0.82) 5. Carpet and pad - 3/4 in. (R-1.30) | 1. Polyisocyanurate - aged - facers - 1 1/2 in. (R-15) 2. Concrete - 80 lb/ft3 - 4 in. (R-1.09) 3. Metal Deck (R-0) 4. OSB - Oriented Strand Board - 5/8 in. (R-0.82) 5. Carpet and pad - 3/4 in. (R-1.30) | 1. Expanded Polystyrene - EPS - 5 2/5 in. (R-21.69) 2. Plywood - 5/8 in. (R-0.78) 3. Carpet and pad - 3/4 in. (R-1.30) | NA | NA | NA | 1.Polyisocyanurate - aged - facers - 1 1/2 in. (R-15) 2. Concrete - 80 lb/ft3 - 4 in. (R-1.09) 3. Metal Deck (R-0) 4. OSB - Oriented Strand Board - 5/8 in. (R-0.82) 5. Carpet and pad - 3/4 in. (R-1.30) | 1. Polyisocyanurate - aged - facers - 1 1/2 in. (R-15) 2. Concrete - 80 lb/ft3 - 4 in. (R-1.09) 3. Metal Deck (R-0) 4. OSB - Oriented Strand Board - 5/8 in. (R-0.82) 5. Carpet and pad - 3/4 in. (R-1.30) | 1. Expanded Polystyrene - EPS - 5 2/5 in. (R-21.69) 2. Plywood - 5/8 in. (R-0.78) 3. Carpet with pad (R-1.34) | 1. Polyisocyanurate - aged - facers - 1 1/2 in. (R-15) 2. Concrete - 80 lb/ft3 - 4 in. (R-1.09) 3. Metal Deck (R-0) 4. 5/8" Wood Sheathing (R-0.65) 5. Carpet and pad - 3/4 in. (R-1.30) | None | None | [122 empty] | n/a | n/a | n/a
| Window Type | Fixed | Fixed | [8 empty] | None | None | [122 empty] | fixed | fixed | fixed
| Window assembly U value | 0.25 | 0.25 | 0.36 | Not part of Test Case | Not part of Test Case | Not part of Test Case | Fixed-0.26, Operable-0.42 | Fixed-0.26, Operable-0.42 | Fixed-0.36, Operable-0.46 | Fixed-0.26, Operable-0.42 | None | None | [122 empty] | South-0.4 (new); N,E,W-0.55 (existing) | South-0.4 (new); N,E,W-0.55 (existing) | South-0.47 (new); N,E,W-0.55 (existing)
| Window SHGC | 0.2 | 0.2 | 0.25 |  |  |  | Fixed-0.20, Operable-0.18 | Fixed-0.20, Operable-0.18 | Fixed-0.25, operable-0.22 | Fixed-0.20, Operable-0.18 | None | None | [122 empty] | South-0.33 (new); N,E,W-0.56 (existing) | South-0.33 (new); N,E,W-0.56 (existing) | South-0.31 (new); N,E,W-0.56 (existing)
| Window VT | 0.45 | 0.45 | 0.42 |  |  |  | Fixed-0.47, Operable-0.35 | Fixed-0.47, Operable-0.35 | Fixed-0.42, Operable-0.32 | Fixed-0.47, Operable-0.35 | None | None | [122 empty] | South-0.5 (new); N,E,W-0.6 (existing) | South-0.5 (new); N,E,W-0.6 (existing) | South-0.42 (new); N,E,W-0.6 (existing)
| Window-Wall Ratio | Not part of Test Case | Not part of Test Case | Not part of Test Case |  |  |  | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | None | None | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | Orientation | Wall Area [ft2] | Window Area [ft2] | WWR [%] | [78 empty] | 45% | 45% | 45%
[14 empty] | Total | 124748.7703 | 64961.5987 | 52.07 | Total | 124748.7703 | 64961.5987 | 52.07 | Total | 124748.7703 | 49903.1033 | 40 | Total | 124748.7703 | 37424.6311 | 30 | Total | 124748.7703 | 37424.6311 | 30 | Total | 124748.7703 | 36177.8527 | 29.0006 | Total | 124748.7703 | 57384.4354 | 46 | Total | 124748.7703 | 57384.4354 | 46 | Total | 124748.7703 | #REF! | #REF! | Total | 124748.7703 | #REF! | #REF! | Total | 124748.7703 | 49935.0239 | 40.0285 | [78 empty] | North-50% | North-50% | North-50%
[14 empty] | North | 37424.6096 | 19488.4904 | 52.07 | North | 37424.6096 | 19488.4904 | 52.07 | North | 37424.6096 | 14970.9848 | 40 | North | 37424.6096 | 9822.7342 | 26.2467 | North | 37424.6096 | 9822.7342 | 26.2467 | North | 37424.6096 | 9822.7342 | 26.2467 | North | 37424.6096 | 18712.3048 | 50 | North | 37424.6096 | 18712.3048 | 50 | North | 37424.6096 | #REF! | #REF! | North | 37424.6096 | #REF! | #REF! | North | 37424.6096 | 16647.958 | 44.484 | [78 empty] | South-50% | South-50% | South-50%
[14 empty] | East | 24949.7756 | 12992.3628 | 52.07 | East | 24949.7756 | 12992.3628 | 52.07 | East | 24949.7756 | 9980.6207 | 40 | East | 24949.7756 | 6551.7637 | 26.2598 | East | 24949.7756 | 6551.7637 | 26.2598 | East | 24949.7756 | 6551.7637 | 26.2598 | East | 24949.7756 | 11227.399 | 45 | East | 24949.7756 | 11227.399 | 45 | East | 24949.7756 | #REF! | #REF! | East | 24949.7756 | #REF! | #REF! | East | 24949.7756 | 9988.7892 | 40.0356 | [78 empty] | East-40% | East-40% | East-40%
[14 empty] | South | 37424.6096 | 19488.4904 | 52.07 | South | 37424.6096 | 19488.4904 | 52.07 | South | 37424.6096 | 14970.9848 | 40 | South | 37424.6096 | 9822.7342 | 26.2467 | South | 37424.6096 | 9822.7342 | 26.2467 | South | 37424.6096 | 9822.7342 | 26.2467 | South | 37424.6096 | 14969.8438 | 40 | South | 37424.6096 | 14969.8438 | 40 | South | 37424.6096 | #REF! | #REF! | South | 37424.6096 | #REF! | #REF! | South | 37424.6096 | 13318.3664 | 35.5872 | [78 empty] | West-40% | West-40% | West-40%
[14 empty] | West | 24949.7756 | 12992.3628 | 52.07 | West | 24949.7756 | 12992.3628 | 52.07 | West | 24949.7756 | 9980.6207 | 40 | West | 24949.7756 | 11227.399 | 45 | West | 24949.7756 | 11227.399 | 45 | West | 24949.7756 | 9980.6207 | 40 | West | 24949.7756 | 12474.8878 | 50 | West | 24949.7756 | 12474.8878 | 50 | West | 24949.7756 | 9979.9102 | 40 | West | 24949.7756 | 9979.9102 | 40 | West | 24949.7756 | 9979.9102 | 40
| Window overhang |  |  |  | South Windows- 2 feet Horizontal overhang West Windows- 2 feet Vertical overhang | South Windows- 2 feet Horizontal overhang West Windows- 2 feet Vertical overhang | None | [6 empty] | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case | [81 empty] | None | None | None
| Skylight overall U value | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | 0.55 | 0.55 | 0.58 | [6 empty] | NA | NA | NA | NA | [6 empty] | NA | [6 empty] | NA | [6 empty] | NA | NA | NA | NA | NA | NA | NA | NA | NA | [9 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | NA |  | NA |  | NA |  |  |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Skylight SHGC | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | 0.2 | 0.2 | 0.25 | [6 empty] | NA | NA | NA | NA | [6 empty] | NA | [6 empty] | NA | [6 empty] | NA | NA | NA | NA | NA | NA | NA | NA | NA | [9 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | NA |  | NA |  | NA |  |  |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Skylight VT | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | 0.4 | 0.4 | 0.49 | [6 empty] | NA | NA | NA | NA | [6 empty] | NA | [6 empty] | NA | [6 empty] | NA | NA | NA | NA | NA | NA | NA | NA | NA | [9 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | NA |  | NA |  | NA |  |  |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Skylight to Roof Ratio | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | NA |  |  |  | 7% | 7% | 5% | 15% | 15% | Calculated by software to prevent overlapping daylit areas from skylights; final number should be 2.5% to 5% SRR. | 5% | 5% | Calculated by software to prevent overlapping daylit areas from skylights; final number should be 2.5% to 5% SRR. | NA | NA | NA | NA | [6 empty] | NA | [6 empty] | NA | [6 empty] | NA | NA | NA | NA | NA | NA | NA | NA | NA | [9 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | NA |  | NA |  | NA |  |  |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Daylit Area (calculated value) | [59 empty] | 80% | 80% | 75% | 55% | 55% | 75%
Internal Load Components
| Occupancy Type | [65 empty] | Office (250 square feet in floor area or less) | Office (250 square feet in floor area or less) | Office (250 square feet in floor area or less) | Retail Merchandise Sales, Wholesale Showroom | Medical and Clinical Care | Office (Greater than 250 square feet in floor area) | Convention, Conference, Multipurpose and Meeting Center Areas | Corridors, Restrooms, Stairs, and Support Areas | Corridors, Restrooms, Stairs, and Support Areas | Lobby, Main Entry | Retail Merchandise Sales, Wholesale Showroom | Medical and Clinical Care | Office (Greater than 250 square feet in floor area) | Convention, Conference, Multipurpose and Meeting Center Areas | Corridors, Restrooms, Stairs, and Support Areas | Corridors, Restrooms, Stairs, and Support Areas | Lobby, Main Entry | Retail Merchandise Sales, Wholesale Showroom | Medical and Clinical Care | Office (Greater than 250 square feet in floor area) | Convention, Conference, Multipurpose and Meeting Center Areas | Corridors, Restrooms, Stairs, and Support Areas | Corridors, Restrooms, Stairs, and Support Areas | Lobby, Main Entry | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | [6 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case |  | Not part of Test Case |  |  |  | Not part of Test Case |  | Not part of Test Case |  | Not part of Test Case |  |  |  | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case | Not part of Test Case | Not part of Test Case
| People Density | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | 50 ft2/person | 100 ft2/person | 100 ft2/person | 33 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 67 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 33 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 67 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 33 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 67 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2 | 10 people/1000ft2
| Sensible Heat/person | [65 empty] | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 245 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 245 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 245 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant
| Latent Heat/person | [65 empty] | 206 Btu/occupant | 206 Btu/occupant | 206 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 155 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 155 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 155 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant
| Equipment Power Density | [65 empty] | 3 W/ft2 | 1.34 W/ft2 | 1.34 W/ft2 | 2 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | 1 W/ft2 | 0.2 W/ft2 | 0.2 W/ft2 | 0.5 W/ft2 | 1 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | 1 W/ft2 | 0.2 W/ft2 | 0.2 W/ft2 | 0.5 W/ft2 | 1 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | 1 W/ft2 | 0.2 W/ft2 | 0.2 W/ft2 | 0.5 W/ft2 | [21 empty] | Office: 0.9 W/ft2 | Computer Room: 25 W/ft2 | Office:1.34 W/ft2 | Computer Room: 25 W/ft2 | Office: 1.34 W/ft2 | Computer Room: | 25 W/ft2
| Lighting Power Density | [65 empty] | 1.2 W/ft2 | 1.2 W/ft2 | 1 W/ft2 | 1W/ft2 | 1 W/ft2 | 0.75 W/ft2 | 1.2 W/ft2 | 0.5 W/ft2 | 0.5 W/ft2 | 1.5 W/ft2 | 1W/ft2 | 1 W/ft2 | 0.75 W/ft2 | 1.2 W/ft2 | 0.5 W/ft2 | 0.5 W/ft2 | 1.5 W/ft2 | 1.2 W/ft2 | 1.2 W/ft2 | 0.75 W/ft2 | 1.4 W/ft2 | 0.6 W/ft2 | 0.6 W/ft2 | 1.5 W/ft2 | Main Entry (Gen. Lighting)- 0.5 W/ft2 Waiting Area (Gen. Lighting)- 0.75 W/ft2 Waiting Area (Décor. Lighting)- 0.2 W/ft2 | Main Entry (Gen. Lighting)- 0.5 W/ft2 Waiting Area (Gen. Lighting)- 0.75 W/ft2 Waiting Area (Décor. Lighting)- 0.2 W/ft2 | Main Entry (Gen. Lighting)- 0.6 W/ft2 Waiting Area (Gen. Lighting)- 0.8 W/ft2 Waiting Area (Décor. Lighting)- 0.2 W/ft2 | Main Entry (Gen. Lighting)- 0.8 W/ft2 Main Entry (Task Lighting)- 0.1 W/ft2 Waiting Area (Gen. Lighting)- 0.6 W/ft2 Waiting Area (Décor. Lighting)- 1.2 W/ft2 Waiting Area (Floor Display Lighting) - 0.1 W/ft2 | Main Entry (Gen. Lighting)- 0.8 W/ft2 Main Entry (Task Lighting)- 0.1 W/ft2 Waiting Area (Gen. Lighting)- 0.6 W/ft2 Waiting Area (Décor. Lighting)- 1.2 W/ft2 Waiting Area (Floor Display Lighting) - 0.1 W/ft2 | Main Entry (Gen. Lighting)- 0.8 W/ft2 Main Entry (Task Lighting)- 0.1 W/ft2 Waiting Area (Gen. Lighting)- 0.6 W/ft2 Waiting Area (Décor. Lighting)- 0.5 W/ft2 Waiting Area (Floor Display Lighting) - 0.1 W/ft2 | 0.9 W/ft2 * (1-0.05) | 0.9 W/ft2 * (1-0.05) | 0.9 W/ft2 |  |  |  | Front Retail (General) - 1.6 W/ft2 Front Retail (task and floor display) - 0.75 W/ft2 Task and floor display area - 50% of space area closest to window | Front Retail (General) - 1.6 W/ft2 Front Retail (task and floor display) - 0.75 W/ft2 Task and floor display area - 50% of space area closest to window | Front Retail (General) - 1.5 W/ft2 Front Retail (task and floor display) - 0.75 W/ft2 Task and floor display area - 50% of space area closest to window
| Ventilation Rate | [65 empty] | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.75 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 1 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.75 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 1 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.495 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.5 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case
| Hot-water Load | [65 empty] | 106 Btu/person | 106 Btu/person | 106 Btu/person | 120 Btuh/person | 160 Btuh/person | 120 Btuh/person | 60 Btuh/person | 0 | 0 | NA | 120 Btuh/person | 160 Btuh/person | 120 Btuh/person | 60 Btuh/person | 0 | 0 | NA | 120 Btuh/person | 160 Btuh/person | 120 Btuh/person | 60 Btuh/person | 0 | 0 | 60 Btuh/person
Infiltration rate (Work in Progress)
| Elevator Power | [65 empty] | 32 kW | 32 kW | 32kW | NA | NA | NA | NA | NA | NA | 244 kW | NA | NA | NA | NA | NA | NA | 244 kW | NA | NA | NA | NA | NA | NA | not tested
| Occupancy Schedule | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly
| Equipment Schedule | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly
| Lighting Schedule | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | [6 empty] | Office | Office | Office
| Hot Water Schedule | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case
| Infiltration(Work in Progress) | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly
| Elevator | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | [18 empty] | NA | NA | NA | [16 empty] | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Daylighting | [101 empty] | Check Only for
| Illuminance Setpoint | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case | [29 empty] | Not part of Test Case | [15 empty] | Office - 400 lux | Office - 400 lux | Office - 400 lux (Ref. P 1, 1600 lux (Ref. P-2) | 950 lux | 950 lux | 950 lux in Primary Daylit Zone 3800 lux in Secondary Daylit Zone
| Daylight Control Type in Primary Daylit Area | [59 empty] | Not part of Test Case | [38 empty] | Continuous Dimming | Continuous Dimming | Continuous Dimming | Continuous Dimming | Continuous Dimming | Continuous Dimming | [30 empty] | None | None | None
| Daylight Control Type in Skylit Area | [98 empty] | Continuous + Off | Continuous + Off | Continuous Dimming | Continuous + Off | Continuous + Off | Continuous Dimming | [30 empty] | NA | NA | NA
| Daylight Control Type in Secondary Daylit Area | [98 empty] | None | None | Continuous Dimming | Continuous Dimming | Continuous Dimming | Continuous Dimming | [30 empty] | None | None | None
| Controlled General Lighting Power In Primary Daylit Area | [98 empty] | 550 W | 550 W | 437 W (Primary Daylit Area= 582.4 sft) | 500 W | 500 W | Point of Sale: General Lighting LPD x 717 ft2 | [30 empty] | None | None | None
| Controlled General Lighting Power In Secondary Daylit Area | [98 empty] | 300 W | 300 W | 350 W (Secondary Daylit Area= 465.34 sft) | 600 W | 600 W | Point of Sale: General Lighting LPD x 717 ft2 | [30 empty] | None | None | None
| Controlled General Lighting Power In Skylit Daylit Area | [98 empty] | NA | NA | NA | 1500 W | 1500 W | Core Retail: General Lighting LPD x 1024ft2 | [30 empty] | None | None | None
| Reference Position 1 | [98 empty] | Office - 5 ft from exterior wall; midpoint of space | Office - 5 ft from exterior wall; midpoint of space; | Office - 8 ft from exterior wall; midpoint of corner window on west façade | Point of Sale: 5 feet from S window and 10 feet from east window Core Retail: Primary-Under Skylight, at edge of skylight | Point of Sale: Primary-at edge of PDZ, at midpoint of zone Core Retail: Primary-Under Skylight | Point of Sale: Primary-at interior edge of PDZ, at midpoint of zone Core Retail: Primary-Under Skylight | [30 empty] | n/a | n/a | n/a
| Reference Position 2 | [98 empty] | None | None | Office - 16 ft from exterior wall; midpoint of corner window on west façade | Point of Sale: 12 feet from S window and 10 feet from east window Core Retail: none | Point of Sale: 12 feet from S window and 10 feet from east window Core Retail: none | Point of Sale: Primary-at interior edge of SDZ, at midpoint of zone Core Retail: none | [30 empty] | n/a | n/a | n/a
HVAC Components | [135 empty] | All HVAC inputs have baseline same as proposed.
| HVAC System Type | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case | [24 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | [6 empty] | Not part of Test Case | [6 empty] | Not part of Test Case | [6 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | PSZ HP | PSZ HP | PSZ AC (System 3) | PVAV with Reheat | PSZ | PVAV with Reheat | PSZ | PVAV with Reheat (System 5) |  | CRAC Unit |  | Built-up VAV with Reheat | Packaged Single Zone | Built-up VAV with Reheat | Packaged Single Zone | VAV with Reheat (System 6) |  | CRAH Unit (System 10) |  | PSZ, no cooling | PSZ, no cooling | Heating Ventilation (System 9) |  | FPFC | FPFC | FPFC |  | PSZ | PSZ | PSZ
| Heating Type | [107 empty] | Heat Pump | Heat Pump | Gas Furnace | Hot Water boiler with reheat | Packaged Single Zone | Hot Water boiler with reheat | Packaged Single Zone | Hot Water boiler with reheat |  | Packaged Single Zone |  | Fossil Fuel | None | Fossil Fuel | None | Hot Water boiler with reheat |  | None |  | Electric Heat pump | Electric Heat pump | Gas Furnace |  | Hot Water | Hot Water | Hot Water |  | Gas Furnace | Gas Furnace | Gas Furnace
| Cooling Type | [107 empty] | DX | DX | Direct Expansion (DX) | DX | DX | DX | DX | DX |  | DX |  | Chilled Water | DX | Chilled Water | Chilled Water | Chilled Water |  | Chilled Water |  | NA | NA | NA |  | Chilled water | Chilled water | Chilled water |  | DX | DX | DX
| Cooling Efficiency | [107 empty] | EER-11.5 | EER-11.5 | Input Based on Proposed System Size- | COP=4 | COP=3.8 | Based on System Capacity and Type, Table 110.2-D | COP=3.8 | Input Based on Proposed System Size- | Final input based on sizing Run- | Input Based on 50% of Proposed System Size- | Final input based on sizing Run- | COP-6.2 | EER-11, SEER-14 | COP-6.2 | EER-11, SEER-14 | Input Based on Proposed System Size- | Final input based on sizing Run- | Input Based on 50% of Proposed System Size- | Final input based on sizing Run- | NA | NA | NA |  | Chiler COP=5.8 | Chiller COP=5.8 | Chiller COP according to system size and Table 110.2-D |  | COP=2.8 | COP=2.8 | COP=2.8
| Heating Efficiency | [107 empty] | COP-3.6 | COP-3.6 | Input Based on Proposed System Size- | 85% | n/a | Based on System Capacity and 110.2 | n/a | Input Based on Proposed System Size- | Final input based on sizing Run- | None | None | 85% | 80% | 85% | 80% | Input Based on Proposed System Size- | Final input based on sizing Run- | n/a | Final input based on sizing Run- | 84% | 84% | Input Based on Proposed System Size- | Final input based on sizing Run- | 90% | 90% | Input Based on Proposed System Size- | Final input based on sizing Run- | 80% | 80% | 80%
| System Oversizing Factor | [107 empty] | Heating- 1.25 Cooling- 1.15 | Heating- 1.25 Cooling- 1.15 | Heating- 1.25 Cooling- 1.15 | n/a | Heating-n/a Cooling- 1.15 | Heating- 1.25 Cooling- 1.15 | Heating-n/a Cooling- 1.15 |  |  |  |  | Heating- 1.25 Cooling- 1.15 | Heating- 1.25 Cooling- 1.15 | Heating- 1.25 Cooling- 1.15 | Heating- 1.25 Cooling- 1.15 | Heating- 1.25 Cooling- 1.15 |  | Heating- 1.25 Cooling- 1.15 | [5 empty] | Heating- 1.25 | Heating- 1.25 | Heating- 1.25 |  | n/a | n/a | n/a
| System Capacity | [107 empty] | Heating Capacity- Cooling Capacity- | Heating Capacity- Cooling Capacity- | Heating Capacity Cooling Capacity | Heating Capacity- Cooling Capacity- | Heating Capacity- Cooling Capacity-110,000 Btuh | Heating Capacity- Cooling Capacity- | Heating Capacity- Cooling Capacity-110,000 Btuh | Heating- 1.25 Cooling- 1.15 |  | Cooling- 1.15 |  | Heating Capacity- Cooling Capacity- | Cooling Capacity- 650,000 Btuh | Heating Capacity- Cooling Capacity- | Cooling Capacity- 650,000 Btuh | Heating- 1.25 Cooling- 1.15 |  | Cooling- 1.15 |  | n/a | n/a | Heating- 1.25 |  | User=250 tons | 250 tons, except if there are excessive UMLH, then prompt user to resize | Based on system capacity and Table 110.-2D |  | Not part of Test Case |  | Same as proposed
| Supply Air Temperature | [107 empty] | Heating - 105F Cooling - 55F | Heating - 105F Cooling - 55F | Heating- 105F Cooling- 55F | Heating-70F Cooling - 55F | Cooling - 55F | Heating-70F Cooling - 55F | Cooling - 55F | Heating- 70F Cooling- 55F |  | Heating- None Cooling- 60F |  | Heating- 70F Cooling- 55F | Heating- none Cooling- 55F | Heating- 70F Cooling- 55F | Heating- none Cooling- 55F | Heating- 70F Cooling- 55F |  | Cooling- 60F |  | Heating- 100F Cooling- NA | Heating- 100F Cooling- NA | Heating- 100F Cooling- NA |  | Heating - NA Cooling - NA | Heating - NA Cooling - NA | Heating - NA Cooling - NA |  | Heating - 105 Cooling - 55 | Heating - 105 Cooling - 55 | Heating - 105 Cooling - 55
| SAT Reset Control | [107 empty] | Fixed | Fixed | Heating- Fixed, Cooling- Fixed | Heating- Fixed, Cooling- Reset by Demand | Heating- n/a, Cooling- Reset by OA | Heating- Fixed, Cooling- Reset by Demand | Heating- n/a, Cooling- Reset by Demand | Heating- Fixed Cooling- Reset by outside dry-bulb temperature. |  | Heating- n/a Cooling- Reset by demand, airflow-first sequence. |  | Heating- Cooling- |  | Heating- Cooling- |  | Heating- Fixed Cooling- Reset by demand. |  | Heating- none Cooling- Reset by "Airflow First" reset sequence - reset airflow to min, then reset SAT |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Economizer | [107 empty] | None | None | Yes - integrated if load over 54 kBtu/h; partially integrated if over 45 kBtu/h | Yes - Integrated | Yes - Integrated | Yes - Integrated | Yes - Integrated |  | Final input based on sizing Run- |  | Yes - Integrated | integrated | none | integrated | none | integrated | Final input based on sizing Run- | integrated if load>5 ton; none if not | Final input based on sizing Run- | None | None | None |  | Water-side economizer: eff=60%, non-integrated | Water-side economizer: eff=60%, non-integrated | None |  | None | None | None
| Economizer Limits | [107 empty] | NA | NA | Differential dry-bulb | Fixed Dry-Bulb | Differential Dry-bulb | Differential Dry-Bulb | Differential Dry-Bulb |  | Final input based on sizing Run- |  | Differential Dry-Bulb | 70F high limit | none | 70F high limit | none |  | Final input based on sizing Run- |  | Final input based on sizing Run- | None | None | None |  | 50F | 50F | n/a |  | Fixed Dry-bulb 70F | Fixed Dry-bulb 70F | Fixed Dry-bulb 70F
| Fan Brake Horsepower | [107 empty] | NA | NA | Fan Power - 0.365W/cfm | 11 bhp | 0.60 W/cfm | 11 bhp (since 11> 0.95% of 10) | 0.60 W/cfm | Static Pressure=f(cfm,#stories) | Final input based on sizing Run- | Static Pressure=f(cfm,#stories) | 0.49 W/cfm | 16 | 5 | 16 | 5 | Static pressure = f(cfm, # stories) | Final input based on sizing Run- | 0.49 W/cfm | Final input based on sizing Run- | 6 bhp | Use Max (6, 95% of next smaller motor size) = 7.125 | None | Final input based on sizing Run- | fan coil= 0.25 W/cfm | fan coil= 0.25 W/cfm | 0.35 W/cfm | Final input based on sizing Run- | n/a | n/a | n/a | Final input based on sizing Run-
| Motor Horsepower | [107 empty] | NA | NA | NA | 15 |  | n/a |  | n/a |  | n/a |  | 20 | 10 | 20 | 10 |  |  | N/A | N/A | 10 MHP | n/a
| Fan Control Method | [107 empty] | Constant Volume | Constant Volume | Constant Volume | Variable flow, VSD | Constant Volume | Variable flow, VSD | Constant Volume | Variable flow, VSD |  | Constant-speed if load<= 5tons; variable-speed if > 5tons |  | Variable-flow, VSD | Variable-flow, VSD | Variable-flow, VSD | Variable-flow, VSD | Variable-flow, variable speed drive |  | Variable-flow, variable speed drive |  | Constant Volume | Constant Volume | Constant Volume |  | Constant Volume | Constant Volume | Constant Volume |  | Constant Volume | Constant Volume | Constant Volume
| DX Cooling Efficiency Adjustment Curve | [107 empty] | Default | Default | Default | Default | Default | Default | Default | Default |  | Default |  | NA | NA | NA | NA | NA |  | NA |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Cooling Capacity Adjustment Curve | [107 empty] | Default | Default | Default | Default | Default | Default | Default | Default |  | Default |  | NA | NA | NA | NA | NA |  | NA |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Heating (Furnace) Part-load Efficiency Curve | [107 empty] | Fixed | Fixed | Fixed | NA |  | NA |  | NA |  | NA |  | NA | NA | NA | NA | NA |  | NA |  | NA | NA | Default |  | NA | NA | Default |  | NA | NA | Default
| Electric Heat Pump Heating Capacity Adjustment Curve | [107 empty] | NA | NA | NA | NA | Default | NA | Default | NA |  | Default |  | NA | NA | NA | NA | NA |  | NA |  | Default | Default | NA |  | Default | Default | NA |  | Default | Default | NA
| Electric Heat Pump Heating Efficiency Adjustment Curve | [107 empty] | NA | NA | NA | NA | Default | NA | Default | NA |  | Default |  | NA | NA | NA | NA | NA |  | NA |  | Default | Default | NA |  | Default | Default | NA |  | Default | Default | NA
| Fan Part-load Performance Curve | [107 empty] | NA | NA | NA | Cubic: coefficients 0.025, 0.57, 0.12, 0.285 | Default | Any Fan with VSD | Default | Any Fan with VSD |  | Default | [5 empty] | Any Fan with VSD |  | VSD with Static Pressure Reset |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| HVAC(Availability/Fan) Schedule | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | [18 empty] | Office | Office | Office | Office | Office | Office | Office | Office |  | Office |  | Office | Office | Office | Office | Office |  | Office |  | Office | Office | Office |  | Hotel | Hotel | Hotel |  | Office | Office | Office
| Cooling Schedule | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | [18 empty] | Office | Office | Office | Office | Office | Office | Office | Office |  | Office |  | Office | Office | Office | Office | Office |  | NA |  | NA | NA | NA |  | Hotel | Hotel | Hotel |  | Office | Office | Office
| Heating Schedule | [65 empty] | Office | Office | Office | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | Retail | Health | Office | Assembly | Office | Office | Assembly | [18 empty] | Office | Office | Office | Office | Office | Office | Office | Office |  | Office |  | Office | Office | Office | Office | Office |  | Office |  | Office | Office | Office |  | Hotel | Hotel | Hotel |  | Office | Office | Office
| Terminal Heat Type | [107 empty] | NA | NA | NA | Hot Water | NA | Hot Water | NA | Hot Water |  | NA |  | Hot Water | NA | Hot Water | NA | Hot Water |  | NA |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Terminal Heat Capacity | [107 empty] | NA | NA | NA | Sized on load with 1.25 oversizing factor | NA | Sized on load with 1.25 oversizing factor | NA | Sized on load with 1.25 oversizing factor |  | NA |  | Not part of Test Case | NA | Not part of Test Case | NA | 1.25 |  | NA |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Terminal Unit Fan Power | [118 empty] | NA |  | NA | [9 empty] | 0.25 W/cfm | 0.25 W/cfm | NA |  | NA | NA | NA
| Reheat Delta T | [107 empty] | NA | NA | NA | 30F | NA | 30F | NA | Based on load, but limited to max 40F |  | NA |  | Not part of Test Case | NA | Not part of Test Case | NA | NA |  | NA |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
Boiler Components
| Number of boilers | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | 1 | NA | 1 | NA | 1 |  | NA |  | 1 | NA | 1 | NA | 1 |  | NA |  | NA | NA | NA |  | 1 | 1 | 0 |  | 0 | 0 | 0
| Boiler Capacity | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | autosize x 1.25 | NA | autosize x 1.25 | NA | autosize x 1.25 |  | NA |  |  | NA |  | NA | 1.25 |  | NA |  | NA | NA | NA |  | Based on load calc with oversizing factor of 1.25 | Based on load calc with oversizing factor of 1.25 | NA |  | NA |  | NA
| Boiler Efficiency | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | 86% | NA | 86% | NA | Input Based on Proposed System Size- | Final input based on sizing Run- | NA |  | 80% | NA | 80% | NA | Input Based on Proposed System Size- | Final input based on sizing Run- | NA |  | NA | NA | NA |  | Based on capacity and 110.2 | Based on capacity and 110.2 | Based on capacity and 110.2 |  | Based on capacity and 110.2 | Based on capacity and 110.2 | Based on capacity and 110.2
| Boiler Type | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | Hot Water Boiler | NA | Hot Water Boiler | NA | Hot Water Boiler |  | NA |  | Hot Water Boiler | NA | Hot Water Boiler | NA | Hot Water Boiler |  | NA |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Boiler Heat Loss | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | 0% | NA | 0% | NA | 0% |  | NA |  | 0% | NA | 0% | NA | 0% |  | NA |  | NA | NA | NA |  | 0% | 0% | NA |  | NA | NA | NA
| Boiler Performance Curve | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | Default Curve | NA | Default Curve | NA | Default |  | NA |  | Default Curve | NA | Default Curve | NA | Default |  | NA |  | NA | NA | NA |  | default | Default | NA |  | NA | NA | NA
| Boiler Min. Unloading Ratio | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | 25% | NA | 25% | NA | 25% |  | NA |  | 25% | NA | 25% | NA | 25% |  | NA |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Hot Water Supply Temperature | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | 180F | n/a | 180F | n/a | 180F |  | NA |  | 165F | NA | 165F | NA | 180F |  | NA |  | NA | NA | NA |  | 180F | 180F | NA |  | NA | NA | NA
| Hot Water Return Temperature | [107 empty] | NA | NA | NA | 130F | n/a | 130F | n/a | 130F |  | NA |  | 135F | NA | 135F | NA | 130F |  | NA |  | NA | NA | NA |  | 130F | 130F | NA |  | NA | NA | NA
| Pump Control Type | [110 empty] | Fixed Speed Variable flow pump (Intermittent/CF) |  | Fixed Speed Variable flow pump (Intermittent/CF) |  | Fixed Speed Variable Flow pump (Intermittent/CF) |  | NA |  | Fixed Speed Variable flow pump (Intermittent/CF) |  | Fixed Speed Variable flow pump (Intermittent/CF) |  | Fixed Speed Variable Flow pump (Intermittent/CF) |  |  |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Pump Motor Power | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | CHW: 20 W/gpm CW: 17 W/gpm HHW: 16 W/gpm | NA | CHW: 20 W/gpm CW: 17 W/gpm HHW: 16 W/gpm | NA | CHW: head=40 ft + 0.03xtons, 70% pump eff CW: head=54 ft, 70% pump eff HHW: 19 W/gpm |  | NA |  | CHW: 20 W/gpm CW: 17 W/gpm HHW: 16 W/gpm | NA | CHW: 20 W/gpm CW: 17 W/gpm HHW: 16 W/gpm | NA | CHW: head=40 ft + 0.03xtons, 70% pump eff CW: head=54 ft, 70% pump eff HHW: 19 W/gpm |  | NA |  | NA | NA | NA |  | CHW: 20 W/gpm CW: 17 W/gpm HHW: 16 W/gpm | CHW: 20 W/gpm CW: 17 W/gpm HHW: 16 W/gpm | CHW: head=40 ft + 0.03xtons, 70% pump eff CW: head=54 ft, 70% pump eff HHW: 19 W/gpm |  | 16 W/gpm HHW | 16 W/gpm HHW | 19 W/gpm HHW
| Pump Motor Efficiency | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | 92% | NA | 92% | NA | See Table 27 of ACM Reference Manual |  | NA |  | 89% | NA | 89% | NA | Based on ACM Table 27 |  | NA |  | NA | NA | NA |  | 90% | 90% | From ACM Table 27 |  | NA | NA | NA
| Pump Part Load Curve | [110 empty] | Default Curve | NA | Default Curve | NA | Default |  | NA |  | Default Curve | NA | Default Curve | NA | Default |  | NA |  | NA | NA | NA |  | Default | Default | Default |  | NA | NA | NA
Chiller Components
| Chiller Type | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | Centrifugal chiller | Centrifugal Chiller | Centrifugal chiller | Centrifugal Chiller | Centrifugal Chiller |  | Centrigfugal Chiller |  | NA | NA | NA |  | Screw | Screw | Based on size - Centrifugal if >300 tons |  | NA | NA | NA
| Number of Chillers | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | 2 (for building) |  | 2 (for building) |  | 2 |  | same as building central plant |  | NA | NA | NA |  | 1 | 1 | Based on cooling capacity |  | NA | NA | NA
| Chiller Fuel | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | Electricity |  | Electricity |  | Electricity |  |  |  | NA | NA | NA |  | Electric | Electric | Electric |  | NA | NA | NA
| Chiller Oversizing Factor | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | 1.15 | NA | 1.15 | NA | 1.15 |  | 1.15 |  | NA | NA | NA |  | 1.15 | 1.15 | 1.15 |  | NA | NA | NA
| Chiller Capacity (tons) | [122 empty] | autosize (report value) |  | autosize x 1.15
| Chiller Efficiency | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | COP=6.6 | NA | COP=6.6 | NA | Based on capacity and type, Table 110.2-D |  | Based on system capacity and Table in 110.2 |  | NA | NA | NA |  | COP=5.8 | COP=5.8 if greater than min eff in 110.2; otherwise none | Based on system size and Table 110.2-D |  | NA | NA | NA
| Chiller Part-Load Efficiency (IPLV) | [118 empty] | IPLV=0.45 kW/ton |  | IPLV=0.45 kW/ton |  |  |  | n/a | [5 empty] | IPLV=0.39 kW/ton
| Chiller Min. Unloading Ratio | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | 10% | 15% | 10% | 15% | 10% |  | 15% |  | NA | NA | NA |  | 10% | Based on type - 15% for centrifugal | Based on system type (0.15 for centrifugal) |  | NA | NA | NA
| Chiller Cooling Capacity Adjustment Curve | [114 empty] | NA |  |  |  | Not a User Input | Default | Not a User Input | NA | Default |  | Default |  | NA | NA | NA |  | default | default | default |  | NA | NA | NA
| Chiller Cooling Efficiency Adjustment Curve | [114 empty] | NA |  |  |  | Not a User Input | NA | Not a User Input | NA | Path A or Path B curve from Appendix 5.7 based on system size |  | Path A or Path B curve from Appendix 5.7 based on system size |  | NA | NA | NA |  | not a user input | not a user input | Path A or Path B curve from Appendix 5.7 based on system size |  | NA | NA | NA
| Chilled Water Supply Temperature | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | 42F |  | 44F |  | 44F |  | 44F |  | NA | NA | NA |  | 44 | 44 | 44 |  | NA | NA | NA
| Chilled Water ReturnTemperature | [114 empty] | NA |  |  |  | 54F |  | 64F |  | 64F |  | 64F |  | NA | NA | NA |  | 56 | 56 | 64 |  | NA | NA | NA
| Condensor Type | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | Water-cooled |  | Water-cooled |  | Water-cooled |  | Water-cooled |  | NA | NA | NA |  |  |  | NA |  | NA | NA | NA
| Cooling tower Fan Control Type | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | two-speed |  | two-speed |  | variable-speed |  | Open Tower axial with variable-speed fan |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
| Cooling Tower Fan Horse Power | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | 44 gpm/hp |  | 44 gpm/hp |  | 60 gpm/hp |  | n/a |  | NA | NA | NA |  | 50 gpm/hp | 50 gpm/hp | 60 gpm/hp |  | NA | NA | NA
| Cooling Tower Set Point Control | [107 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | 70F |  | 70F |  | 70F |  | design WB |  | NA | NA | NA |  | wet-bulb reset | wet-bulb reset | Fixed at design dry-bulb |  | NA | NA | NA
| Chiller, Condenser Pump Control Type | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA | [7 empty] | Chilled-water pump- Variable Speed, Variable flow Condenser Water-Fixed Speed |  | Chilled-water pump- Variable Speed, Variable flow Condenser Water-Fixed Speed |  | NA | NA | NA |  | CHW-variable-speed CW = constant-speed | CHW-variable-speed CW = constant-speed | CHW-variable-speed CW = constant-speed |  | NA | NA | NA
| Chiller, Condenser Pump Motor Power | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA | [7 empty] | Chilled-water pump- 22W/gpm Condenser Water-19W/gpm |  | Chilled-water pump- 22W/gpm Condenser Water-19W/gpm |  | NA | NA | NA |  | CHW=20 W/gpm x 2.0 gpm/ton CW 19 W/gpm x 2.4 gpm/ton | CHW=20 W/gpm x 2.0 gpm/ton CW 19 W/gpm x 2.4 gpm/ton | CHW=X W/gpm based on load, 1.2 gpm/ton CW = 19 W/gpm |  | NA | NA | NA
| Chiller, Condenser Pump Motor Efficiency | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | 90% | 90% | 90% | 90% | From ACM Reference Manual based on Table 27 |  | From ACM Reference Manual based on Table 27 |  | NA | NA | NA |  | 90% | 90% | Based on Table 27 in ACM and Standard Design hp |  | NA | NA | NA
| Chiller, Condenser Pump Design Flow | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [53 empty] | NA | NA | NA | [39 empty] | NA | NA | NA | NA |  | NA |  | NA |  |  |  | Chiller- 2.0 gpm/ton Condenser- 2.4 gpm/ton |  | Chiller- 2.0 gpm/ton Condenser- 2.4 gpm/ton |  | Chiller- 1.2 gpm/ton Condenser-2.4 gpm/ton |  | Chiller- 1.2 gpm/ton Condenser-2.4 gpm/ton |  | NA | NA | NA |  | NA | NA | NA |  | NA | NA | NA
Service Hot Water
| Thermal Efficiency | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case | [20 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | [6 empty] | Not part of Test Case | [6 empty] | Not part of Test Case | [6 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | 0.78 | 0.78 | 0.78 | Not part of Test Case | Not part of Test Case | Not part of Test Case | 0.85 |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  | Not part of Test Case |  | Not part of Test Case |  |  |  | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case | Not part of Test Case | Not part of Test Case
| Energy Factor | [104 empty] | n/a | n/a | n/a |  |  |  | n/a | n/a
| Hot Water Load/person | [104 empty] | 106 Btuh/person | 106 Btuh/person | 106 Btuh/person |  |  |  | 0.5 gph/person |  | From App 5.4A
| SHW Schedule | [104 empty] | Office | Office | Office
Exterior Load
| Exterior LPD | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case |  |  |  | Not part of Test Case | [20 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | [6 empty] | Not part of Test Case | [6 empty] | Not part of Test Case | [6 empty] | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case | Driveway- 1115 W | Driveway- 1115 W | 1184 W | Not part of Test Case | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case |  | Not part of Test Case |  |  |  | Not part of Test Case |  | Not part of Test Case |  | Not part of Test Case |  |  |  | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case | Not part of Test Case | Not part of Test Case |  | Not part of Test Case | Not part of Test Case | Not part of Test Case
[106 empty] | Parking Lot- 6566 W | Parking Lot- 6566 W | 7725.2 W
[106 empty] | Sidewalk- 977 W | Sidewalk- 977 W | 1018.4 W
[106 empty] | Building Entrance- 90 W | Building Entrance- 90 W | 90 W
[106 empty] | Hardscape Ornamental Light- 2 W | Hardscape Ornamental Light- 2 W | 2 W
[106 empty] | Building Façade- 9352.75 W | Building Façade- 9352.75 W | 13093.85 W
[106 empty] | Signage- 80 W | Signage- 80 W | 92 W
[106 empty] | Total- 18182.75 W | Total- 18182.75 W | 23205.45 W
Exterior lighting control
| Exterior lighting schedule | [106 empty] | Same as Proposed
Note on DY2: John Arent: Recommend Removing this test
Note on BV42: John Arent: This space will also have demand control ventilation. I'm checking for this in another test case
Note on CC42: John Arent: This space will also have demand control ventilation. I'm checking for this in another test case
Note on BP43: John Arent: Change units to gph/person as needed.
Note on BQ43: John Arent: Change units to gph/person as needed.
Note on BP45: John Arent: I don't think we need to model elevator power if it doesn't contribute to building load.
Note on BQ45: John Arent: I don't think we need to model elevator power if it doesn't contribute to building load.
Note on DX70: John Arent: This is the space setpoint temp, not the supply air temperature
Note on B92: Nambiar, Chitra: Sizing will be at either system or palnt level, not both.
Note on B97: Nambiar, Chitra: This input is not an option in E+ HVAc Template:Plant:Boiler object.
Note on DW105: John Arent: I think these two systems should be on the same central plant.

## Test Status Summary_Old (hidden)
|  |  |  | Pass Date | 141223 | Ruleset Implementation Test Case Directory: |  |  | Ruleset Implementation Test Case Directory:
|  |  |  | CBECC version | CBECC-Com 2013-3a (687) | Repo\trunk\CBECC-Com13\ Projects\RulesetImplementationTests |  |  | Repo\trunk\CBECC-Com13\ Projects\RulesetImplementationTests
Ruleset Implementation Tests |  |  |  | Detailed Geometry Tests |  |  | Simplified Geometry Tests
Test No | Building Type | Category | Test Criteria | Test Complete | Test Notes (include date, verison of ruleset trunk, version of CBECC) | File Path | Test Complete | Test Notes (include date, verison of ruleset trunk, version of CBECC) | File Path
1 | Small Office | Exterior Envelope | Envelope &Window Assy Performance | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 020006-OffSml-Run01\ 020006-OffSml-Run01.cibd | X | PASS - 141223 - CBECC-Com 2013-3a (687) | S020006-OffSml-Run01\S020006-OffSml-Run01.cibd
2 | Small Office | Exterior Envelope | Envelope &Window Assy Performance | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 020015-OffSml-Run02\ 020015-OffSml-Run02.cibd | X | PASS - 141223 - CBECC-Com 2013-3a (687) | S020015-OffSml-Run02\S020015-OffSml-Run02.cibd
3 | Small Hotel | Exterior Envelope | Envelope &Window Assy Performance | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 070015-HotSml-Run03\ 070015-HotSml-Run03.cibd |  | Simplified model not yet available
4 | Medium Office | Exterior Envelope | Envelope Minimum Requirements | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 030006-OffMed-Run04\ 030006-OffMed-Run04.cibd | X | PASS - 141223 - CBECC-Com 2013-3a (687) | S030006-OffMed-Run04\S030006-OffMed-Run04.cibd
5 | Large Office | Fenestration | WWR | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 040006-OffLrg-Run05\ 040006-OffLrg-Run05.cibd |  | Simplified model not yet available
6 | Large Office | Fenestration | WWR | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 040006-OffLrg-Run06\ 040006-OffLrg-Run06.cibd |  | Simplified model not yet available
7 | Warehouse | Skylight | SRR and Skylight Performance | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 080006-Whse-Run07\ 080006-Whse-Run07.cibd |  | Simplified model not yet available
8 | Warehouse | Skylight | SRR and Daylit Area | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 080006-Whse-Run08\ 080006-Whse-Run08.cibd |  | Daylighting simulation not supported in simplified mode
9 | Warehouse | Skylight | SRR and Daylit Area |  | Adding/Enlarging Skylights to meet 140.3C daylit area requirements currently not supported Revisit Point of test and whether it is appropriate to enlarge skyights for 140.3C |  | na | Daylighting simulation not supported in simplified mode
10 | Medium Office | Space Function | Internal Loads- Complete Bldg method |  | Complete Building test method currently not supported |  | na | Complete Building Method not currently supported in CBECC
11 | Large Office | Space Function | Internal Loads- Space by Space | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 040006-OffLrg-Run11\ 040006-OffLrg-Run11.cibd |  | Simplified model not yet available
12 | Medium Office | Lighting | Lighting - tailored lighting method | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 030006-OffMed-Run12\ 030006-OffMed-Run12.cibd |  | Tailiored Method not supported in simplified mode (Requires knowledge of space perimeter)
13 | Medium Office | Lighting | Lighting - tailored lighting method | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 030006-OffMed-Run13\ 030006-OffMed-Run13.cibd | na | Tailiored Method not supported in simplified mode (Requires knowledge of space perimeter)
14 | Small Office | Lighting | Lighting - PAF rules | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 020006-OffSml-Run14\ 020006-OffSml-Run14.cibd | X | PASS - 141223 - CBECC-Com 2013-3a (687) | S020006-OffSml-Run14\S020006-OffSml-Run14.cibd
15 | Warehouse | Lighting Control | Daylighting | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 080006-Whse-Run15\ 080006-Whse-Run15.cibd | na | Daylighting simulation not supported in simplified mode
16 | Medium Retail | Lighting Control | Lighting&Daylighting | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 050006-RetlMed-Run16\050006-RetlMed-Run16.cibd | na | Daylighting simulation not supported in simplified mode
17 | Large Office | Ext.Lighting/SHW | Ext. Lighting/SHW |  | Prescriptive Exterior Lighting Compliance not supported |  | na | Prescriptive Exterior Lighting Compliance not supported
18 | Small Office | HVAC | HVAC-PSZ Baseline | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 020006-OffSml-Run18\ 020006-OffSml-Run18.cibd | X | PASS - 141223 - CBECC-Com 2013-3a (687) | S020006-OffSml-Run18\S020006-OffSml-Run18.cibd
19 | Medium Office | HVAC | HVAC-PVAV& CRAC | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 030006-OffMed-Run19\030006-OffMed-Run19.cibd | na | Prescriptive Exterior Lighting Compliance not supported for December Release
20 | Large Office | HVAC | HVAC-VAV& CRAH | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 040006-OffLrg-Run20\040006-OffLrg-Run20.cibd | na
21 | Warehouse | HVAC | HVAC-H&V only | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 080006-Whse-Run21\ 080006-Whse-Run21.cibd | na | Simplified model not yet available
22 | Hotel | HVAC | HVAC-FPFC | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 070015-HotSml-Run22\070015-HotSml-Run22.cibd | na | Dedicated Commercial Kitchen System not supported Water Side Economizer - Review with David
23 | Medium Office | Existing Alteration | Window Alteration and HVAC Replacement |  |  | 030006-OffMed-Run23\ 030006-OffMed-Run23.cibd |  | Simplified model not yet initiated
24 | Small Office | Existing Alteration | Window Alteration and HVAC Replacement | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 020006-OffSml-Run24\ 020006-OffSml-Run24.cibd |  | Simplified model not yet initiated
25 | Small Office | Existing Alteration | Window Alteration | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 020006-OffSml-Run25\ 020006-OffSml-Run25.cibd |  | Simplified model not yet initiated
26 | Small Office | Existing Alteration | Window Alteration | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 020006-OffSml-Run26\ 020006-OffSml-Run26.cibd |  | Simplified model not yet initiated
27 | Retail Medium | Existing Addition | Zones Added and HVAC Added | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 050006-RetlMed-Run27\ 050006-RetlMed-Run27.cibd |  | Simplified model not yet initiated
28 | Retail Medium | Existing Addition and Alteration | Zones Added and HVAC Added | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 050006-RetlMed-Run28\ 050006-RetlMed-Run28.cibd |  | Simplified model not yet initiated
29 | Medium Office | New Envelope | Zones Added and HVAC Added | X | PASS - 141223 - CBECC-Com 2013-3a (687) | 030006-OffMed-Run29\ 030006-OffMed-Run29.cibd |  | Simplified model not yet initiated
30 | Medium Office | New Mechanical and Partial Lighting | Zones Added and HVAC Added | X | PASS - 140609 - CBECC-Com 2013-2b | 030006-OffMed-Run30\ 030006-OffMed-Run30.cibd |  | Simplified model not yet initiated

## Test Status Summary
| Ruleset Implementation Tests - Test Specification Status | [14 empty] | Status of Example Test Files - Detailed Geometry |  | Status of Example Test Files - Simplified Geometry
| Test No | Building Type | Test Name | Compliance Type | Test Category | Test Criteria | Notes | Version 2016.1.0 | Additional notes | Version 2016.2.0 | Additional notes | Streamlined Set | Additional notes | Streamlined Set | Additional notes | Example Test File Status | Example Test File Path | Example Test File Status | Example Test File Path
| 1 | Small Office | 020006-OffSml-Run01 | NewComplete | Exterior Envelope | Envelope and window assembly performance |  | X |  | X | For Simplified Geometry Test use 020006S-OffSml-Run01.cibd16 |  |  |  |  | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006-OffSml-Run01\020006-OffSml-Run01.cibd16 | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006S-OffSml-Run01\020006S-OffSml-Run01.cibd16
| 2 | Small Office | 020006-OffSml-Run02 | NewComplete | Exterior Envelope | Envelope and window assembly performance |  | X |  | X | For Simplified Geometry Test use 020015S-OffSml-Run02.cibd16 |  |  |  |  | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020015-OffSml-Run02\020015-OffSml-Run02.cibd16 | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020015S-OffSml-Run02\020015S-OffSml-Run02.cibd16
| 3 | Small Hotel | 070015-HotSml-Run03 | NewComplete | Exterior Envelope, Fenestration and HVAC | Envelope and window assembly performance Ventilation strategies - OA via system, DOAS, natural ventilation and Ventilation induced via exhaust fans. |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 070015-HotSml-Run03\070015-HotSml-Run03.cibd16 | Status: Test Not Performed Date: Version: | na
| 4 | Medium Office | 030006-OffMed-Run04 | NewComplete | Exterior Envelope | Envelope minimum requirements |  | X |  | X | For Simplified Geometry Test use 030006S-OffMed-Run04.cibd16 |  |  |  |  | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 030006-OffMed-Run04\030006-OffMed-Run04.cibd16 | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 030006S-OffMed-Run04\030006S-OffMed-Run04.cibd16
| 5 | Large Office | 040006-OffLrg-Run05 | NewComplete | Fenestration | Window Wall Ratio (WWR) |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 040006-OffLrg-Run05\040006-OffLrg-Run05.cibd16 | Status: Test Not Performed Date: Version: | na
| 6 | Large Office | 040006-OffLrg-Run06 | NewComplete | Fenestration | Window Wall Ratio (WWR) |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 040006-OffLrg-Run06\040006-OffLrg-Run06.cibd16 | Status: Test Not Performed Date: Version: | na
| 7 | Warehouse | 080006-Whse-Run07 | NewComplete | Skylight | Skylight to Roof Ratio (SRR) and Skylight Performance |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 080006-Whse-Run07\080006-Whse-Run07.cibd16 | Status: Test Not Performed Date: Version: | na
| 8 | Warehouse | 080006-Whse-Run08 | NewComplete | Skylight | Skylight to Roof Ratio (SRR) and Daylit Area | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 080006-Whse-Run08\080006-Whse-Run08.cibd16 | Status: Test Not Performed Date: Version: | na
| 9 | Warehouse | 080006-Whse-Run09 | NewComplete | Skylight | SRR and Daylit Area | Adding/Enlarging Skylights to meet 140.3C daylit area requirements currently not supported | [8 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
| 10 | Medium Office | 030006-OffMed-Run10 | NewComplete | Space Function | Internal Loads- Complete Bldg method | Complete Building test method currently not supported | [8 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
| 11 | Large Office | 040006-OffLrg-Run11 | NewComplete | Space Function | Internal loads - Space-by-Space |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 040006-OffLrg-Run11\040006-OffLrg-Run11.cibd16 | Status: Test Not Performed Date: Version: | na
| 12 | Medium Office | 030006-OffMed-Run12 | NewComplete | Lighting | Lighting - tailored lighting method |  | X |  | X | For Simplified Geometry Test use 030006S-OffMed-Run12.cibd16 |  |  |  |  | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 030006-OffMed-Run12\030006-OffMed-Run12.cibd16 | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | na
| 13 | Medium Office | 030006-OffMed-Run13 | NewComplete | Lighting | Lighting - tailored lighting method |  | X |  | X | For Simplified Geometry Test use 030006S-OffMed-Run13.cibd16 |  |  |  |  | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 030006-OffMed-Run13\030006-OffMed-Run13.cibd16 | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | na
| 14 | Small Office | 020006-OffSml-Run14 | NewComplete | Lighting | Lighting - Power Adjustment Factors (PAF) rules |  | X |  | X | For Simplified Geometry Test use 020006S-OffSml-Run14.cibd16 |  |  |  |  | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006-OffSml-Run14\020006-OffSml-Run14.cibd16 | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006S-OffSml-Run14\020006S-OffSml-Run14.cibd16
| 15 | Warehouse | 080006-Whse-Run15 | NewComplete | Lighting Control | Daylighting | Exclude Test for Simplified Geometry: Only daylighting parameters are being tested. | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 080006-Whse-Run15\080006-Whse-Run15.cibd16 | Status: Date: Version: | Test Excluded for Simplified geometry
| 16 | Medium Retail | 050006-RetlMed-Run16 | NewComplete | Lighting Control | Lighting and daylighting | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 050006-RetlMed-Run16\050006-RetlMed-Run16.cibd16 | Status: Test Not Performed Date: Version: | na
| 17 | Large Office | 040006-OffLrg-Run17 | NewComplete | Ext.Lighting/SHW | Ext. Lighting/SHW | Prescriptive Exterior Lighting Compliance not supported | [8 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
| 18 | Small Office | 020006-OffSml-Run18 | NewComplete | HVAC | HVAC - SZAC |  | X |  | X | For Simplified Geometry Test use 020006S-OffSml-Run18.cibd16 |  |  |  |  | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006-OffSml-Run18\020006-OffSml-Run18.cibd16 | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006S-OffSml-Run18\020006S-OffSml-Run18.cibd16
| 19 | Medium Office | 030006-OffMed-Run19 | NewComplete | HVAC | HVAC - PVAV and CRAC |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 030006-OffMed-Run19\030006-OffMed-Run19.cibd16 | Status: Test Not Performed Date: Version: | na
| 20 | Large Office | 040006-OffLrg-Run20 | NewComplete | HVAC | HVAC - VAV and CRAH |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 040006-OffLrg-Run20\040006-OffLrg-Run20.cibd16 | Status: Test Not Performed Date: Version: | na
x | 21 | Warehouse | 080006-Whse-Run21 | NewComplete | HVAC | HVAC - SZAC and HV |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 080006-Whse-Run21\080006-Whse-Run21.cibd16 | Status: Test Not Performed Date: Version: | na
| 22 | Hotel | 070015-HotSml-Run22 | NewComplete | HVAC | HVAC - PVAV, SZAC and FPFC |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 070015-HotSml-Run22\070015-HotSml-Run22.cibd16 | Status: Test Not Performed Date: Version: | na
| 23 | Medium Office | 030006-OffMed-Run23 | ExistingAlteration | Exterior Envelope, Fenestration and HVAC | Window alteration and HVAC replacement |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 030006-OffMed-Run23\030006-OffMed-Run23.cibd16 | Status: Test Not Performed Date: Version: | na
| 24 | Small Office | 020006-OffSml-Run24 | ExistingAlteration | Fenestration and HVAC | Window alteration and HVAC replacement |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006-OffSml-Run24\020006-OffSml-Run24.cibd16 | Status: Test Not Performed Date: Version: | na
| 25 | Small Office | 020006-OffSml-Run25 | ExistingAlteration | Fenestration | Window alteration |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006-OffSml-Run25\020006-OffSml-Run25.cibd16 | Status: Test Not Performed Date: Version: | na
| 26 | Small Office | 020006-OffSml-Run26 | ExistingAlteration | Fenestration | Window alteration |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 020006-OffSml-Run26\020006-OffSml-Run26.cibd16 | Status: Test Not Performed Date: Version: | na
| 27 | Retail Medium | 050006-RetlMed-Run27 | ExistingAddition | Fenestration and HVAC | Addition modeled alone: Envelope performance, window assembly performance and HVAC - SZAC |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 050006-RetlMed-Run27\050006-RetlMed-Run27.cibd16 | Status: Test Not Performed Date: Version: | na
| 28 | Retail Medium | 050006-RetlMed-Run28 | ExistingAdditionAndAlteration | Exterior Envelope, Fenestration and HVAC | Addition modeled with an altered existing building: Envelope performance, Window Wall Ratio (WWR) and HVAC - SZAC |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 050006-RetlMed-Run28\050006-RetlMed-Run28.cibd16 | Status: Test Not Performed Date: Version: | na
| 29 | Medium Office | 030006-OffMed-Run29 | NewEnvelope | Exterior Envelope and HVAC | Envelope and correct assignment of proposed HVAC systems. |  | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 030006-OffMed-Run29\030006-OffMed-Run29.cibd16 | Status: Test Not Performed Date: Version: | na
| 30 | Medium Office | 030006-OffMed-Run30 | NewMechanicalAndPartialLighting | HVAC and Partial Lighting | New/exisiting lighting and HVAC - PVAV | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | X |  | X | [5 empty] | Status: Verified Date: 07/08/2016 Version: CBECC-Com 2016.2.0 (861) | svn.code.sf.net/p/cbecc-com/code/tags/CBECC-Com16.1.0_3833/CBECC-Com13/Projects/RulesetImplementation2016 Tests 030006-OffMed-Run30\030006-OffMed-Run30.cibd16 | Status: Test Not Performed Date: Version: | na

## Small Office
Key:
| Base PrototypeTest Parameters | Most General parameters of prototype building. Specific test instances to be generated based on this model.
| Not Part of Test Case | Not Specified - Not Part of Test Case
| Test Instance Specification Incomplete | Updates to test instance specfication in progress
| Test Instance Specification Complete | Updates to test instance specification have been completed
| Daylighting (Detailed Geometry Models Only) | Exclude Testing/Verification of Daylighting Parameters in Simplified Geometry Models
|  | Small Office General Prototype | Relevant SDD Properties | 020006-OffSml- Run01 |  |  | 020015-OffSml- Run02 |  |  | 020006-OffSml- Run14 |  |  | 020006-OffSml-Run18 |  |  | 020006-OffSml-Run24 - Existing Alteration |  |  | 020006-OffSml-Run25 - Existing Alteration |  |  | 020006-OffSml-Run26 - Existing Alteration
|  | User model |  | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model
Building Type |  |  |  | Small Office |  |  | Small Office |  | Small Office | Small Office | Small Office | Small Office | Small Office | Small Office | Small Office | Small Office |  |  | Small Office | Small Office | Small Office | Small Office | Small Office | Small Office
Vintage |  |  |  | New Construction |  |  | New Construction |  |  | New Construction |  |  | New Construction |  |  | New Construction |  |  | New Construction |  |  | New Construction
Climate Zone |  |  |  | CZ-6 |  |  | CZ-15 |  | CZ-15 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6
Geometry
| Total Floor Area (sq feet) | 5500 (90.8 ft x 60.5 ft)
| Aspect Ratio | 1.5
| Number of Floors | 1
| Azimuth | 0
| Thermal Zoning | Perimeter zone depth: 16.4 ft. Four perimeter zones, one core zone and an attic zone. Percentages of floor area: Perimeter 70%, Core 30%
| Floor to floor height (feet) | 10
| Floor to ceiling height (feet) | 10
| Roof Dimensions | Based on floor area and aspect ratio
| Roof Tilt and Orientation | hipped roof, 2 foot soffit, 18° tilt
| Foundation Dimensions | Based on floor area and aspect ratio
| Window Fraction (Window to Wall Ratio) | 24.4% for South and 19.8% for the other three orientations | [13 empty] | Overall: 21% North: 20% East: 20% South: 24% (Window Compliance Status: Altered) West: 20% | Overall: 21% North: 20% East: 20% South: 24% West: 20% | Overall: 21% North: 20% East: 20% South: 24% West: 20% | Overall: 42% North: 20% East: 20% South: 94% (Window Compliance Status: Altered) West: 20% | Overall: 42% North: 20% East: 20% South: 94% West: 20% | Overall: 42% North: 20% East: 20% South: 94% West: 20% | Overall: 42% North: 20% East: 20% South: 94% (Window Compliance Status: New) West: 20% | Overall: 42% North: 20% East: 20% South: 94% West: 20% | Overall: 40% North: 20% East: 20% South: 87% West: 20%
| Window Dimensions | Window Dimensions: 6.0 ft x 5.0 ft punch windows for all façades
| Glazing Sill Height (feet) | 3 (top of the window is 8 ft high with 5 ft high glass)
| Window Location | evenly distributed along four façades
| Skylight Fraction (Skylight to Roof Ratio) | NA
| Skylight Dimensions | NA
| Skylight Locations | NA
Envelope Components
| Roof Construction Assembly Type Slope Category | WoodFramingandOtherRoof Steep | Roof:ConsType | WoodFramingAndOtherRoof Steep | WoodFramingAndOtherRoof Steep | WoodFramingAndOtherRoof Steep | WoodFramingAndOtherRoof Steep | WoodFramingAndOtherRoof Steep | WoodFramingAndOtherRoof Steep
| Roof Construction Assembly overall U value | 0.044 | Roof:OverallUFactor | 0.044 | 0.044 | 0.049 | 0.053 | 0.053 | 0.034
| Roof Construction Assembly layers | 1.Asphalt roll roofing - 1/4 in. (R-0.15) 2.Hardboard - HDF - 50 lb/ft3 - 3/4 in. (R-1.03) 3. Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | ConsAssm:MatRef[X] | 1. Asphalt roll roofing - 1/4 in. 2. Hardboard - HDF - 50 lb/ft3 - 3/4 in. 3. Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | 1. Asphalt roll roofing - 1/4 in. 2. Hardboard - HDF - 50 lb/ft3 - 3/4 in. 3. Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | 1.Metal Standing Seam - 1/16 in. 2. Compliance Insulation R19.63 | 1.Asphalt roll roofing - 1/4 in. 2.Hardboard - HDF - 50 lb/ft3 - 3/4 in. 3.Expanded Polystyrene - EPS - 4 1/16 in. R17 | 1. Asphalt roll roofing - 1/4 in. 2. Hardboard - HDF - 50 lb/ft3 - 3/4 in. 3. Expanded Polystyrene - EPS - 4 1/16 in. R17 | 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R28.63
| Roof Aged Solar Reflectance (Solar Absorptance) | 0.75 (0.25) | ConsAssm:CRRCAgedRefl (ConsAssm:ExtSolAbs) | 0.75 (0.25) | 0.75 (0.25) | 0.20 (0.92) | 0.60 (0.40) | 0.60 (0.40) | 0.20 (0.92)
| Roof Aged Thermal emittance (Thermal Absorptance) | 0.78 (0.78) | ConsAssm:CRRCAgedEmittance (ConsAssm:ExtThrmlAbs) | 0.78 (0.78) | 0.78 (0.78) | 0.85 (0.85) | 0.70 (0.70) | 0.70 (0.70) | 0.85 (0.85)
| Exterior Wall Construction Assembly Type | WoodFramingAndOtherWall | ExtWall:ConsType | WoodFramingAndOtherWall | WoodFramingAndOtherWall | MetalFrameWall | MetalFrameWall | MetalFrameWall | MetalFrameWall
| Exterior Wall Construction Assembly overall U value | 0.091 | ExtWall:OverallUFactor | 0.091 | 0.091 | 0.069 | 0.056 | 0.056 | 0.062
| Exterior Wall Construction Assembly layers | 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3. Insulation/Framing Layer (Wood 16in OC, R-15, 2x4) 4. Gypsum Board - 1/2 in. | ConsAssm:MatRef[X] | 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3. Wood framed wall, 16in. OC, 4.0in., R-15 4. Gypsum Board - 1/2 in. | 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3.Wood framed wall, 16in. OC, 4.0in., R-15 4. Gypsum Board - 1/2 in. | 1. Stucco - 7/8 in. 2. Compliance Insulation R10.06 3. Compliance Insulation R2.00 4. Compliance Insulation R0.20 5. Compliance Insulation R0.10 6. Air - Metal Wall Framing - 16 or 24 in. OC 7. Gypsum Board - 1/2 in. | 1. Stucco 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3 in. R13 4. Metal, Wall 16in. OC, 2X6, Cav. R-19 5.Gypsum Board - 1/2 in. | 1. Stucco 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3 in. R13 4. Metal, Wall 16in. OC, 2X6, Cav. R-19 5. Gypsum Board - 1/2 in. | 1. Stucco 7/8 in. 2. Compliance Insulation R13.99 3. Air - Metal Wall Framing - 16 or 24 in. OC 4. Gypsum Board - 1/2 in.
| Above-grade Floor Construction Assembly Type | Ground Floor: NA (Slab-on grade) Soffit: Other Floor | ExtFlr:ConsType | Ground Floor: MassFloor Soffit: OtherFloor | Ground Floor: MassFloor Soffit: OtherFloor | Other Floor | Ground Floor: NA (Slab -on grade) Soffit: OtherFloor | Ground Floor: NA (Slab -on grade) Soffit: OtherFloor | NA (Slab -on grade) Soffit: OtherFloor
| Above-grade Floor Construction Assembly overall U value | Exterior Floor: Ground Floor: NA Exterior Floor: Soffit: 0.070 | ExtFlr:OverallUFactor | Exterior Floor: Ground Floor: 0.039 Exterior Floor: Soffit: 0.070 | Exterior Floor: Ground Floor: 0.039 Exterior Floor: Soffit: 0.070 | 0.071 | Exterior Floor: Ground Floor - NA Exterior Floor: Soffit - 0.070 | Exterior Floor: Ground Floor - NA Exterior Floor: Soffit - 0.070 | Exterior Floor: Ground Floor - NA Exterior Floor: Soffit - 0.039
| Above-grade Floor Construction Assembly layers | Exterior Floor: Ground Floor NA Exterior Floor: Soffit 1. Plywood -3/4in. 2. Insulation/Framing Layer (R-15, 2x4) | ConsAssm:MatRef[X] | Exterior Floor: Ground Floor 1. Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 2. Concrete - 80 lb/ft3 - 4 in. 3. Metal Deck - 1/16in. 4. OSB - Oriented Strand Board - 5/8 in. 5. Carpet - 3/4 in. Exterior Floor: Soffit 1. Plywood -3/4in. 2. Wood, Floor16in OC, 2x4, cav. R-15 | Exterior Floor: Ground Floor 1. Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 2. Concrete - 80 lb/ft3 - 4 in. 3. Metal Deck - 1/16in. 4. OSB - Oriented Strand Board - 5/8 in. 5. Carpet - 3/4 in. Exterior Floor: Soffit 1. Plywood -3/4in. 2. Wood, Floor16in OC, 2x4, cav. R-15 | Exterior Floor: Ground Floor 1. Compliance Insulation R9.83 2. Plywood - 5/8 in. 3. Carpet - 3/4 in. Exterior Floor: Soffit 1. Compliance Insulation R9.83 2. Plywood - 5/8 in. 3. Carpet - 3/4 in. | Exterior Floor: Ground Floor - NA Exterior Floor: Soffit 1. Plywood -3/4in. 2. Wood, Floor16in OC, 2x4, cav. R-15 | Exterior Floor: Ground Floor - NA Exterior Floor: Soffit 1. Plywood -3/4in. 2. Wood, Floor16in OC, 2x4, cav. R-15 | Exterior Floor: Ground Floor - NA Exterior Floor: Soffit 1. Compliance Insulation R21.39 2. Plywood - 5/8 in. 3. Carpet - 3/4 in.
| On/Below Grade Floor F-factor Total Perimeter Area Total Perimeter exposed | 0.70 3891.16 ft2 302.6 ft | UndgrFlr:OverallFFactor |  |  |  | 0.70 3891.16 ft2 302.82 ft | 0.70 3891.16 ft2 302.82 ft | 0.73 3891.16 ft2 302.82 ft
| Vertical Window Type | Fixed | FenCons:FenProdType | Fixed | Fixed | Fixed | Fixed | Fixed | Fixed | [6 empty] | Fixed | Fixed | Fixed | Fixed | Fixed | Fixed | Fixed | Fixed | Fixed
| Window assembly U value | 0.25 | FenCons:UFactor | 0.25 | 0.25 | 0.36 | 0.25 | 0.25 | 0.36 | [6 empty] | Window Compliance status: Altered (South elevation): U-Value = 0.40 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55 | Window Compliance status: Altered (South elevation): U-Value = 0.40 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55 | Window Compliance status: Altered (South elevation): U-Value = 0.47 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55 | Window Compliance status: Altered (South elevation): U-Value = 0.40 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55 | Window Compliance status: Altered (South elevation): U-Value = 0.40 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55 | Window Compliance status: Altered (South elevation): U-Value = 0.47 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55 | Window Compliance status: New (South elevation): U-Value = 0.35 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55 | Window Compliance status: New (South elevation): U-Value = 0.35 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55 | Window Compliance status: New (South elevation): U-Value = 0.36 Window Compliance status: Existing (All Other Elevations N, E, W): U-Value = 0.55
| Window SHGC | 0.2 | FenCons:SHGC | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.25 | [6 empty] | Window Compliance status: Altered (South elevation): SHGC = 0.33 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56 | Window Compliance status: Altered (South elevation): SHGC = 0.33 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56 | Window Compliance status: Altered (South elevation): SHGC = 0.31 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56 | Window Compliance status: Altered (South elevation): SHGC = 0.33 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56 | Window Compliance status: Altered (South elevation): SHGC = 0.33 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56 | Window Compliance status: Altered (South elevation): SHGC = 0.31 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56 | Window Compliance status: New (South elevation): SHGC = 0.32 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56 | Window Compliance status: New (South elevation): SHGC = 0.32 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56 | Window Compliance status: New (South elevation): SHGC = 0.25 Window Compliance status: Existing (All Other Elevations N, E, W): SHGC = 0.56
| Window VT | 0.45 | FenCons:VT | 0.45 | 0.45 | 0.42 | 0.45 | 0.45 | 0.42 | [6 empty] | Window Compliance status: Altered (South elevation) VT = 0.50 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60 | Window Compliance status: Altered (South elevation): VT = 0.50 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60 | Window Compliance status: Altered (South elevation): VT = 0.42 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60 | Altered Windows (South elevation): VT = 0.50 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60 | Window Compliance status: Altered (South elevation): VT = 0.50 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60 | Window Compliance status: Altered (South elevation): VT = 0.42 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60 | Window Compliance status: New (South elevation): VT = 0.53 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60 | Window Compliance status: New (South elevation): VT = 0.53 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60 | Window Compliance status: New (South elevation): VT = 0.42 Window Compliance status: Existing (All Other Elevations N, E, W): VT = 0.60
| Window overhang | NA | Win:ExtShdgObj |  |  |  | South Windows- 2 feet Horizontal overhang West Windows- 2 feet Vertical fin | South Windows- 2 feet Horizontal overhang West Windows- 2 feet Vertical fin | None
| Skylight overall U value | NA
| Skylight SHGC | NA
| Skylight VT | NA
| Daylit Area (calculated value) | Calculated by Software According to ACM section 5.4.5
Internal Load Components
| Occupancy Type | Office (Greater than 250 square feet in floor area)
| People Density | 200 ft2/person
| Sensible Heat/person | 250 Btu/h-person
| Latent Heat/person | 200 Btu/h-person
| Equipment Power Density | 1.5 W/ft2
| Lighting Power Density | 0.9 W/ft2 | Spc:IntLPDReg Spc:IntLtgSpecMthd Spc:IntLtgSys:TailoredMthdAllowType Spc:TMGenLPD Spc:TMTotAllowLPD | [6 empty] | Zone 1: 0.94*(1-0.05) = 0.90 -Demand Responsive Control Zone 2: 0.88*(1-0.05) = 0.84 -Demand Responsive Control Zone 3: 0.94*(1-0.05) = 0.90 -Demand Responsive Control Zone 4: 0.88*(1-0.05) = 0.84 -Demand Responsive Control Core Zone: 0.87*(1-0.05) = 0.83 -Demand Responsive Control Attic Zone: 0 | Zone 1: 0.90 Zone 2: 0.84 Zone 3: 0.90 Zone 4: 0.84 Core Zone: 0.83 Attic Zone: 0 | Zone 1: 0.75 Zone 2: 0.75 Zone 3: 0.75 Zone 4: 0.75 Core Zone: 0.75 Attic Zone: 0
| Ventilation Rate Per Person | 0.15 cfm/ft2
Ventilation Rate Per Area
Simulated Ventilation Rate
| Infiltration Rate | 0.0448 cfm/ft2
| Infiltration Schedule | Office Infiltration | Spc: InfSchRef
| Infiltration Method | FlowExteriorWallArea | Spc: InfMthd
| Elevator Power | NA | Spc: DsgnInfRt
Occupancy Schedule
Equipment Schedule
| Lighting Schedule |  | Spc:IntLtgRegSchRef | [7 empty] | Zone 1: OfficeLights Zone 2: OfficeLights Zone 3: OfficeLights Zone 4: OfficeLights Core Zone: OfficeLights Attic Zone: na | Zone 1: OfficeLights Zone 2: OfficeLights Zone 3: OfficeLights Zone 4: OfficeLights Core Zone: OfficeLights Attic Zone: na
| Elevator Schedule | NA
Daylighting - verify these properties for detailed geometry models only.
| Illuminance Setpoint | 287.5 lux | Spc:PriSideDayltgIllumSetPt
| Daylight Control Type | Continuous | ThrmlZn:DayltgCtrlType
| Controlled General Lighting Power In Primary Daylit Area | Defaulted: Lighting Power Density*(Daylit Area/Total Area) | ThrmlZn:PriSideDayltgCtrlLtgPwr
| Controlled General Lighting Power In Secondary Daylit Area | 0 | ThrmlZn:SecSideDayltgCtrlLtgPwr
| Controlled General Lighting Power In Skylit Daylit Area | NA | ThrmlZn:SkylitDayltgCtrlLtgPwr
| Reference Position 1 | Calculated by Software According to ACM section 5.4.5 | ThrmlZn:DayltgIllumRefPt1Coord[1] ThrmlZn:DayltgIllumRefPt1Coord[2] ThrmlZn:DayltgIllumRefPt1Coord[3]
| Reference Position 2 | Calculated by Software According to ACM section 5.4.5 | ThrmlZn:DayltgIllumRefPt2Coord[1] ThrmlZn:DayltgIllumRefPt2Coord[2] ThrmlZn:DayltgIllumRefPt2Coord[3]
HVAC Components
| HVAC System Type | SZAC | [10 empty] | Air System Compliance Status: New (Perimeter_ZN_1): SPVHP (Perimeter_ZN_2): SPVAC (Perimeter_ZN_3): SZAC (Perimeter_ZN_4): SZAC (Core_ZN): PSVAC | Air System Compliance Status: New (Perimeter_ZN_1): SPVHP (Perimeter_ZN_2): SPVAC (Perimeter_ZN_3): SZAC (Perimeter_ZN_4): SZAC (Core_ZN): PTAC | Base Air System 3 (SZAC) | Air System Compliance Status: New (South Perimeter Zone): SZAC Air System Compliance Status: Existing (All Other Zones): SZAC | Air System Compliance Status: New (South Perimeter Zone): SZAC Air System Compliance Status: Existing (All Other Zones): SZAC | Air System Compliance Status: New (South Perimeter Zone): Base Air System 3 (SZAC) Air System Compliance Status: Existing (All Other Zones): SZAC
| Heating Type | Gas Furnace | [10 empty] | (Perimeter_ZN_1): HeatPump (All Other Zones): Gas Furnace | Same as user model | Gas Furnace | Coil Heating Compliance Status: New & Exisiting Gas Furnace | Same as user model | Coil Heating Compliance Status: New & Existing Gas Furnace
| Cooling Type | Direct Expansion (DX) | [10 empty] | Direct Expansion (DX) | Same as user model | Direct Expansion (DX) | Coil Cooling Compliance Status: New & Existing Direct Expansion (DX) | Same as user model | Coil Cooling Compliance Status: New & Existing Direct Expansion (DX)
| Cooling Efficiency | Zone 1: SEER - 13 Zone 2: SEER - 13 Zone 3: SEER - 13 Zone 4: SEER - 13 Core Zone: EER - 10.8 | [10 empty] | (Perimeter_ZN_1) and (Perimeter_ZN_2): EER - 12 (Perimeter_ZN_3) and (Perimeter_ZN_4): SEER - 17.58 (EER - 13.1 , COP-3.83 for reference, not input) (Core_ZN): EER - 12 | (Perimeter_ZN_1) and (Perimeter_ZN_2): EER - 12 (Perimeter_ZN_3) and (Perimeter_ZN_4): EER - 13 (Core_ZN): EER - 12 | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat) | Coil Cooling Compliance Status: New (South Perimeter Zone): SEER 18.0 (EER - 13.2 , COP-3.88 for reference, not input) Coil Cooling Compliance Status: Existing (All Other Zones): SEER - 13.0 (EER - 10.8 , COP-3.17 for reference, not input) | Coil Cooling Compliance Status: New (South Perimeter Zone): EER - 13 Coil Cooling Compliance Status: Existing (All Other Zones): EER - 10.8 | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
| Heating Efficiency | 81% Thrml, 78% AFUE | [10 empty] | 78% AFUE (80% Thermal Efficiency for reference, not input) Perimeter_Zn_1: 3.5 COP | 80% Thermal Efficiency | Min Req. Based on Coil Capacity < 225,000 Btu/hr: 78% AFUE or 80% Thrml >=225,000 Btu/hr: 80% Thrml | Coil Heating Compliance Status: New (South Perimeter Zone): 78.8% AFUE, (80.4% Thermal Efficiency,) Coil Heating Compliance Status: Existing (All Other Zones): 78% AFUE (80% Thermal Efficiency for reference, not input) | Coil Heating Compliance Status: New (South Perimeter Zone): 80.4% Thermal Efficiency Coil Heating Compliance Status: Existing (All Other Zones): 80% Thermal Efficiency | Min Req. Based on Coil Capacity < 225,000 Btu/hr: 78% AFUE or 80% Thrml >=225,000 Btu/hr: 80% Thrml
| System Oversizing Factor | NA | [10 empty] | NA | Same as user model | Heating- 1.25 Cooling- 1.15 | NA | Same as user model | Air System Compliance Status: New (Bottom Floor, South Perimeter Zone): Heating- 1.25 Cooling- 1.15
| System Capacity | Heating Capacity - default Cooling Capacity - default | [10 empty] | Heating Capacity - default Cooling Capacity - default | Same as user model | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat | Heating Capacity - default Cooling Capacity - default | Same as user model | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat
| Design Supply Air Temperature | Cooling - 55F Perimeter, 60F Core Heating 95F | [10 empty] | Cooling - 55F Perimeter, 55F Core Heating - 95F Perimeter, 95F Core | Same as user model | Cooling - 55F Perimeter, 55F Core Heating - 95F Perimeter, 95F Core | Cooling - 55F Perimeter, 55F Core Heating - 95F Perimeter, 95F Core | Same as user model | Cooling - 55F Perimeter, 55F Core Heating - 95F Perimeter, 95F Core
| SAT Reset Control | Fixed | [10 empty] | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Same as user model | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Same as user model | No SAT Control (Htg/clg cycles on/off based on call from thermostat)
| Economizer | None | [10 empty] | Perim1ZnSPVHP AirSys - Non Integrated All Other Systems: None | Same as user model | Integrated if load over 54 kBtu/h (If Economizer is specified) | None | NA | Integrated if load over 54 kBtu/h (If Economizer is specified)
| Economizer Limits | NA | [10 empty] | Perim1ZnSPVHP AirSys - Fixed Dry Bulb, High DryBulb Loackout 70F All Other Systems: NA | Same as user model | Differential Dry-Bulb (If Economizer is specified) | NA | NA | Differential Dry-Bulb (If Economizer is specified)
| Fan Power Specification | Brake Horsepower Method: Zone 1: 1.2 bhp Zone 2: 0.8 bhp Zone 3: 1.2 bhp Zone 4: 0.8 bhp Core Zone: 1.6 bhp | [10 empty] | Brake Horsepower Method: Core Zone: 1.6 bhp 0.865 Motor Eff Zone 1: 1.12 bhp 0.855 Motor Eff Zone 2: 0.8 bhp 0.855 Motor Eff Zone 3: 1.2 bhp 0.855 Motor Eff Zone 4: 0.8 bhp 0.855 Motor Eff | Same as user model | Static Pressure Method: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 | Brake Horsepower Method: Fan Compliance Status: New (South Perimeter Zone): Zone 1: 1.12 bhp 0.855 Motor Eff Fan Compliance Status: Existing (All Other Zones): Core Zone: 1.6 bhp 0.865 Motor Eff Zone 2: 0.8 bhp 0.855 Motor Eff Zone 3: 1.2 bhp 0.855 Motor Eff Zone 4: 0.8 bhp 0.855 Motor Eff | Same as user model | Static Pressure Method: Fan Compliance Status: New (South Perimeter Zone): The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Brake Horsepower Method: Fan Compliance Status: Existing (All Other Zones): Core Zone: 1.6 bhp 0.865 Motor Eff Zone 2: 0.8 bhp 0.855 Motor Eff Zone 3: 1.2 bhp 0.855 Motor Eff Zone 4: 0.8 bhp 0.855 Motor Eff
| Motor Horsepower | [11 empty] | Core Zone: 2.0 hp Zone 1: 1.5 hp Zone 2: 1.0 hp Zone 3: 1.5 hp Zone 4: 1.0 hp | Same as user model | Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 | Fan Compliance Status: New (South Perimeter Zone): Zone 1: 1.5 hp Fan Compliance Status: Existing (All Other Zones): Core Zone: 2.0 hp Zone 2: 1.0 hp Zone 3: 1.5 hp Zone 4: 1.0 hp | Same as user model | Fan Compliance Status: New (South Perimeter Zone): Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Fan Compliance Status: Existing (All Other Zones): Core Zone: 2 hp Zone 2: 1 hp Zone 3: 1.5 hp Zone 4: 1.0 hp
| Fan Control Method | Constant Volume | [10 empty] | Constant Volume | Same as user model | Constant Volume | Constant Volume | Same as user model | Constant Volume
| Cooling Coil Curve(s) | Not Input (DXEIR_fTempCrvRef) (DXEIR_fPLFCrvRef) (DXEIR_fFlowCrvRef) | [10 empty] | Not input | Curve Selection Dependent On Coil Capacity: SPVAC and SPVHP (without economizers): CoilClgPTACEIRRatio_fTwbToadbSI CoilClgPTACEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio SPVHP (with economizer): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Curve Selection Dependent On Coil Capacity: For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Not input | Curve Selection Dependent On Coil Capacity: For SEER Rated Coils (< 65,000 Bth/h): Air System Compliance Status: Existing (All Other Zones): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio Air System Compliance Status: New (South Perimeter Zone): CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Curve Selection Dependent On Coil Capacity: For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio
| Heating Coil Curve(s) | Not Input (FurnHIR_fPLRCrvRef) | [10 empty] | Not input | Perim1ZnSPVHP AirSys: CoilHtgHPEIRRatio_fQFrac All Other Systems: CoilHtgFurnFIRRatio_fQRatio | CoilHtgFurnFIRRatio_fQRatio | Not input | CoilHtgFurnFIRRatio_fQRatio | CoilHtgFurnFIRRatio_fQRatio
| Fan Part-load Performance Curve | Not Input | [10 empty] | Not input | None (Constant Volume) | None (Constant Volume) | Not input | None (Constant Volume) | None (Constant Volume)
| HVAC(Availability/Fan) Schedule | Not Input | [10 empty] | Not input | OfficeHVACAvail | OfficeHVACAvail | Not input | OfficeHVACAvail | OfficeHVACAvail
| Cooling Thermostat Schedule | Not Input | [10 empty] | Not input | OfficeClgSetPt | OfficeClgSetPt | Not input | OfficeClgSetPt | OfficeClgSetPt
| Heating Thermostat Schedule | Not Input | [10 empty] | Not input | OfficeHtgSetPt | OfficeHtgSetPt | Not input | OfficeHtgSetPt | OfficeHtgSetPt
| Terminal Heat Type | NA
| Terminal Heat Capacity | NA
| Terminal Unit Fan Power | NA
| Reheat Delta T | NA
Boiler Components
| Number of boilers | NA
| Boiler Capacity | NA
| Boiler Efficiency | NA
| Boiler Type | NA
| Boiler Heat Loss | NA
| Boiler Performance Curve | NA
| Boiler Min. Unloading Ratio | NA
| Hot Water Supply Temperature | NA
| Hot Water Return Temperature | NA
| Pump Control Type | NA
| Pump Power | NA
| Pump Motor Efficiency | NA
| Pump Part Load Curve | NA
Chiller Components
| Chiller Type | NA
| Number of Chillers | NA
| Chiller Fuel | NA
| Chiller Oversizing Factor | NA
| Chiller Capacity (tons) | NA
| Chiller Efficiency | NA
| Chiller Part-Load Efficiency (IPLV) | NA
| Chiller Min. Unloading Ratio | NA
| Chiller Cooling Capacity Adjustment Curve | NA
| Chiller Cooling Efficiency Adjustment Curve | NA
| Chilled Water Supply Temperature | NA
| Chilled Water ReturnTemperature | NA
| Condensor Type | NA
| Cooling tower Fan Control Type | NA
| Cooling Tower Fan Horse Power | NA
| Cooling Tower Set Point Control | NA
| Chiller, Condenser Pump Control Type | NA
| Chiller, Condenser Pump Motor Power | NA
| Chiller, Condenser Pump Motor Efficiency | NA
| Chiller, Condenser Pump Design Flow | NA
Service Hot Water
| SWH type | Storage | WtrHtr:Type
| Fuel type | Natural Gas | WtrHtr:FuelSrc
| Thermal Efficiency | 85% | WtrHtr:ThrmlEff
| Energy Factor | 0.77 | WtrHtr:EF
| Hot Water Load/person (gal/h-person) | 0.18 | Spc:HotWtrHtgRt
| SHW Schedule |  | Spc:HotWtrHtgSchRef
| Tank Volume (gal) |  | WtrHtr:StorCap
| Availability Schedule | None | FluidSys:AvailSchRef
| Water temperature setpoint Schedule | Fixed | FluidSys:TempCtrl
| Water temperature setpoint | 180 | FluidSys:FixedSupTemp
| Water Heater Max Capacity (Btuh) | 80000 | WtrHtr:CapRtd
| Performance Curve | Default | WtrHtr:HIR_fPLRCrvRef
| Standby Loss (Btuh) | 726 | WtrHtr:StbyLoss
Note on D151: Jason Acosta: this varies based on temp control

## Medium Office
Key:
| Base PrototypeTest Parameters | Most General parameters of prototype building. Specific test instances to be generated based on this model.
| Not Part of Test Case | Not Specified - Not Part of Test Case
| Test Instance Specification Incomplete | Updates to test instance specfication in progress
| Test Instance Specification Complete | Updates to test instance specification have been completed
| Daylighting (Detailed Geometry Models Only) | Exclude Testing/Verification of Daylighting Parameters in Simplified Geometry Models
|  | Medium Office General Prototype | Relevant SDD Properties | 030006-OffMed-Run04 |  |  | Run10 - INCOMPLETE |  |  | 030006-OffMed-Run12 |  |  | 030006-OffMed-Run13 |  |  | 030006-OffMed-Run19 - VAV reheat system with CRAC Unit | [5 empty] | 030006-OffMed-Run23 - Existing Alteration |  |  | 030006-OffMed-Run29 - New Envelope |  |  | 030006-OffMed-Run30 - New Mechanical and Partial Lighting
|  | User model |  | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model |  | Proposed Model |  | Baseline model |  | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model
Building Type |  |  |  | Medium Office |  | Medium Office | Medium Office | Medium Office | Medium Office | Medium Office |  |  | Medium Office | Medium Office | Medium Office | Medium Office, All Core- Zones are Computer Rooms | [5 empty] | Medium Office |  |  | Medium Office |  | Medium Office | Medium Office |  | Medium Office
Vintage |  |  |  | New Construction |  |  | New Construction |  |  | New Construction |  |  | New Construction |  |  | New Construction | [5 empty] | New Construction |  |  | New Construction |  |  | New Construction
Climate Zone |  |  |  | CZ-6 |  | CZ-6 | CZ-6 | CZ-6 | CZ-6 | CZ-6 |  |  | CZ-6 | CZ-6 | CZ-6 | CZ-6 | [5 empty] | CZ-6 |  |  | CZ-6 |  | CZ-6 | CZ-6 |  | CZ-6
Geometry | [15 empty] | Office | Computer Data Room | Office | Computer Data Room | Office | Computer Data Room
| Total Floor Area (sq feet) | 53600 sq. ft. (163.8 x 109.2)
| Aspect Ratio | 1.5
| Number of Floors | 3
| Azimuth | 0
| Thermal Zoning | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 40%, Core 60%
| Floor to floor height (feet) | 13
| Floor to ceiling height (feet) | 9 (4 ft ceiling plenum)
| Roof Dimensions | Based on floor area and aspect ratio
| Roof Tilt and Orientation | Horizontal
| Foundation Dimensions | Based on floor area and aspect ratio
| Window Fraction (Window to Wall Ratio) | 33% in all orientations | [19 empty] | Overall: 31% North: 33% East: 33% South: 33% West: 22% (Top Floor Window removed) | Overall: 31% North: 33% East: 33% South: 33% West: 22% | Overall: 31% North: 33% East: 33% South: 33% West: 22%
| Window Dimensions | 163.8 ft x 4.29 ft on the long side of facade 109.2 ft x 4.29 ft on the short side of the façade)
| Glazing Sill Height (feet) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass)
| Window Location | evenly distributed along four façades | [19 empty] | evenly distributed along four façades Except on Top Floor West Perimeter Zone, where window is replaced by a In-Fill wall. | evenly distributed along four façades Except on Top Floor West Perimeter Zone, where window is replaced by a In-Fill wall. | evenly distributed along four façades Except on Top Floor West Perimeter Zone, where window is replaced by a In-Fill wall.
| Skylight Fraction (Skylight to Roof Ratio) | NA
| Skylight Dimensions | NA
| Skylight Locations | NA
Envelope Components
| Roof Construction Assembly Type Slope Category | Metal Frame Roof (Wood Frame and Other), horizontal | Roof:ConsType | [18 empty] | Roof Compliance Status: New Metal Frame Roof (Wood Frame and Other) Low | Roof Compliance Status: New Metal Frame Roof (Wood Frame and Other) Low | Roof Compliance Status: New Metal Frame Roof (Wood Frame and Other) Low | Roof Compliance Status: New Metal Frame Roof (Wood Frame and Other) Low | Roof Compliance Status: New Metal Frame Roof (Wood Frame and Other) Low | Roof Compliance Status: New Metal Frame Roof (Wood Frame and Other) Low
| Roof Construction Assembly overall U value | 0.065 | Roof:OverallUFactor | [18 empty] | 0.065 | 0.065 | 0.049 | 0.065 | 0.065 | 0.075
| Roof Construction Assembly layers | "WoodFramingAndOtherRoofU065": 1. "Metal Deck - 1/16 in." (R-0), 2. "Expanded Polystyrene - EPS - 3 1/2." (R-14.58) | ConsAssm:MatRef[X] | [18 empty] | Roof Compliance Status: New 1. Metal Standing Seam - 1/16 2. Expanded Polystyrene - EPS - 3 1/2 in. R15 | Roof Compliance Status: Altered 1. Metal Standing Seam - 1/16 2. Expanded Polystyrene - EPS - 3 1/2 in. R15 | Roof Compliance Status: Altered 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R19.63 | 1. Metal Standing Seam - 1/16. 2. Expanded Polystyrene - EPS - 3 1/2 in. R15 | 1. Metal Standing Seam - 1/16 2. Expanded Polystyrene - EPS - 3 1/2 in. R15 | 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R12.55
| Roof Aged Solar Reflectance (Solar Absorptance) | 0.1 | ConsAssm:CRRCAgedRefl ConsAssm:ExtSolAbs | [18 empty] | 0.10 (0.90) | 0.10 (0.90) | 0.63 (0.37) | 0.75 (0.25) | 0.75 (0.25) | 0.63 (0.37)
| Roof Aged Thermal emittance (Thermal Absorptance) | 0.8 | ConsAssm:CRRCAgedEmittance ConsAssm:ExtThrmlAbs | [18 empty] | 0.80 (0.80) | 0.80 (0.80) | 0.85 (0.85) | 0.78 (0.78) | 0.78 (0.78) | 0.85 (0.85)
| Exterior Wall Construction Assembly Type | MetalFrameWall | ExtWall:ConsType | MetalFrameWall | NONE - PROJECT FAILS MANDATORY MINIMUM PERFORMANCE CHECKS | NONE - PROJECT FAILS MANDATORY MINIMUM PERFORMANCE CHECKS | [15 empty] | Exterior Wall Compliance Status: Existing Exterior Wall Compliance Status: New (Infill) MetalFrameWall | Exterior Wall Compliance Status: Existing Exterior Wall Compliance Status: New (Infill) MetalFrameWall | MetalFrameWall | MetalFrameWall | MetalFrameWall | MetalFrameWall
| Exterior Wall Construction Assembly overall U value | 0.068 | ExtWall:OverallUFactor | 0.189 | [17 empty] | Exterior Wall Compliance Status: Existing Exterior Wall Compliance Status: New (Infill) 0.068 | Exterior Wall Compliance Status: Existing Exterior Wall Compliance Status: Altered (Infill) 0.068 | Exterior Wall Compliance Status: Existing 0.068 Exterior Wall Compliance Status: Altered 0.069 | 0.068 | 0.068 | 0.098
| Exterior Wall Construction Assembly layers | MetalFrameWallU068: 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3in. R13 4. Air - Metal Wall Framing - 16 or 24 in. OC 5. Gypsum Board - 1/2 in. | ConsAssm:MatRef[X] | 1. Stucco 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3/4 in. R3.1 4. Air - Metal Wall Framing - 16 or 24in. OC 5. Gypsum Board - 1/2 in. | [17 empty] | Exterior Wall Compliance Status: Existing Exterior Wall Compliance Status: New (Infill) 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3in. R13 4. Air - Metal Wall Framing - 16 or 24 in. OC 5. Gypsum Board - 1/2 in. | Exterior Wall Compliance Status: Existing Exterior Wall Compliance Status: Altered (Infill) 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3in. R13 4. Air - Metal Wall Framing - 16 or 24 in. OC 5. Gypsum Board - 1/2 in. | Exterior Wall Compliance Status: Existing 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3in. R13 4. Air - Metal Wall Framing - 16 or 24 in. OC 5. Gypsum Board - 1/2 in. Exterior Wall Compliance Status: Altered (Infill) 1. Stucco 7/8 in. 2. Compliance Insulation R10.06 3. Compliance Insulation R2.00 4. Compliance Insulation R0.20 5. Compliance Insulation R0.10 6. Air - Metal Wall Framing - 16 or 24 in. OC 7. Gypsum Board - 1/2 in. | 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3in. R13 4. Air - Metal Wall Framing - 16 or 24 in. OC 5. Gypsum Board - 1/2 in. | 1. Stucco - 7/8 in. 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3in. R13 4. Air - Metal Wall Framing - 16 or 24 in. OC 5. Gypsum Board - 1/2 in. | 1. Stucco 7/8 in. 2. Compliance Insulation R8.07 3. Air - Metal Wall Framing - 16 or 24 in. OC 4. Gypsum Board - 1/2 in.
| Above-grade Floor Construction Assembly Type | NA (Slab-on grade) | ExtFlr:ConsType | [21 empty] | MassFloor | MassFloor | MassFloor
| Above-grade Floor Construction Assembly overall U value | NA | ExtFlr:OverallUFactor | [21 empty] | 0.039 | 0.039 | 0.071
| Above-grade Floor Construction Assembly layers | NA | ConsAssm:MatRef[X] | [21 empty] | 1. Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 2. Concrete - 80 lb/ft3 - 4 in. 3. Metal Deck - 1/16 in. 4. OSB - Oriented Strand Board - 5/8 in. 5. Carpet - 3/4 in. | 1. Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 2. Concrete - 80 lb/ft3 - 4 in. 3. Metal Deck - 1/16 in. 4. OSB - Oriented Strand Board - 5/8 in. 5. Carpet - 3/4 in. | 1. Compliance Insulation R9.83 2. Plywood - 5/8 in. 3. Carpet - 3/4 in.
| On/Below Grade Floor F-factor Total Perimeter Area Total Perimeter exposed | 0.54 Btu/hr.ft.F 17875 ft2 545.8 ft | UndgrFlr:OverallFFactor
| Vertical Window Type | Fixed | FenCons:FenProdType | [12 empty] | Refer tab: Run19_MedOff - Glzg Config | Refer tab: Run19_MedOff - Glzg Config | Refer tab: Run19_MedOff - Glzg Config | Refer tab: Run19_MedOff - Glzg Config | Refer tab: Run19_MedOff - Glzg Config | Refer tab: Run19_MedOff - Glzg Config | Fixed | Fixed | Fixed | Fixed | Fixed | Fixed
| Window assembly U value | CZ-6 Standard Design "Fixed Window" U-0.26 | FenCons:UFactor | [18 empty] | Window Compliance status: New (Top Floor South Window)-0.40; Window Compliance status: Existing (All other windows - N,E, S, W)-0.55 | Window Compliance status: New (Top Floor South Window)-0.40; Window Compliance status: Existing (All other windows - N,E, S, W)-0.55 | Window Compliance status: New (Top Floor South Window)-0.36; Window Compliance status: Existing (All other windows - N,E, S, W)-0.55 | 0.35 | 0.35 | 0.36
| Window SHGC | CZ-6 Standard Design "Fixed Window" SHGC-0.25 | FenCons:SHGC | [18 empty] | Window Compliance status: New (Top Floor South Window)-0.33; Window Compliance status: Existing (All other windows - N,E, S, W)-0.56 | Window Compliance status: New (Top Floor South Window)-0.33; Window Compliance status: Existing (All other windows - N,E, S, W)-0.56 | Window Compliance status: New (Top Floor South Window)-0.25; Window Compliance status: Existing (All other windows - N,E, S, W)-0.56 | 0.32 | 0.32 | 0.25
| Window VT | CZ-6 Standard Design "Fixed Window" VT-0.42 | FenCons:VT | [18 empty] | Window Compliance status: New (Top Floor South Window)-0.50; Window Compliance status: Existing (All other windows - N,E, S, W)-0.60 | Window Compliance status: New (Top Floor South Window)-0.50; Window Compliance status: Existing (All other windows - N,E, S, W)-0.60 | Window Compliance status: New (Top Floor South Window)-0.42; Window Compliance status: Existing (All other windows - N,E, S, W)-0.60 | 0.53 | 0.53 | 0.42
| Window overhang | None
| Skylight overall U value | NA
| Skylight SHGC | NA
| Skylight VT | NA
| Daylit Area (calculated value) | Core Bottom, Core Mid, Core Top: 0 ft2 Perimeter Bottom Zone 1, Perimeter Mid Zone 1, Perimeter Top Zone 1: Floor Area: 2231 ft2 Daylit Area: 2231 ft2 (100%) (Primary Side: 1191 ft2, Secondary Side 1041 ft2) Perimeter Bottom Zone 2, Perimeter Mid Zone 2, Perimeter Top Zone 2: Floor Area: 1413 ft2 Daylit Area: 1413 ft2 (100%) (Primary Side: 774 ft2, Secondary Side 638 ft2) Perimeter Bottom Zone 3, Perimeter Mid Zone 3, Perimeter Top Zone 3: Floor Area: 2231 ft2 Daylit Area: 2231 ft2 (100%) (Primary Side: 1190 ft2, Secondary Side 1041 ft2) Perimeter Bottom Zone 4, Perimeter Mid Zone 4, Perimeter Top Zone 4: Floor Area: 1413 ft2 Daylit Area: 1413 ft2 (100%) (Primary Side: 774 ft2, Secondary Side 638 ft2)
Internal Load Components
| Occupancy Type | Office (Greater than 250 square feet in floor area) | Spc:SpcFunc |  |  |  | Office (250 square feet in floor area or less) | Office (250 square feet in floor area or less) | Office (250 square feet in floor area or less) | Perimeter Spaces (all lvls): Lobby, Main Entry Core Spaces (all lvls): Waiting Area | Perimeter Spaces (all lvls): Lobby, Main Entry Core Spaces (all lvls): Waiting Area | Perimeter Spaces (all lvls): Lobby, Main Entry Core Spaces (all lvls): Waiting Area | Perimeter Spaces (all lvls): Lobby, Main Entry Core Spaces (all lvls): Waiting Area | Perimeter Spaces (all lvls): Lobby, Main Entry Core Spaces (all lvls): Waiting Area | Perimeter Spaces (all lvls): Lobby, Main Entry Core Spaces (all lvls): Waiting Area | Perimeter Spaces (all lvls): Office (Greater than 250 square feet in floor area) | Core Spaces (all lvls): Computer Room | Perimeter Spaces (all lvls): Office (Greater than 250 square feet in floor area) | Core Spaces (all lvls): Computer Room | Perimeter Spaces (all lvls): Office (Greater than 250 square feet in floor area) | Core Spaces (all lvls): Computer Room
| People Density | 200 ft2/person | Spc:OccDens |  |  |  | 50 ft2/person | 100 ft2/person | 100 ft2/person | [7 empty] | 666.67 ft2/person |  | 666.67 ft2/person |  | 666.67 ft2/person
| Sensible Heat/person | 250 Btu/h-person | Spc:OccSensHtRt |  |  |  | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant
| Latent Heat/person | 200 Btu/h-person | Spc:OccLatHtRt |  |  |  | 206 Btu/occupant | 206 Btu/occupant | 206 Btu/occupant
| Equipment Power Density | 1.34 W/ft2 | Spc:RecptPwrDens |  |  |  | 3 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | [6 empty] | Office: 0.8 W/ft2 | Computer Room: 18 W/ft2 | Office: 1.5 W/ft2 | Computer Room: 20 W/ft2 | Office: 1.5 W/ft2 | 20 W/ft2
| Lighting Power Density | 0.8 (Int LPD reg.) | Spc:IntLPDReg Spc:IntLtgSpecMthd Spc:IntLtgSys:TailoredMthdAllowType Spc:TMGenLPD Spc:TMTotAllowLPD |  |  |  | 1.2 W/ft2 | 1.2 W/ft2 | 0.8 W/ft2 | Office (Greater than 250 square feet in floor area)-Perimeter Spaces (Zone 4 only) all lvls Simulated LPD: 0.5W/ft2 Total Area Category Method: (Gen. Lighting)- 0.5 W/ft2 Lobby, Main Entry-Perimeter Spaces (except Zone 4) all lvls Simulated LPD: 0.5W/ft2 Total Tailored Method: (Gen. Lighting)- 0.5 W/ft2 Waiting Area-Core Spaces all Lvls Simulated LPD: 0.95W/ft2 Total, (Gen. Lighting)- 0.75 W/ft2 (TailoredOrnamentalAndSpecialEffectAllowance)- 0.2 W/ft2 | Office (Greater than 250 square feet in floor area)-Perimeter Spaces (Zone 4 only) all lvls Simulated LPD: 0.5W/ft2 Total Area Category Method: (Gen. Lighting)- 0.5 W/ft2 Lobby, Main Entry-Perimeter Spaces (except Zone 4) all lvls Simulated LPD: 0.5W/ft2 Total Tailored Method: (Gen. Lighting)- 0.5 W/ft2 Waiting Area-Core Spaces all Lvls Simulated LPD: 0.95 W/ft2 Total, (Gen. Lighting)-0.75 W/ft2 (TailoredOrnamentalAndSpecial EffectAllowance)-0.2 W/ft2 | Office (Greater than 250 square feet in floor area)-Perimeter Spaces (Zone 4 only) all lvls Simulated LPD: 0.75 W/ft2 Total, Lobby, Main Entry-Perimeter Spaces (except Zone 4) all lvls Simulated LPD: 0.64 W/ft2 Total, Waiting Area-Core Spaces all Lvls Simulated LPD: 0.84 W/ft2 Total, (Gen. Lighting)-0.64 W/ft2 (TailoredOrnamentalAndSpecial EffectAllowance)-0.2 W/ft2 | Office (Greater than 250 square feet in floor area)-Perimeter Spaces (Zone 4 only) all lvls Simulated LPD: 0.8W/ft2 Total Area Category Method: (Gen. Lighting)- 0.8 W/ft2 Lobby, Main Entry-Perimeter Spaces (except Zone 4) all lvls Simulated LPD: 0.9 W/ft2 Total, (Gen. Lighting) - 0.8 W/ft2 (TailoredTaskAllowance) - 0.1 W/ft2 Waiting Area-Core Spaces all Lvls Simulated LPD: 1.9 W/ft2 Total, (Gen. Lighting) - 0.6 W/ft2 (TailoredOrnamentalAndSpecialEffectAllowance) - 1.2 W/ft2 (TailoredFloorDisplayAllowance) - 0.1 W/ft2 | Office (Greater than 250 square feet in floor area)-Perimeter Spaces (Zone 4 only) all lvls Simulated LPD: 0.8W/ft2 Total Area Category Method: (Gen. Lighting)- 0.8 W/ft2 Lobby, Main Entry-Perimeter Spaces (except Zone 4) all lvls Simulated LPD: 0.9 W/ft2 Total, (Gen. Lighting) - 0.8 W/ft2 (TailoredTaskAllowance) - 0.1 W/ft2 Waiting Area-Core Spaces all Lvls Simulated LPD: 1.9 W/ft2 Total, (Gen. Lighting) - 0.6 W/ft2 (TailoredOrnamentalAndSpecialEffectAllowance) - 1.2 W/ft2 (TailoredFloorDisplayAllowance) - 0.1 W/ft2 | Office (Greater than 250 square feet in floor area)-Perimeter Spaces (Zone 4 only) all lvls Simulated LPD: 0.75W/ft2 Total Lobby, Main Entry-Perimeter Spaces (except Zone 4) all lvls Simulated LPD: 0.74 W/Ft2 (Gen. Lighting)- 0.64 W/ft2 (TailoredTaskAllowance) - 0.1 W/ft2 Waiting Area-Core Spaces all Lvls Simulated LPD: 1.24 W/ft2 Total, (Gen. Lighting) - 0.64 W/ft2 (TailoredOrnamentalAndSpecialEffectAllowance) - 0.5 W/ft2 (TailoredFloorDisplayAllowance) - 0.1 W/ft2 | [9 empty] | No lighting system is specified in the proposed design (LightingStatus - Future) | 0.75 W/ft2 | 0.75 W/ft2 | Lighting Compliance Status: New Core Spaces: (0.8 W/ft2) 0.48 W/ft2 w/ Occupant Sensing Controls (OccupantSensingControls-1to125SF) Lighting Compliance Status: New South Perimeter Spaces: 0.8 W/ft2 Lighting Compliance Status: Existing All other Perimeter Spaces: 1.2 W/ft2 | Lighting Compliance Status: New Core Spaces: 0.48 Lighting Compliance Status: New South Perimeter Spaces: 0.8 W/ft2 Lighting Compliance Status: Existing Perimeter Spaces: 1.2 W/ft2 | Lighting Compliance Status: New Core Spaces: 0.75 Lighting Compliance Status: New South Perimeter Spaces: 0.75 W/ft2 Lighting Compliance Status: Existing Perimeter Spaces: 1.2 W/ft2
| Ventilation Rate Per Person | 0.15 cfm/ft2 |  |  |  |  | 0.15 cfm/ft2 | 0.15 cfm/ft3 | 0.15 cfm/ft2
Ventilation Rate Per Area
Simulated Ventilation Rate
| Infiltration Rate | 0.0448 cfm/ft2 |  |  |  |  | 106 Btu/person | 106 Btu/person | 106 Btu/person
| Infiltration Schedule | Office | Spc:InfSchRef
| Infiltration Method | Flow Exterior Wall area
| Elevator Power | NA
| Occupancy Schedule | [5 empty] | Office Not Part of Test Case | Office Not Part of Test Case | Office Not Part of Test Case
| Equipment Schedule | [5 empty] | Office Not Part of Test Case | Office Not Part of Test Case | Office Not Part of Test Case | [8 empty] | OfficeReceptacle | DataReceptacle | OfficeReceptacle | DataReceptacle
| Lighting Schedule |  | Spc:IntLtgRegSchRef |  |  |  | Office Not Part of Test Case | Office Not Part of Test Case | Office Not Part of Test Case |  | OfficeLights | OfficeLights |  | OfficeLights | OfficeLights
| Elevator Schedule | [5 empty] | Office Not Part of Test Case | Office Not Part of Test Case | Office Not Part of Test Case
Daylighting
| Illuminance Setpoint | 287.5 lux | Spc:PriSideDayltgIllumSetPt | [24 empty] | Perimeter Spaces: -Skylit: none -Primary Sidelit: 287.5 lux (287.5 lux Adj.) -Secondary Sidelit: none | Perimeter Spaces: -Skylit: none -Primary Sidelit: 287.5 lux (287.5 lux Adj.) -Secondary Sidelit: none | Perimeter Spaces: -Skylit: none -Primary Sidelit: All Spaces: 287.5 lux (287.5 lux Adj.) -Secondary Sidelit: South Perimeter Spaces: 287.5 lux (1150 lux Adj.) North Perimeter Spaces: none East and West Perimeter Spaces: none
| Daylight Control Type | Continuous | ThrmlZn:DayltgCtrlType | [24 empty] | ContinuousDimming | ContinuousDimming | ContinuousDimming
| Controlled General Lighting Power In Primary Daylit Area | Defaulted: Lighting Power*(Daylit Area/Total Area) | ThrmlZn:PriSideDayltgCtrlLtgPwr | [24 empty] | South Perimeter Spaces: 952.36 W North Perimeter Spaces: 1428.54 W East and West Perimeter Spaces: 929.11 W | South Perimeter Spaces: 952.36 W North Perimeter Spaces: 1428.54 W East and West Perimeter Spaces: 929.11 W | South Perimeter Spaces: 892.84 W North Perimeter Spaces: 1428.54 W East and West Perimeter Spaces: 929.11 W
| Controlled General Lighting Power In Secondary Daylit Area | NA | ThrmlZn:SecSideDayltgCtrlLtgPwr | [26 empty] | South Perimeter Spaces: 780.60 W North Perimeter Spaces: NA East and West Perimeter Spaces: NA
| Controlled General Lighting Power In Skylit Daylit Area | NA | ThrmlZn:SkylitDayltgCtrlLtgPwr
| Reference Position 1 | Calculated by Software According to ACM section 5.4.5 | [25 empty] | Calculated by Software According to ACM section 5.4.5 | Same as user input | Calculated by Software According to ACM section 5.4.5
| Reference Position 2 | Calculated by Software According to ACM section 5.4.5 | [25 empty] | Calculated by Software According to ACM section 5.4.5 | Same as user input | Calculated by Software According to ACM section 5.4.5
HVAC Components | [15 empty] | Office | Comp Room | Office | Comp Room | Office | Comp Room
| HVAC System Type | PVAV with Reheat | [13 empty] | PVAV with Reheat | SZAC | Same as user model | Same as user model | PVAV with Reheat (System 5) | CRAC (System 11) | Air System Compliance Status: New (Top Floor West Perimeter Zone): SZAC Air System Compliance Status: Existing Fluid System Compliance Status: Existing (All Other Zones): PVAV with Reheat. | Air System Compliance Status: New (Top Floor West Perimeter Zone): SZAC Air System Compliance Status: Existing Fluid System Compliance Status: Existing (All Other Zones): PVAV with Reheat. | Air System Compliance Status: New (Top Floor West Perimeter Zone):Base Air System 3 (SZAC) Air System Compliance Status: Existing Fluid System Compliance Status: Existing (All Other Zones): Same as Proposed | No Mechnaical system is specified in the proposed design | BaseAirSys5 (PVAV) | BaseAirSys5 (PVAV) | Air System Compliance Status: New Fluid System Compliance Status: New PVAV with Reheat | Air System Compliance Status: New Fluid System Compliance Status: New PVAV with Reheat | Air System Compliance Status: New Fluid System Compliance Status: New BaseAirSys5 (PVAV)
| Heating Type | Hot Water boiler with reheat | [13 empty] | Hot Water boiler with reheat | None | Same as user model | Same as user model | Hot Water boiler with reheat | None | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): Gas Furnace Coil Heating Compliance Status: Existing (All Other Zones): Hot Water boiler with reheat | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): Gas Furnace Coil Heating Compliance Status: Existing (All Other Zones): Hot Water boiler with reheat | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): Gas Furnace Coil Heating Compliance Status: Existing (All Other Zones): Hot Water boiler with reheat | Not Input | Hot Water boiler with reheat | Hot Water boiler with reheat | Coil Heating Compliance Status: Existing Hot Water boiler with reheat | Coil Heating Compliance Status: Existing Hot Water boiler with reheat | Coil Heating Compliance Status: Existing Hot Water boiler with reheat
| Cooling Type | Direct Expansion (DX) | [13 empty] | DX | DX | Same as user model | Same as user model | DX | DX | Coil Cooling Compliance Status: New (Top Floor West Perimeter Zone): Direct Expansion (DX) Coil Cooling Compliance Status: Existing (All Other Zones): Direct Expansion (DX) | Coil Cooling Compliance Status: New (Top Floor West Perimeter Zone): Direct Expansion (DX) Coil Cooling Compliance Status: Existing (All Other Zones): Direct Expansion (DX) | Coil Cooling Compliance Status: New (Top Floor West Perimeter Zone): Direct Expansion (DX) Coil Cooling Compliance Status: Existing (All Other Zones): Direct Expansion (DX) | Not Input | Direct Expansion (DX) | Direct Expansion (DX) | Coil Cooling Compliance Status: New Direct Expansion (DX) | Coil Cooling Compliance Status: New Direct Expansion (DX) | Coil Cooling Compliance Status: New Direct Expansion (DX)
| Cooling Efficiency | EER=9.8 | [13 empty] | EER - 12.96 IEER - 15.2 (COP-3.8 for reference, not input) | EER - 13.65 IEER - 15.7 (COP-4 for reference, not input) | Same as user model | Same as user model | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat) | Minimum req. based on 2013 Appl Std Table C-9 | Coil Cooling Compliance Status: New (Top Floor West Perimeter Zone): SEER - 18 (EER - 13.2, COP - 3.88 for reference, not input) Coil Cooling Compliance Status: Existing (All Other Zones): EER - 9.8 IEER - 11.4 (COP - 2.87 for reference, not input) | Coil Cooling Compliance Status: New (Top Floor West Perimeter Zone): EER - 13 (The default EER constrained to be no greater than 13 asper the ACM 5.7.5.2 Direct Expansion.) Coil Cooling Compliance Status: Existing (All Other Zones): EER - 9.8 IEER - 11.4 (COP - 2.87 for reference, not input) | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat) | Not Input | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat) | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat) | Coil Cooling Compliance Status: New EER=13.1 (COP - 3.84, for reference, not input) | Coil Cooling Compliance Status: New EER=13.1 | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
| Heating Efficiency | NA | [13 empty] | NA | NA | Same as user model | Same as user model | NA | None | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): 81% Thermal Efficiency 79% AFUE Coil Heating Compliance Status: Existing (All Other Zones): NA | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): 81% Thermal Efficiency Coil Heating Compliance Status: Existing (All Other Zones): NA | Min Req. Based on Coil Capacity < 225,000 Btu/hr: 78% AFUE or 80% Thrml >=225,000 Btu/hr: 80% Thrml | Not Input | NA | NA | NA | NA | NA
| System Oversizing Factor | NA | [13 empty] | NA | NA | Same as user model | Same as user model | Heating- 1.25 Cooling- 1.15 | Heating- NA Cooling- 1.15 | NA | NA | Heating- 1.25 Cooling- 1.15 | Not Input | NA | Heating- 1.25 Cooling- 1.15 | NA | NA | Heating- 1.25 Cooling- 1.15
| System Capacity | Heating Capacity - default Cooling Capacity - default | [13 empty] | Heating Capacity - default Cooling Capacity - default | Heating Capacity - default Cooling Capacity - default | Same as user model | Same as user model | Autosized with sizing factors | Autosized with sizing factors | Heating Capacity - default Cooling Capacity - default | Heating Capacity - default Cooling Capacity - default | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat | Not Input | NA | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat | Heating Capacity - default Cooling Capacity - default | Heating Capacity - default Cooling Capacity - default | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat
| Design Supply Air Temperature | Heating - 70 Cooling - 55 | [13 empty] | Heating - 60F Cooling - 55F | Heating - NA Cooling - 60F | Same as user model | Same as user model | Heating - 60F Cooling - 55F | Heating - NA Cooling - 60F | Air System Compliance Status: New (Top Floor West Perimeter Zone): Heating 95F Cooling - 55F Air System Compliance Status: Existing (All Other Zones): Heating - 60 Cooling - 55 | Air System Compliance Status: New (Top Floor West Perimeter Zone): Heating 95F Cooling - 55F Air System Compliance Status: Existing (All Other Zones): Heating - 60 Cooling - 55 | Air System Compliance Status: New (Top Floor West Perimeter Zone): Heating 95F Cooling - 55F Air System Compliance Status: Existing (All Other Zones): Heating - 60 Cooling - 55 | Not Input | Heating - 60 Cooling - 55 | Heating - 60 Cooling - 55 | Air System Compliance Status: New Heating - 60 Cooling - 55 | Air System Compliance Status: New Heating - 60 Cooling - 55 | Air System Compliance Status: New Heating - 60 Cooling - 55
| SAT Reset Control | Control System Type: DDCToZone WarmestResetFlowFirst High - 65 F Low - 55 F | [13 empty] | Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Same as user model | Same as user model | Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Air System Compliance Status: New (Top Floor West Perimeter Zone): No SAT Control (Htg/clg cycles on/off based on call from thermostat) Air System Compliance Status: Existing (All Other Zones): Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | Air System Compliance Status: New (Top Floor West Perimeter Zone): No SAT Control (Htg/clg cycles on/off based on call from thermostat) Air System Compliance Status: Existing (All Other Zones): Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | Air System Compliance Status: New (Top Floor West Perimeter Zone): No SAT Control (Htg/clg cycles on/off based on call from thermostat) Air System Compliance Status: Existing (All Other Zones): Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | Not Input | Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | Air System Compliance Status: New Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | Air System Compliance Status: New Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | Air System Compliance Status: New Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55
| Economizer | Bottom VAV - Integrated Mid VAV - NonIntegrated Top VAV - Integrated | [13 empty] | Bottom VAV - Integrated Mid VAV - NonIntegrated Top VAV - Integrated | Integrated | Same as user model | Same as user model | Bottom VAV - Integrated Mid VAV - Integrated Top VAV - Integrated | Integrated if load over 54 kBtu/h (If Economizer is specified) | Outside Air Control Compliance Status:: New (Top Floor West Perimeter Zone): None Outside Air Control Compliance Status:: Existing (All Other Zones): Bottom VAV - Integrated Mid VAV - NonIntegrated Top VAV - Integrated | Outside Air Control Compliance Status:: New (Top Floor West Perimeter Zone): None Outside Air Control Compliance Status:: Existing (All Other Zones): Bottom VAV - Integrated Mid VAV - NonIntegrated Top VAV - Integrated | Outside Air Control Compliance Status: New (Top Floor West Perimeter Zone): Integrated if load over 54 kBtu/h (If Economizer is specified) Outside Air Control Compliance Status: Existing (All Other Zones): Bottom VAV - Integrated Mid VAV - NonIntegrated Top VAV - Integrated | Not Input | Integrated if load over 54 kBtu/h (If Economizer is specified) | Integrated if load over 54 kBtu/h (If Economizer is specified) | Outside Air Control Compliance Status: New Bottom VAV - Integrated Mid VAV - NonIntegrated Top VAV - Integrated | Outside Air Control Compliance Status: New Bottom VAV - Integrated Mid VAV - NonIntegrated Top VAV - Integrated | Outside Air Control Compliance Status: New Bottom VAV - Integrated if load over 54 kBtu/h (If Economizer is specified) Mid VAV - Integrated if load over 54 kBtu/h (If Economizer is specified) Top VAV - Integrated if load over 54 kBtu/h (If Economizer is specified)
| Economizer Limits | Bottom VAV - Differential Enthalpy, high lockout 28.0 BTU/lb Mid VAV - Fixed Dry Bulb, high lockout 75 F Top VAV - Differential Dry bulb and enthlapy, high lockout 80 F, 28.0 BTU/lb | [13 empty] | Bottom VAV - Differential Enthalpy, high lockout 28.0 BTU/lb Mid VAV - Fixed Dry Bulb, high lockout 75 F Top VAV - Differential Dry bulb and enthlapy, high lockout 80 F, 28.0 BTU/lb | Differential Dry-Bulb | Bottom VAV - Differential Enthalpy, high lockout 80 F, 30.0 BTU/lb Mid VAV - Fixed Dry Bulb, high lockout 75 F Top VAV - Differential Dry bulb and enthlapy, high lockout 80 F, 30.0 BTU/lb | Same as user model | Bottom VAV - DifferentialDryBulb, Mid VAV - DifferentialDryBulb, Top VAV - DifferentialDrybulb, | Differential Dry-Bulb (If Economizer is specified) | Outside Air Control Compliance Status: New (Top Floor West Perimeter Zone): None Outside Air Control Compliance Status: Existing (All Other Zones): Bottom VAV - Differential Enthalpy, 28.0 BTU/lb Mid VAV - Fixed Dry Bulb, high lockout 75 F Top VAV - Differential Dry bulb and enthlapy, high lockout 80 F, 28.0 BTU/lb | Outside Air Control Compliance Status: New (Top Floor West Perimeter Zone): None Outside Air Control Compliance Status: Existing (All Other Zones): Bottom VAV - Differential Enthalpy, 30.0 BTU/lb Mid VAV - Fixed Dry Bulb, high lockout 75 F Top VAV - Differential Dry bulb and enthlapy, high lockout 80 F, 30.0 BTU/lb | Outside Air Control Compliance Status: New (Top Floor West Perimeter Zone): Differential Dry-Bulb (If Economizer is specified) Outside Air Control Compliance Status: Existing (All Other Zones): Bottom VAV - Differential Enthalpy, high lockout 80 F, 30.0 BTU/lb Mid VAV - Fixed Dry Bulb, high lockout 75 F Top VAV - Differential Dry bulb and enthlapy, high lockout 80 F, 30.0 BTU/lb | Not Input | Differential Dry-Bulb (If Economizer is specified) | Differential Dry-Bulb (If Economizer is specified) | Outside Air Control Compliance Status: New Bottom VAV - Differential Enthalpy, 28.0 BTU/lb Mid VAV - Fixed Dry Bulb, high lockout 75 F Top VAV - Differential Dry bulb and enthlapy, high lockout 80 F, 28.0 BTU/lb | Outside Air Control Compliance Status: New Bottom VAV - Differential Enthalpy, 30.0 BTU/lb Mid VAV - Fixed Dry Bulb, high lockout 75 F Top VAV - Differential Dry bulb and enthlapy, high lockout 80 F, 30.0 BTU/lb | Outside Air Control Compliance Status: New Bottom VAV - Differential Dry-Bulb (If Economizer is specified) Mid VAV - Differential Dry-Bulb (If Economizer is specified) Top VAV - Differential Dry-Bulb (If Economizer is specified)
| Fan Power Specification | Brake Horsepower Bottom VAV - 14.085 Mid VAV - 13 Top VAV - 18.175 | [13 empty] | Bottom VAV: Brake Horsepower Method: 6.21 bhp 0.9 Motor Eff Mid VAV: Static Pressure Method: 3 in H2O 0.650 Fan Eff 0.90 Motor Eff 7.89 bhp (For Reference only) Top VAV: Static Pressure Method: 3.5 in H2O 0.60 Fan Eff 0.90 Motor Eff 9.38 bhp (For Reference only) | Brake Horsepower Method: 9.5 bhp 0.917 Motor Eff | Same as user model | Same as user model | Bottom VAV, Mid VAV and Top VAV: Static Pressure Method: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | PowerPerUnitFlow: 0.49 W/cfm | Fan Compliance Status: New (Top Floor West Perimeter Zone): Brake Horsepower 1.23bhp 0.865 Motor Eff Fan Compliance Status: Existing (All Other Zones): Brake Horsepower Bottom VAV: 20.45 bhp 0.936 Motor Eff Mid VAV: 20.80 bhp 0.936 Motor Eff Top VAV: 18.76 bhp 0.93 Motor Eff | Fan Compliance Status: New (Top Floor West Perimeter Zone): Brake Horsepower 1.23 bhp 0.865 Motor Eff Fan Compliance Status: Existing (All Other Zones): Brake Horsepower Bottom VAV: 20.45 bhp 0.936 Motor Eff Mid VAV: 20.80 bhp 0.936 Motor Eff Top VAV: 18.76 bhp 0.93 Motor Eff | Static Pressure Method: Fan Compliance Status: New (Top Floor West Perimeter Zone): The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Fan Compliance Status: Existing (All Other Zones): Brake Horsepower Bottom VAV: 20.45 bhp 0.936 Motor Eff Mid VAV: 20.80 bhp 0.936 Motor Eff Top VAV: 18.76 bhp 0.93 Motor Eff | Not Input | Static Pressure Method: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | Static Pressure Method: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | Fan Compliance Status: New Bottom VAV: Brake Horsepower Method: 14.085 bhp 0.9 Motor Eff Mid VAV: Static Pressure Method: 3 in H2O 0.650 Fan Eff 0.90 Motor Eff 13.0 bhp (For Reference only) Top VAV: Static Pressure Method: 4 in H2O 0.62 Fan Eff 0.90 Motor Eff 18.2 bhp (For Reference only) | Fan Compliance Status: New Bottom VAV: Brake Horsepower Method: 14.085 bhp 0.9 Motor Eff Mid VAV: Static Pressure Method: 3 in H2O 0.650 Fan Eff 0.90 Motor Eff 13.002 bhp (For Reference only) Top VAV: Static Pressure Method: 4 in H2O 0.62 Fan Eff 0.90 Motor Eff 18.2 bhp (For Reference only) | Fan Compliance Status: New Bottom VAV, Mid VAV and Top VAV: Static Pressure Method: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3
| Motor Horsepower | Bottom VAV - 15 Mid VAV - 15 Top VAV - 20 | [13 empty] | Bottom VAV - 7.5 Mid VAV - 10 Top VAV - 10 | 10 | Same as user model | Same as user model | Bottom VAV, Mid VAV and Top VAV: Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 |  | Fan Compliance Status: New (Top Floor West Perimeter Zone): 1.5 Fan Compliance Status: Existing (All Other Zones): Bottom VAV - 25 Mid VAV - 25 Top VAV - 20 | Fan Compliance Status: New (Top Floor West Perimeter Zone): 1.5 Fan Compliance Status: Existing (All Other Zones): Bottom VAV - 25 Mid VAV - 25 Top VAV - 20 | Fan Compliance Status: New (Top Floor West Perimeter Zone): Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Fan Compliance Status: Existing (All Other Zones): Bottom VAV - 25 Mid VAV - 25 Top VAV - 20 | Not Input | Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | Fan Compliance Status: New Bottom VAV - 15 Mid VAV - 15 Top VAV - 20 | Fan Compliance Status: New Bottom VAV - 15 Mid VAV - 15 Top VAV - 20 | Fan Compliance Status: New Bottom VAV, Mid VAV and Top VAV: Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3
| Fan Control Method | Variable flow, VSD | [13 empty] | Variable flow, VSD | Constant Volume | Same as user model | Same as user model | Variable flow, VSD | Constant-speed if load<= 17.5kW; Variable flow, VSD if > 17.5kW | Fan Compliance Status: New (Top Floor West Perimeter Zone): Constant Volume Fan Compliance Status: Existing (All Other Zones): Variable flow(VSD) | Fan Compliance Status: New (Top Floor West Perimeter Zone): Constant Volume Fan Compliance Status: Existing (All Other Zones): Variable flow(VSD) | Fan Compliance Status: New (Top Floor West Perimeter Zone): Constant Volume Fan Compliance Status: Existing (All Other Zones): Variable flow(VSD) | Not Input | VariableSpeedDrive | VariableSpeedDrive | Fan Compliance Status: New ConstantVolume | Fan Compliance Status: New ConstantVolume | Fan Compliance Status: New VariableSpeedDrive
| Cooling Coil Curve(s) | Not Input (DXEIR_fTempCrvRef) (DXEIR_fPLFCrvRef) (DXEIR_fFlowCrvRef) | [13 empty] | Not input | Not input | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio | Not Input | Air System Compliance Status: New (Top Floor West Perimeter Zone): CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio Air System Compliance Status: Existing (All Other Zones): CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Air System Compliance Status: New (Top Floor West Perimeter Zone): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio Air System Compliance Status: Existing (All Other Zones): CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Not Input | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio | Not Input | Air System Compliance Status: New CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Air System Compliance Status: New CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio
| Heating Coil Curve(s) | Not Input (FurnHIR_fPLRCrvRef) | [13 empty] | NA | NA | NA | NA | NA | NA | Not Input | Air System Compliance Status: New (Top Floor West Perimeter Zone): CoilHtgFurnFIRRatio_fQRatio | Air System Compliance Status: New (Top Floor West Perimeter Zone): CoilHtgFurnFIRRatio_fQRatio
| Fan Part-load Performance Curve | Not Input | [13 empty] | Not input | None (Constant Volume) | Variable flow, VSD with Static Pressure Reset FanVSDGoodSpResetPwrRatio_fCFMRatio | None (Constant Volume) | Variable flow, VSD with Static Pressure Reset FanVSDGoodSpResetPwrRatio_fCFMRatio | Variable flow, FanVSDPerfSpResetPwrRatio_fCFMRatio | Perimeter_top_ZN_4 New AirSys: None (Constant Volume) Bottom VAV, Mid VAV and Top VAV: Not Input | Perimeter_top_ZN_4 New AirSys (New): None (Constant Volume) Bottom VAV, Mid VAV and Top VAV (Existing): Variable flow, VSD with Static Pressure Reset FanVSDGoodSpResetPwrRatio_fCFMRatio | Perimeter_top_ZN_4 New AirSys (New): None (Constant Volume) Bottom VAV, Mid VAV and Top VAV (Existing): Variable flow, VSD with Static Pressure Reset FanVSDGoodSpResetPwrRatio_fCFMRatio | Not Input | BaseAIrSys5, BaseAIrSys5-2, BaseAIrSys5-3 (New): Variable flow, VSD with Static Pressure Reset FanVSDGoodSpResetPwrRatio_fCFMRatio Base Relief Fans (All): FanVSDPwrRatio_fCFMRatio | BaseAIrSys5, BaseAIrSys5-2, BaseAIrSys5-3 (New): Variable flow, VSD with Static Pressure Reset FanVSDGoodSpResetPwrRatio_fCFMRatio Base Relief Fans (All): FanVSDPwrRatio_fCFMRatio | Not Input | None (Constant Volume) | BaseAIrSys5, BaseAIrSys5-2, BaseAIrSys5-3 (New): Variable flow, VSD with Static Pressure Reset FanVSDGoodSpResetPwrRatio_fCFMRatio Base Relief Fans (All): FanVSDPwrRatio_fCFMRatio
| HVAC(Availability/Fan) Schedule | Not Input | [13 empty] | Not Input | Not Input | OfficeHVACAvail | DataHVACAvail | OfficeHVACAvail | DataHVACAvail | Not Input | OfficeHVACAvail | OfficeHVACAvail | Not Input | OfficeHVACAvail | OfficeHVACAvail | Not Input | OfficeHVACAvail | OfficeHVACAvail
| Cooling Thermostat Schedule | Not Input | [13 empty] | Not Input | Not Input | OfficeClgSetpt | DataClgSetpt | OfficeClgSetpt | DataClgSetpt | Not Input | OfficeClgSetPt | OfficeClgSetPt | Not Input | OfficeClgSetPt | OfficeClgSetPt | Not Input | OfficeClgSetPt | OfficeClgSetPt
| Heating Thermostat Schedule | Not Input | [13 empty] | Not Input | Not Input | OfficeHtgSetpt | DataHtgSetpt | OfficeHtgSetpt | DataHtgSetpt | Not Input | OfficeHtgSetPt | OfficeHtgSetPt | Not Input | OfficeHtgSetPt | OfficeHtgSetPt | Not Input | OfficeHtgSetPt | OfficeHtgSetPt
| Terminal Heat Type | Hot Water | [13 empty] | Hot Water | NA | Same as user model | Same as user model | Hot Water | NA | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): NA Coil Heating Compliance Status: Existing (All Other Zones): Hot Water | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): NA Coil Heating Compliance Status: Existing (All Other Zones): Hot Water | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): NA Coil Heating Compliance Status: Existing (All Other Zones): Hot Water | Not Input | Hot Water | Hot Water | Hot Water | Hot Water | Hot Water
| Terminal Heat Capacity | Default | [13 empty] | Default | NA | Default | Same as user model | Default | NA | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): NA Coil Heating Compliance Status: Existing (All Other Zones):Default | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): NA Coil Heating Compliance Status: Existing (All Other Zones):Default | Coil Heating Compliance Status: New (Top Floor West Perimeter Zone): NA Coil Heating Compliance Status: Existing (All Other Zones):Default | Not Input | Default | Default | Default | Default | Default
| Terminal Unit Fan Power | NA | [13 empty] | Not Input | NA | Same as user model | Same as user model | Default | NA | NA | NA | NA | Not Input | NA | NA | Not Input | NA | NA
| Reheat Delta T | NA | [13 empty] | NA | NA | Same as user model | Same as user model | NA | NA | NA | NA | NA | Not Input | NA | NA | Not Input | NA | NA
Boiler Components
| Number of boilers | 1 | [14 empty] | Computer room system not served by HW plant |  | Computer room system not served by HW plant |  | Computer room system not served by HW plant | Boiler Compliance Status: Existing Qty: 1 | Boiler Compliance Status: Existing Qty: 1 | Boiler Compliance Status: Existing Qty: 1 | Not Input | 2 | 2 | Boiler Compliance Status: New Qty: 1 | Boiler Compliance Status: New Qty: 1 | Boiler Compliance Status: New Qty: 2
| Boiler Capacity (btuh) | 1700000 | [19 empty] | Boiler Compliance Status: Existing 600,000 | Boiler Compliance Status: Existing 600,000 | Boiler Compliance Status: Existing 600,000 | Not Input | 311701 | 323366 | Boiler Compliance Status: New 700,000 | Boiler Compliance Status: New 700,000 | Boiler Compliance Status: New 240,522
| Boiler Efficiency | 0.8 | [19 empty] | 0.8 | 0.8 | 0.8 | Not Input | 0.8225 | 0.8 | 80% | 80% | 0.8225 (82% AFUE)
| Boiler Type | Hot Water Boiler | [19 empty] | Hot Water | Hot Water | Hot Water | Not Input | Hot Water | Hot Water | Hot Water | Hot Water | Hot Water
| Boiler Heat Loss | 0 | [22 empty] | Not Input
| Boiler Performance Curve | Default Curve (HIR_fPLRCrvRef) | [19 empty] | Not Input | BlrHWBlrFIRRatio_fQRatioSI | BlrHWBlrFIRRatio_fQRatioSI | Not Input | BlrHWBlrFIRRatio_fQRatioSI | BlrHWBlrFIRRatio_fQRatioSI | Not Input | BlrHWBlrFIRRatio_fQRatioSI | BlrHWBlrFIRRatio_fQRatioSI
| Boiler Min. Unloading Ratio | 25% | [19 empty] | 0.25 | 0.25 | 0.25 | Not Input | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Hot Water Supply Temperature | 180F | [19 empty] | 180F | 180F | 180F | Not Input | 180F | 180F | 180F | 180F | 180F
| Hot Water Return Temperature | 140F | [19 empty] | 140F | 140F | 140F | Not Input | 140F | 140F | 140F | 140F | 140F
| Pump Control Type | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow | [19 empty] | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow | Not Input | OnDemand | OnDemand | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow
| Pump Power | [20 empty] | 0.538 kW (17.9 W/gpm) (For Reference only, Not specified in the ACM) Design Flow Rate: 30 gpm Pump Head: 60 ft H20 Impeller Efficiency: 0.7 Name Plate HP: 0.8 hp | 0.59 kW (19.68 W/gpm) (MotorBHP calculated for pump 'HotWater Pump' using user inputs is less than the ACM required value for the user specified MotorHP. The Proposed TotHd revised to 65.86 ft for compliance analysis) | 0.59 kW (19.68 W/gpm) | Not Input | 0.296 kW (19 W/gpm) | (19 W/gpm) | 0.627 kW (17.9 W/gpm) (For Reference only, Not specified in the ACM Design Flow Rate: 35 gpm Pump Head: 60 ft H20 Impeller Efficiency: 0.7) | 1.18 (33.74 W/gpm) (MotorBHP calculated for pump 'HotWater Pump' using user inputs is less than the ACM required value for the user specified MotorHP. The Proposed TotHd revised to 112.9 ft for compliance analysis) | (19 W/gpm)
| Pump Motor Efficiency | 0.9 | [19 empty] | 0.9 | 0.9 | 0.9 | Not Input | 0.855 | 0.855 | 0.9 | 0.9 | 0.855
| Pump Part Load Curve | Not Input
Chiller Components
| Chiller Type | NA
| Number of Chillers | NA
| Chiller Fuel | NA
| Chiller Oversizing Factor | NA
| Chiller Capacity (tons) | NA
| Chiller Efficiency | NA
| Chiller Part-Load Efficiency (IPLV) | NA
| Chiller Min. Unloading Ratio | NA
| Chiller Cooling Capacity Adjustment Curve | NA
| Chiller Cooling Efficiency Adjustment Curve | NA
| Chilled Water Supply Temperature | NA
| Chilled Water ReturnTemperature | NA
| Condensor Type | NA
| Cooling tower Fan Control Type | NA
| Cooling Tower Fan Horse Power | NA
| Cooling Tower Set Point Control | NA
| Chiller, Condenser Pump Control Type | NA
| Chiller, Condenser Pump Motor Power | NA
| Chiller, Condenser Pump Motor Efficiency | NA
| Chiller, Condenser Pump Design Flow | NA
Service Hot Water
| SWH type | Storage | WtrHtr:Type
| Fuel type | Natural Gas | WtrHtr:FuelSrc
| Thermal Efficiency | 85% | WtrHtr:ThrmlEff
| Energy Factor | 77% | WtrHtr:EF
| Hot Water Load/person (gal/h-person) | 0.18 | Spc:HotWtrHtgRt
| SHW Schedule |  | Spc:HotWtrHtgSchRef
| Tank Volume (gal) | 140 | WtrHtr:StorCap
| Availability Schedule | Not Input | FluidSys:AvailSchRef
| Water temperature setpoint Schedule | Fixed | FluidSys:TempCtrl
| Water temperature setpoint | 120 | FluidSys:FixedSupTemp
| Water Heater Max Capacity (Btuh) | 80000 | WtrHtr:CapRtd
| Performance Curve | Not Input | WtrHtr:HIR_fPLRCrvRef
| Standby Loss (Btuh) | 1271 | WtrHtr:StbyLoss
Note on J61: Sandeep: Value returned in baseline is 0.75, UNSURE this is accurate
Note on H65: John Arent: Change units to gph/person as needed.
Note on I65: John Arent: Change units to gph/person as needed.
Note on V90: David Reddy: See GC Issue 301
Note on Q98: David Reddy: See GC Issue 238
Note on B108: Nambiar, Chitra: Sizing will be at either system or plant level, not both.
Note on B113: Nambiar, Chitra: This input is not an option in E+ HVAc Template:Plant:Boiler object.

## Large Office
Key:
| Base PrototypeTest Parameters | Most General parameters of prototype building. Specific test instances to be generated based on this model.
| Not Part of Test Case | Not Specified - Not Part of Test Case
| Test Instance Specification Incomplete | Updates to test instance specfication in progress
| Test Instance Specification Complete | Updates to test instance specification have been completed
| Daylighting (Detailed Geometry Models Only) | Exclude Testing/Verification of Daylighting Parameters in Simplified Geometry Models
|  | Large Office General Prototype | Relevant SDD Properties | 040006-OffLrg-Run05 |  |  | 040006-OffLrg-Run06 |  |  | 040006-OffLrg-Run11 | [17 empty] | Run17 - INCOMPLETE |  |  | 040006-OffLrg-Run20
|  | User model |  | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | [5 empty] | Proposed Model | [5 empty] | Baseline Model | [5 empty] | User Model | Proposed Model | Baseline model | User Model |  | Proposed Model |  | Baseline model
Building Type |  |  |  | Large Office |  |  | Large Office |  |  | Large Office | [5 empty] | Large Office | [5 empty] | Large Office | [5 empty] | Large Office | Large Office | Large Office | Large Office (Basement floor is a data center)
Vintage |  |  |  | New Construction |  |  | New Construction |  |  | New Construction | [5 empty] | New Construction | [5 empty] | New Construction | [8 empty] | New Construction
Climate Zone |  |  |  | CZ-6 |  |  | CZ-6 |  |  | CZ-6 | [5 empty] | CZ-6 | [5 empty] | CZ-6 | [5 empty] | CZ-6 | CZ-6 | CZ-6 | CZ-6
Geometry | [30 empty] | All Above Grade Floors | Basement Floor | All Above Grade Floors | Basement Floor | All Above Grade Floors | Basement Floor
| Total Floor Area (sq feet) | 498,600 (240 ft x 160 ft)
| Aspect Ratio | 1.5
| Number of Floors | 13 (including basement)
| Azimuth | 0
| Thermal Zoning | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 33%, Core 67%
| Floor to floor height (feet) | 19
| Floor to ceiling height (feet) | 9
| Roof Dimensions | Based on floor area and aspect ratio
| Roof Tilt and Orientation | horizontal
| Foundation Dimensions | Based onfloor area and aspect ratio
| Window Fraction (Window to Wall Ratio) | 40% of above-grade gross walls 37.5% of gross walls (including the below-grade walls) |  | Overall: 52% North: 52% East: 52% South: 52% West: 52% | Overall: 52% North: 52% East: 52% South: 52% West: 52% | Overall: 40% North: 40% East: 40% South: 40% West: 40% | Overall: 46% North: 50% East: 45% South: 39% West: 50% | Overall: 46% North: 50% East: 45% South: 39% West: 50% | Overall: 40% North: 45% East: 40% South: 35% West: 40%
| Window Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glazing Sill Height (feet) | 3
| Window Location | evenly distributed along four façades
| Skylight Fraction (Skylight to Roof Ratio) | NA
| Skylight Dimensions | NA
| Skylight Locations | NA
Envelope Components
| Roof Construction Assembly Type Slope Category | Metal Frame Roof (Wood Frame and Other), horizontal
| Roof Construction Assembly overall U value | 0.065
| Roof Construction Assembly layers | WoodFramingAndOtherRoofU065: Metal Deck - 1/16 in. Expanded Polystyrene - EPS - 3 1/2.
| Roof Aged Solar Reflectance (Solar Absorptance) | 0.63
| Roof Aged Thermal emittance (Thermal Absorptance) | 0.75
| Exterior Wall Construction Assembly Type | Metal Framed
| Exterior Wall Construction Assembly overall U value | 0.068
| Exterior Wall Construction Assembly layers | MetalFrameWallU068: 1. Stucco - 7/8 in., 2. Building Paper - 1/16 in. 3. Expanded Polystyrene - EPS - 3in. 4. Air - Metal Wall Framing - 16 or 24 in. OC 5. Gypsum Board - 1/2 in.
| Above-grade Floor Construction Assembly Type | NA (Slab-on grade)
| Above-grade Floor Construction Assembly overall U value | NA
| Above-grade Floor Construction Assembly layers | NA
| On/Below Grade Floor F-factor Total Perimeter Area Total Perimeter exposed | 0.69, 35352.97 ft2, 799.51 ft
| Vertical Window Type | Fixed
| Window assembly U value | CZ-6 Standard Design "Fixed Window" U-0.26
| Window SHGC | CZ-6 Standard Design "Fixed Window" SHGC-0.25
| Window VT | CZ-6 Standard Design "Fixed Window" VT-0.42
| Window overhang | None
| Skylight overall U value | NA
| Skylight SHGC | NA
| Skylight VT | NA
| Daylit Area (calculated value) | Calculated by Software According to ACM section 5.4.5
Internal Load Components
| Occupancy Type | Office (Greater than 250 square feet in floor area) | Spc:SpcFunc | [6 empty] | Level -1, Core and North, West Perimeter Zones - Retail Merchandise Sales, Wholesale Showroom | Levels - 2 to 6 Core and South, West, North Perimeter Zones - Medical and Clinical Care | Basement and Levels - 7 to 11 Core and South, West, North Perimeter Zones - Office (Greater than 250 square feet in floor area) | Level - 12 Core and South, West, North Perimeter Zones - Convention, Conference, Multipurpose and Meeting Center Areas | Levels - 1 to 12 East Perimeter Zone - Corridors, Restrooms, Stairs, and Support Areas | Level -1, South Perimeter Zone - Lobby, Main Entry | Level -1, Core and North, West Perimeter Zones - Retail Merchandise Sales, Wholesale Showroom | Levels - 2 to 6 Core and South, West, North Perimeter Zones - Medical and Clinical Care | Basement and Levels - 7 to 11 Core and South, West, North Perimeter Zones - Office (Greater than 250 square feet in floor area) | Level - 12 Core and South, West, North Perimeter Zones - Convention, Conference, Multipurpose and Meeting Center Areas | Levels - 1 to 12 East Perimeter Zone - Corridors, Restrooms, Stairs, and Support Areas | Level -1, South Perimeter Zone - Lobby, Main Entry | Level -1, Core and North, West Perimeter Zones - Retail Merchandise Sales, Wholesale Showroom | Levels - 2 to 6 Core and South, West, North Perimeter Zones - Medical and Clinical Care | Basement and Levels - 7 to 11 Core and South, West, North Perimeter Zones - Office (Greater than 250 square feet in floor area) | Level - 12 Core and South, West, North Perimeter Zones - Convention, Conference, Multipurpose and Meeting Center Areas | Levels - 1 to 12 East Perimeter Zone - Corridors, Restrooms, Stairs, and Support Areas | Level -1, South Perimeter Zone - Lobby, Main Entry
| People Density | 200 ft2/person | Spc:OccDens | [6 empty] | 60 ft2/person | 200 ft2/person | 200 ft2/person | 30 ft2/person | 200 ft2/person | 30 ft2/person | 60 ft2/person | 200 ft2/person | 200 ft2/person | 30 ft2/person | 200 ft2/person | 30 ft2/person | 60 ft2/person | 200 ft2/person | 200 ft2/person | 30 ft2/person | 200 ft2/person | 30 ft2/person
| Sensible Heat/person | 250 Btu/h-person | Spc:OccSensHtRt | [6 empty] | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 245 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 245 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 245 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant
| Latent Heat/person | 200 Btu/h-person | Spc:OccLatHtRt | [6 empty] | 200 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 155 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 155 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 200 Btu/occupant | 155 Btu/occupant | 250 Btu/occupant | 250 Btu/occupant
| Equipment Power Density | 1.34 W/ft2 | Spc:RecptPwrDens | [6 empty] | 2 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | 1 W/ft2 | 0.2 W/ft2 | 0.5 W/ft2 | 1 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | 1 W/ft2 | 0.2 W/ft2 | 0.5 W/ft2 | 1 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | 1 W/ft2 | 0.2 W/ft2 | 0.5 W/ft2
| Lighting Power Density | 0.8 (Int LPD reg.) | Spc:IntLPDReg Spc:IntLtgSpecMthd Spc:IntLtgSys:TailoredMthdAllowType Spc:TMGenLPD Spc:TMTotAllowLPD | [6 empty] | 1W/ft2 | 1 W/ft2 | 0.75 W/ft2 | 1.2 W/ft2 | 0.5 W/ft2 | 0.95 W/ft2 | 1W/ft2 | 1 W/ft2 | 0.75 W/ft2 | 1.2 W/ft2 | 0.5 W/ft2 | 0.95 W/ft2 | 1.2 W/ft2 | 1.2 W/ft2 | 0.75 W/ft2 | 1.2 W/ft2 | 0.6 W/ft2 | 0.95 W/ft2
| Ventilation Rate Per Person | - | Spc:VentRt | [6 empty] | 15 cfm/Person | 15 cfm/Person | Core_hi: 0 All Other spaces:15 cfm/Person | 15 cfm/Person | Perimeter_hi_ZN_2: 0 (Unconditioned Space) All other Spaces:15 cfm/Person | 15 cfm/Person | 15 cfm/Person | 15 cfm/Person | Core_hi: 0 All Other spaces:15 cfm/Person | 15 cfm/Person | Perimeter_hi_ZN_2: 0 (Unconditioned Space) All other Spaces:15 cfm/Person | 15 cfm/Person
| Ventilation Rate Per Area | - | [7 empty] | 0.2 cfm/ft2 | 0.2 cfm/ft2 | Core_hi: 0.162 cfm/ft2 (4415 cfm) All Other spaces: 0.15 cfm/ft2 | 0.15 cfm/ft2 | Perimeter_hi_ZN_2: 0 (Unconditioned Space) All other Spaces: 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.2 cfm/ft2 | 0.2 cfm/ft2 | Core_hi: 0.162 cfm/ft2 (4415 cfm) All Other spaces: 0.15 cfm/ft2 | 0.15 cfm/ft2 | Perimeter_hi_ZN_2: 0 (Unconditioned Space) All other Spaces: 0.15 cfm/ft2 | 0.15 cfm/ft2
| Simulated Ventilation Rate | - | [7 empty] | Max value of 'Ventilation Rate Per Person' and 'Ventilation Rate Per Area' | [5 empty] | Max value of 'Ventilation Rate Per Person' and 'Ventilation Rate Per Area' | [5 empty] | 0.25 cfm/ft2 | 0.152 cfm/ft2 | Core_hi: 0.162 cfm/ft2 All Other spaces: 0.15 cfm/ft2 | 0.50 cfm/ft2 | Perimeter_hi_ZN_2: 0 (Unconditioned Space) Perimeter_mid_ZN_2: 0.11 All other Spaces 0.15 cfm/ft2 | 0.50 cfm/ft2
| Infiltration Rate | 0.0448 cfm/ft2
| Infiltration Schedule | Not Input | Spc:InfSchRef
| Infiltration Method | FlowExteriorWallArea
| Elevator Power | NA
| Occupancy Schedule |  | Spc:OccSchRef | [12 empty] | RetailOccupancy | HealthOccupancy | OfficeOccupancy | AssemblyOccupancy | Level 1: RetailOccupancy Level 2-6: HealthOccupancy Level 7-11: OfficeOccupancy Level 12: AssemblyOccupancy | RetailOccupancy | RetailOccupancy | HealthOccupancy | OfficeOccupancy | AssemblyOccupancy | Level 1: RetailOccupancy Level 2-6: HealthOccupancy Level 7-11: OfficeOccupancy Level 12: AssemblyOccupancy | RetailOccupancy
| Equipment Schedule |  | Spc:RecptSchRef | [12 empty] | RetailReceptacle | HealthReceptacle | OfficeReceptacle | AssemblyReceptacle | Level 1: RetailReceptacle Level 2-6: HealthReceptacle Level 7-11: OfficeReceptacle Level 12: AssemblyReceptacle | RetailReceptacle | RetailReceptacle | HealthReceptacle | OfficeReceptacle | AssemblyReceptacle | Level 1: RetailReceptacle Level 2-6: HealthReceptacle Level 7-11: OfficeReceptacle Level 12: AssemblyReceptacle | RetailReceptacle
| Lighting Schedule |  | Spc:IntLtgRegSchRef | [12 empty] | RetailLights | HealthLights | OfficeLights | AssemblyLights | Level 1: RetailLights Level 2-6: HealthLights Level 7-11: OfficeLights Level 12: AssemblyLights | RetailLights | RetailLights | HealthLights | OfficeLights | AssemblyLights | Level 1: RetailLights Level 2-6: HealthLights Level 7-11: OfficeLights Level 12: AssemblyLights | RetailLights
| Elevator Schedule |  | Spc:InfSchRef
Daylighting
| Illuminance Setpoint | 287.5 lux | Spc:PriSideDayltgIllumSetPt
| Daylight Control Type | Continuous | ThrmlZn:DayltgCtrlType
| Controlled General Lighting Power In Primary Daylit Area | Defaulted: Lighting Power Density*(Daylit Area/Total Area) | ThrmlZn:PriSideDayltgCtrlLtgPwr
| Controlled General Lighting Power In Secondary Daylit Area | NA | ThrmlZn:SecSideDayltgCtrlLtgPwr
| Controlled General Lighting Power In Skylit Daylit Area | NA | ThrmlZn:SkylitDayltgCtrlLtgPwr
| Reference Position 1 | Calculated by Software According to ACM section 5.4.5
| Reference Position 2 | Calculated by Software According to ACM section 5.4.5
HVAC Components | [30 empty] | Office | Data Center | Office | Data Center | Office | Data Center
| HVAC System Type | Built-up VAV with Reheat | [28 empty] | Built-up VAV with Reheat | SZAC | Built-up VAV with Reheat | SZAC | VAV with Reheat (System 6) | CRAH Unit (SZVAVAC) (System 10)
| Heating Type | Fossil Fuel | [28 empty] | Hot Water boiler with reheat | None | Same as user model | Same as user model | Hot Water boiler with reheat | None
| Cooling Type | Chilled Water | [28 empty] | Chilled Water | Direct Expansion (DX) | Same as user model | Same as user model | Chilled Water | Chilled Water
| Cooling Efficiency | NA | [28 empty] | NA | EER-11.4 IEER-13.16 (COP - 3.34 for reference, not input) | NA | Same as user model | NA | NA
| Heating Efficiency | NA | [28 empty] | NA | NA | NA | NA | NA | NA
| System Oversizing Factor | NA | [28 empty] | NA | NA | NA | NA | Heating- 1.25 Cooling- 1.15 | Heating- NA Cooling- 1.15
| System Capacity | Heating Capacity- Default Cooling Capacity- Default | [28 empty] | Heating Capacity - default Cooling Capacity - default | Heating Capacity - default Cooling Capacity - default | Heating Capacity - default Cooling Capacity - default | Heating Capacity - default Cooling Capacity - default | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat
| Design Supply Air Temperature | Heating- 70F Cooling- 55F | [28 empty] | Heating- 60F Cooling- 55F | Heating - NA Cooling - 60F | Same as user model | Same as user model | Heating - 60F Cooling - 55F | Heating - 95F Cooling - 60F
| SAT Reset Control | WarmestResetFlowFirst High - 70 F Low - 55 F | [28 empty] | Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Same as user model | Same as user model | Control System Type: DDCToZone WarmestResetFlowFirst Heating - 60 Cooling - 55 | No SAT Control (Htg/clg cycles on/off based on call from thermostat)
| Economizer | Integrated | [28 empty] | Integrated | None | Same as user model | Same as user model | Integrated if load over 54 kBtu/h (If Economizer is specified) | Integrated if load over 54 kBtu/h (If Economizer is specified)
| Economizer Limits | Differential Dry Bulb | [28 empty] | Differential Dry-Bulb | NA | Same as user model | Same as user model | Differential Dry-Bulb (If Economizer is specified) | Differential Dry-Bulb (If Economizer is specified)
| Fan Power Specification | Brake Horsepower Basement - 33 Bottom - 42.3 Hi - 46 Mid - 46 Top - 44.65 | [28 empty] | Static Pressure Method: BaseAirSys6-Bot 4.5 in H2O 0.62 Fan Eff 0.945 Motor Eff BaseAirSys6-Mid 4.5 in H2O 0.62 Fan Eff 0.945 Motor Eff BaseAirSys6-Hi 4.5 in H2O 0.62 Fan Eff 0.945 Motor Eff BaseAirSys6-Top 4.5 in H2O 0.62 Fan Eff 0.945 Motor Eff | Static Pressure Method: BsmntZnPSZ AirSys 3.5 in H2O 0.62 Fan Eff 0.962 Motor Eff | Static Pressure Method: BaseAirSys6-Bot 4.5 in H2O 0.62 Fan Eff 0.95 Motor Eff BaseAirSys6-Mid 4.5 in H2O 0.62 Fan Eff 0.945 Motor Eff BaseAirSys6-Hi 4.5 in H2O 0.62 Fan Eff 0.945 Motor Eff BaseAirSys6-Top 4.5 in H2O 0.62 Fan Eff 0.945 Motor Eff | Static Pressure Method: BsmntZnPSZ AirSys 3.5 in H2O 0.62 Fan Eff 0.962 Motor Eff | BaseAirSys6-Bot, BaseAirSys6-Mid, BaseAirSys6-Hi and BaseAirSys6-Top: Static Pressure Method: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | PowerPerUnitFlow Method: BaseAirSys10 0.49 W/cfm
| Motor Horsepower | Basement - 40 Bottom - 50 Hi - 50 Mid - 50 Top - 50 | [28 empty] | BaseAirSys6-Bot 50 BaseAirSys6-Mid 50 BaseAirSys6-Hi 50 BaseAirSys6-Top 50 | BsmntZnPSZ AirSys 200 | BaseAirSys6-Bot 50 BaseAirSys6-Mid 50 BaseAirSys6-Hi 50 BaseAirSys6-Top 50 | BsmntZnPSZ AirSys 200 | BaseAirSys6-Bot, BaseAirSys6-Mid, BaseAirSys6-Hi and BaseAirSys6-Top: Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3
| Fan Control Method | Variable-flow, VSD | [28 empty] | Variable-flow, VSD | Constant Volume | Same as user model | Same as user model | Variable-flow, VSD | Variable-flow, VSD
| Cooling Coil Curve(s) | Not Input (DXEIR_fTempCrvRef) (DXEIR_fPLFCrvRef) (DXEIR_fFlowCrvRef) | [28 empty] | Not input | Not input | Same as user model | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | NA | NA
| Heating Coil Curve(s) | Not Input | [28 empty] | Not input | Not input | Same as user model | Same as user model | NA | NA
| Fan Part-load Performance Curve | Not Input
| HVAC(Availability/Fan) Schedule | Not Input (FurnHIR_fPLRCrvRef) | [28 empty] | Not input | Not input | OfficeHVACAvail | DataHVACAvail | OfficeHVACAvail | DataHVACAvail
| Cooling Thermostat Schedule | Not Input | [7 empty] | Not Input | Not Input | Not Input | Not Input | Not Input | Not Input | RetailClgSetPt | HealthClgSetPt | OfficeClgSetPt | AssemblyClgSetPt | OfficeClgSetPt | RetailClgSetPt | RetailClgSetPt | HealthClgSetPt | OfficeClgSetPt | AssemblyClgSetPt | OfficeClgSetPt | RetailClgSetPt |  |  |  | Not input | Not input | OfficeClgSetPt | DataClgSetpt | OfficeClgSetPt | DataClgSetpt
| Heating Thermostat Schedule | Not Input | [7 empty] | Not Input | Not Input | Not Input | Not Input | Not Input | Not Input | RetailHtgSetPt | HealthHtgSetPt | OfficeHtgSetPt | AssemblyHtgSetPt | OfficeHtgSetPt | RetailHtgSetPt | RetailHtgSetPt | HealthHtgSetPt | OfficeHtgSetPt | AssemblyHtgSetPt | OfficeHtgSetPt | RetailHtgSetPt |  |  |  | Not input | Not input | OfficeHtgSetPt | DataHtgSetpt | OfficeHtgSetPt | DataHtgSetpt
| Terminal Heat Type | Hot Water | [28 empty] | Hot Water | NA | Same as user model | Same as user model | Hot Water | NA
| Terminal Heat Capacity | Default | [28 empty] | Default | NA | Same as user model | Same as user model | Default | NA
| Terminal Unit Fan Power | NA | [28 empty] | Not Input | NA | Same as user model | Same as user model | See model | NA
| Reheat Delta T | NA | [28 empty] | Not Input | NA | Same as user model | Same as user model | NA | NA
Boiler Components
| Number of boilers | 1 | [28 empty] | 2 | Data center system not served by HW plant | Same as user model | Data center system not served by HW plant | 2 | Data center system not served by HW plant
| Boiler Capacity | 2887320 | [28 empty] | 2887230 |  | Same as user model |  | Autosized with 1.25 sizing factor
| Boiler Efficiency | 80% | [28 empty] | 82% Et |  | Same as user model |  | Based on capacity, Table 110.2-K
| Boiler Type | Hot Water Boiler | [28 empty] | Hot Water Boiler |  | Same as user model |  | Hot Water Boiler
| Boiler Heat Loss | 0 | [28 empty] | 0% |  | Same as user model |  | 0%
| Boiler Performance Curve | Not Input | [28 empty] | Not input |  | BlrHWBlrFIRRatio_fQRatioSI |  | BlrHWBlrFIRRatio_fQRatioSI
| Boiler Min. Unloading Ratio | 25% | [28 empty] | 25% |  | Same as user model |  | 25%
| Hot Water Supply Temperature | 180 F | [28 empty] | 180F |  | Same as user model |  | 180F, Fixed
| Hot Water Return Temperature | 140 F | [28 empty] | 140F |  | Same as user model |  | 140F
| Pump Control Type | Constant Speed | [28 empty] | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow |  | Same as user model |  | Operation Control: OnDemand Speed Control: Constant Speed, Variable Flow
| Pump Power | (18.1 W/gpm) | [28 empty] | 2.74 kW (19 W/gpm) (For Reference only, Not specified in the ACM) Design Flow Rate: 144.3 gpm Pump Head: 63.2 ft H20 Impeller Efficiency: 0.7 Name Plate HP: 5 hp |  | 2.74 kW (19 W/gpm) (For Reference only, Not specified in the ACM) Design Flow Rate: 144.3 gpm Pump Head: 63.2 ft H20 Impeller Efficiency: 0.7 Name Plate HP:5 hp |  | (19 W/gpm)
| Pump Motor Efficiency | 89.5% | [28 empty] | 89.5% |  | Same as user model |  | Based on ACM min motor efficiency table
| Pump Part Load Curve | Not Input | [28 empty] | Not input |  | Default |  | Default
Chiller Components
| Chiller Type | Centrifugal chiller | [28 empty] | Centrifugal chiller | Building ChW plant serves data center | Same as user model | Building ChW plant serves data center | The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller, sized equally >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons | Building ChW plant serves data center
| Number of Chillers | 2 (for building) | [28 empty] | 2 (for building) |  | Same as user model |  | Based on cooling capacity
| Chiller Fuel | Electricity | [28 empty] | Electricity |  | Same as user model |  | Electricity
| Chiller Oversizing Factor | NA | [28 empty] | Default |  | Same as user model |  | 1.15
| Chiller Capacity (Btu/hr) | 5,268,800 x 2 | [28 empty] | 5,268,800 x 2 |  | Same as user model |  | Autosized
| Chiller Efficiency | COP=6.6 | [28 empty] | 0.585 kW/ton (20.51 EER, 6.01 COP for reference, not input) |  | Same as user model |  | Based on capacity, Table 110.2-D
| Chiller Part-Load Efficiency (IPLV) | IPLV=0.45 kW/ton | [28 empty] | IPLV=0.38 kW/ton |  | Same as user model |  | NA
| Chiller Min. Unloading Ratio | 10% | [28 empty] | 10% |  | Same as user model |  | Based on system type
| Chiller Cooling Capacity Adjustment Curve | Not Input | [28 empty] | Not input |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | Path B curve from Appendix 5.7 based on chiller size
| Chiller Cooling Efficiency Adjustment Curve | Not Input | [28 empty] | Not input |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | Path B curve from Appendix 5.7 based on chiller size
| Chilled Water Supply Temperature | 42F | [28 empty] | 44F, Fixed |  | Same as user model |  | 44F, Load reset
| Chilled Water ReturnTemperature | 54F | [28 empty] | 64F |  | Same as user model |  | 64F
| Condensor Type | Water-cooled | [28 empty] | Fluid |  | Same as user model |  | Fluid
| Cooling tower Fan Control Type | two-speed | [28 empty] | VariableSpeedDrive, VSD |  | Same as user model |  | VariableSpeedDrive, VSD
| Cooling Tower Fan Horse Power | 44 gpm/hp | [28 empty] | 60 gpm/hp 20.5 HP 1229.9 gpm |  | Same as user model |  | 60 gpm/hp 25.91 HP 1554.87 gpm
| Cooling Tower Set Point Control | 70F | [28 empty] | 70F |  | Same as user model |  | 70F
| Chiller, Condenser Pump Control Type | Chilled-water pump- Variable Speed, Variable flow Condenser Water-Fixed Speed | [28 empty] | CHW: Variable speed, Variable flow CW: Fixed speed, Fixed flow |  | Same as user model |  | CHW: Variable speed, Variable flow CW: Fixed speed, Fixed flow
| Chiller, Condenser Pump Motor Power | Chilled-water pump- 22W/gpm Condenser Water-19W/gpm | [28 empty] | CHW: 15.5 W/gpm CW: 13W/gpm |  | Same as user model |  | CHW: 16.5 W/gpm CW: 12.9 W/gpm
| Chiller, Condenser Pump Motor Efficiency | 90% | [28 empty] | CHW: 92.4 % CW: 93 % |  | Same as user model |  | CHW: 924 % CW: 936 %
| Chiller, Condenser Pump Design Flow | Chiller- 2.0 gpm/ton Condenser- 2.4 gpm/ton | [28 empty] | Chiller- 1.2 gpm/ton Condenser- 2.4 gpm/ton |  | Chiller- 1.2 gpm/ton Condenser- 2.4 gpm/ton |  | Chiller- 1.2 gpm/ton Condenser-2.4 gpm/ton
Service Hot Water
| SWH type | Storage | WtrHtr:Type
| Fuel type | Natural Gas | WtrHtr:FuelSrc
| Thermal Efficiency | 85% | WtrHtr:ThrmlEff | [24 empty] | 0.78 | 0.78 | 0.78
| Energy Factor | 0.77 | WtrHtr:EF | [24 empty] | NA | NA | NA
| Hot Water Load/person (gal/h-person) | 0.18 | Spc:HotWtrHtgRt | [6 empty] | 0.18 | 0.24 | 0.18 | 0.09 | 0 | 0.09 | 0.18 | 0.24 | 0.18 | 0.09 | 0 | 0.09 | 0.18 | 0.24 | 0.18 | 0.09 | 0 | 0.09 | 106 Btuh/person | 106 Btuh/person | 106 Btuh/person
| SHW Schedule |  | Spc:HotWtrHtgSchRef | [12 empty] | RetailServiceHotWater | HealthServiceHotWater | OfficeServiceHotWater | AssemblyServiceHotWater | OfficeServiceHotWater | RetailServiceHotWater | RetailServiceHotWater | HealthServiceHotWater | OfficeServiceHotWater | AssemblyServiceHotWater | OfficeServiceHotWater | RetailServiceHotWater | Office | Office | Office
| Tank Volume (gal) | 500 | WtrHtr:StorCap
| Availability Schedule | Not Input | FluidSys:AvailSchRef
| Water temperature setpoint Schedule | Fixed | FluidSys:TempCtrl
| Water temperature setpoint | 180 | FluidSys:FixedSupTemp
| Water Heater Max Capacity (Btuh) | 250000 | WtrHtr:CapRtd
| Performance Curve | Not Input | WtrHtr:HIR_fPLRCrvRef
| Standby Loss (Btuh) | 4538 | WtrHtr:StbyLoss

## Small Hotel
Key:
| Base PrototypeTest Parameters | Most General parameters of prototype building. Specific test instances to be generated based on this model.
| Not Part of Test Case | Not Specified - Not Part of Test Case
| Test Instance Specification Incomplete | Updates to test instance specfication in progress
| Test Instance Specification Complete | Updates to test instance specification have been completed
| Daylighting (Detailed Geometry Models Only) | Exclude Testing/Verification of Daylighting Parameters in Simplified Geometry Models
|  | Small Hotel General Prototype | Relevant SDD Properties | 070015-HotSml-Run03 |  |  | 070015-HotSml-Run22
|  | User model |  | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model
Building Type |  |  |  | Small Hotel |  | Small Hotel | Hotel
Vintage |  |  |  | New Construction |  |  | New Construction
Climate Zone |  |  |  | CZ-15 |  | CZ-15 | CZ-12
Geometry
| Total Floor Area (sq feet) | 43200 (180 ft x 60 ft)
| Aspect Ratio | 3
| Number of Floors | 4
| Azimuth | 0
| Thermal Zoning | Ground Floor: 19 zones including guest rooms, lobby, office space, meeting room, laundry room, employee lounge, restrooms, exercise room, mechanical room, corridor, stairs, storage; 2nd-4th Floor: 16 zones per floor, including guest rooms, corridor, stairs and storage; Guest rooms accounts for 63% of total floor area.
| Floor to floor height (feet) | Ground floor: 11 ft, Upper floors: 9 ft
| Floor to ceiling height (feet) | Ground floor: 11 ft, Upper floors: 9 ft
| Roof Dimensions | Based on floor area and aspect ratio
| Roof Tilt and Orientation | horizontal
| Foundation Dimensions | Based on floor area and aspect ratio
| Window Fraction (Window to Wall Ratio) | Average total - 10.9% South - 3.1% East - 11.4% West - 15.2% North - 4%
| Window Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glazing Sill Height (feet) | 3 ft in ground floor, 2 ft. in upper floors
| Window Location | one per guestroom (4' x 5')
| Skylight Fraction (Skylight to Roof Ratio) | NA
| Skylight Dimensions | NA
| Skylight Locations | NA
Envelope Components
| Roof Construction Assembly Type Slope Category | Metal Frame Roof (Wood Frame and Other), horizontal | Roof:ConsType | Metal Frame Roof (Wood Frame and Other), Low | Metal Frame Roof (Wood Frame and Other), Low | WoodFramingAndOtherRoof, Low Residential: Flat Res Wood Framing And Other Roof NonResidential: Flat Nonres Wood Framing And Other Roof
| Roof Construction Assembly overall U value | 0.055 | Roof:OverallUFactor | 0.055 | 0.055 | Residential: 0.028 NonResidential 0.039
| Roof Construction Assembly layers | WoodFramingAndOtherRoofU055: 1. Metal Standing Seam - 1/16 in. 2. Expanded Polystyrene - EPS - 4 1/16 in. R17 3. Gypsum Board 1/2in | ConsAssm:MatRef[X] | 1. Metal Standing Seam - 1/16 in. 2. Expanded Polystyrene - EPS - 4 1/16 in. R17 3. Gypsum Board - 1/2 in. | 1. Metal Standing Seam - 1/16 in. 2. Expanded Polystyrene - EPS - 4 1/16 in. R17 3. Gypsum Board - 1/2 in. | Residential: 1.Metal Standing Seam - 1/16 in. 2. Compliance Insulation R34.93 NonResidential: 1.Metal Standing Seam - 1/16 in. 2. Compliance Insulation R24.86
| Roof Aged Solar Reflectance (Solar Absorptance) | 0.6 | ConsAssm:CRRCAgedRefl ConsAssm:ExtSolAbs | 0.60 (0.40) | 0.60 (0.40) | Residential: 0.55 (0.45) NonResidential 0.63 (0.37)
| Roof Aged Thermal emittance (Thermal Absorptance) | 0.70 (0.70) | ConsAssm:CRRCAgedEmittance ConsAssm:ExtThrmlAbs | 0.70 (0.70) | 0.70 (0.70) | Residential: 0.85 (0.85) NonResidential 0.85 (0.85)
| Exterior Wall Construction Assembly Type | MetalFrameWall | ExtWall:ConsType | MetalFrameWall | MetalFrameWall | MetalFrameWall
| Exterior Wall Construction Assembly overall U value | 0.082 | ExtWall:OverallUFactor | 0.082 | 0.082 | Residential: 0.105 NonResidential 0.062
| Exterior Wall Construction Assembly layers | MetalFrameWallU082: 1.Stucco - 7/8 in. 2. Expanded Polystyrene - EPS - 2 7/16 in. R10 3. Air - Metal Wall Framing - 16 or 24 in. OC 4. Gypsum Board - 3/8 in. | ConsAssm:MatRef[X] | 1. Stucco 7/8 in. 2. Expanded Polystyrene - EPS - 2 7/16 in. R10 3. Air - Metal Wall Framing - 16 or 24 in. OC 4. Gypsum Board - 3/8 in. | 1. Stucco 7/8 in. 2. Expanded Polystyrene - EPS - 2 7/16 in. R10 3. Air - Metal Wall Framing - 16 or 24 in. OC 4. Gypsum Board - 3/8 in. | Residential: 1. Stucco 7/8 in. 2. Compliance Insulation R7.39 3. Air - Metal Wall Framing - 16 or 24 in. OC 4.Gypsum Board - 1/2 in. Nonresidential: 1. Stucco 7/8 in. 2. Compliance Insulation R13.99 3. Air - Metal Wall Framing - 16 or 24 in. OC 4. Gypsum Board - 1/2 in.
| Above-grade Floor Construction Assembly Type | MassFloor | ExtFlr:ConsType | MassFloor | MassFloor | Other Floor
| Above-grade Floor Construction Assembly overall U value | 0.058 | ExtFlr:OverallUFactor | 0.058 | 0.058 | Residential and NonResidential: 0.039
| Above-grade Floor Construction Assembly layers | "MassFloorU058": 1. Metal Deck - 1/16 in. 2. Concrete - 80 lb/ft3 - 4 in. 3. Expanded Polystyrene - EPS - 1 7/8 in. R8.0 4. Expanded Polyurethane - 3/4 in. R4.7 5. Carpet - 3/4 in. | ConsAssm:MatRef[X] | 1. Metal Deck - 1/16 in. 2. Concrete - 80 lb/ft3 - 4 in. 3. Expanded Polystyrene - EPS - 1 7/8 in. R8.0 4. Expanded Polyurethane - 3/4 in. R4.7 5. Carpet - 3/4 in. | 1. Metal Deck - 1/16 in. 2. Concrete - 80 lb/ft3 - 4 in. 3. Expanded Polystyrene - EPS - 1 7/8 in. R8.0 4. Expanded Polyurethane - 3/4 in. R4.7 5. Carpet - 3/4 in. | Residential and NonResidential: 1. Compliance Insulation R21.39 2. Plywood - 5/8 in. 3. Carpet - 3/4 in.
| On/Below Grade Floor F-factor Total Perimeter Area Total Perimeter exposed | NA | UndgrFlr:OverallFFactor | NA | NA | NA
| Vertical Window Type | FixedWindow and OperableWindow | FenCons:FenProdType | FixedWindow and OperableWindow | FixedWindow and OperableWindow | FixedWindow and OperableWindow
| Window assembly U value | Fixed-0.25, Operable-0.42 | FenCons:UFactor | Fixed-0.25, Operable-0.42 | Fixed-0.25, Operable-0.42 | Fixed-0.36, Operable-0.46
| Window SHGC | Fixed-0.20, Operable-0.18 | FenCons:SHGC | Fixed-0.20, Operable-0.18 | Fixed-0.20, Operable-0.18 | Fixed-0.25, operable-0.22
| Window VT | Fixed-0.47, Operable-0.35 | FenCons:VT | Fixed-0.47, Operable-0.35 | Fixed-0.47, Operable-0.35 | Fixed-0.42, Operable-0.32
| Window overhang | NA
| Skylight overall U value | NA
| Skylight SHGC | NA
| Skylight VT | NA
| Daylit Area (calculated value) | Calculated by Software According to ACM section 5.4.5
Internal Load Components
| Occupancy Type | Common Areas: Hotel Function Area Guest Rooms: Hotel/Motel Guest Room
| People Density | Common Areas: 14.925 ft2/person Guest Rooms: 200 ft2/person
| Sensible Heat/person | Common Areas: 250 Btu/h-person Guest Rooms: 245 Btu/h-person
| Latent Heat/person | Common Areas: 200 Btu/h-person Guest Rooms: 155 Btu/h-person
| Equipment Power Density | Common Areas: 0.50 Guest Rooms: 0.50
| Lighting Power Density | Common Areas: 1.50 Guest Rooms: 0.50
| Ventilation Rate Per Person | - | Spc:VentRt | FrontLoungeFlr1 Thermal Zone & MeetingRoomFlr1 Thermal Zone: 15 cfm/Person All Other Common Areas: 0 cfm/Person Guest Rooms: NA | Same as user model |  | FrontLoungeFlr1 Thermal Zone: 15 cfm/Person All Other Common Areas: 0 cfm/Person Guest Rooms: NA | Same as user model
| Ventilation Rate Per Area | - |  | All Common Areas: 0.15 cfm/ft2 Guest Rooms: NA | Same as user model |  | All Common Areas: 0.15 cfm/ft2 Guest Rooms: NA | Same as user model
| Simulated Ventilation Rate | Common Areas: 1.50 Guest Rooms: 0.15 |  | FrontLoungeFlr1 Thermal Zone & MeetingRoomFlr1 Thermal Zone: 1.07 cfm/ft2 All Common Areas: Max value of 'Ventilation Rate Per Person' and 'Ventilation Rate Per Area' Guest Rooms: 30 cfm (Min Per Unit) Guest Rooms (3rd Floor Only- Naturally Ventilated): 30 cfm (Min Per Unit) Guest Rooms (4th Floor Only- Exhaust fan): equal to exhaust flow rates or 30 cfm (Min Per Unit) | Same as user model | FrontLoungeFlr1 Thermal Zone & MeetingRoomFlr1 Thermal Zone: 1.07 cfm/ft2 All Other Common Areas: 0.15 cfm/dt2 Guest Rooms: 30 cfm (Min Per Unit) Guest Rooms (3rd Floor Only- Naturally Ventilated): 30 cfm (Min Per Unit) Guest Rooms (4th Floor Only- Exhaust fan): equal to exhaust flow rates or 30 cfm (Min Per Unit) | FrontLoungeFlr1 Thermal Zone: 1.07 cfm/ft2 All Common Areas: Max value of 'Ventilation Rate Per Person' and 'Ventilation Rate Per Area' KitchenFlr1 Thermal Zone: 1.215 cfm/ft2 (1050 cfm Exhaust Flow) Guest Rooms: 30 cfm (Min Per Unit) Guest Rooms (3rd Floor Only- Naturally Ventilated): 30 cfm (Min Per Unit) Guest Rooms (4th Floor Only- Exhaust fan): equal to exhaust flow rates or 30 cfm (Min Per Unit) | Same as user model | FrontLoungeFlr1 Thermal Zone: 1.07 cfm/ft2 All Other Common Areas: 0.15 cfm/dt2 KitchenFlr1 Thermal Zone: 1.215 cfm/ft2 (1050 cfm Exhaust Flow) Guest Rooms: 30 cfm (Min Per Unit) Guest Rooms (3rd Floor Only- Naturally Ventilated): 30 cfm (Min Per Unit) Guest Rooms (4th Floor Only- Exhaust fan): equal to exhaust flow rates or 30 cfm (Min Per Unit)
| Infiltration Rate | 0.0448
| Infiltration Schedule | Default
| Infiltration Method | FlowExteriorWallArea
| Elevator Power | NA
Occupancy Schedule
Equipment Schedule
Lighting Schedule
Elevator Schedule
Daylighting
| Illuminance Setpoint | Front Lounge: 767.8 Front Office: 287.5 Meeting Room: 175 | Spc:PriSideDayltgIllumSetPt
| Daylight Control Type | Continuous | ThrmlZn:DayltgCtrlType
| Controlled General Lighting Power In Primary Daylit Area | Defaulted: Lighting Power Density*(Daylit Area/Total Area) | ThrmlZn:PriSideDayltgCtrlLtgPwr
| Controlled General Lighting Power In Secondary Daylit Area | 0 | ThrmlZn:SecSideDayltgCtrlLtgPwr
| Controlled General Lighting Power In Skylit Daylit Area | NA | ThrmlZn:SkylitDayltgCtrlLtgPwr
| Reference Position 1 | Calculated by Software According to ACM section 5.4.5
| Reference Position 2 | Calculated by Software According to ACM section 5.4.5
HVAC Components
| HVAC System Type | Common Areas: PVAV Guest Rooms: FPFC |  | Common Areas: PVAV Guest Rooms: FPFC DOAS system (2nd Floor): SZAC | Same as user model | Common Areas: PVAV Guest Rooms: FPFC | Common Areas: PVAV Guest Rooms: Guest Room 101: Packaged SZAC, single phase Guest Room 102: Split SZAC, single phase Guest Room 103: Packaged SZHP, single phase Guest Room 104: Split SZHP, single phase All other Guest Rooms: FPFC Zone-KitchenFlr1: SZAC | Same as user model | Common Areas: PVAV Guest Rooms: FPFC Zone-KitchenFlr1: SZAC
| Heating Type | Common Areas: Hot Water Guest Rooms: Hot Water |  | Common Areas: Hot Water Guest Rooms: Hot Water DOAS system (2nd Floor): Furnace (Natural Gas) | Same as user model | Common Areas: Hot Water Guest Rooms: Hot Water | Common Areas: Hot Water Guest Rooms: Guest Room 101: Furnace (Natural Gas) Guest Room 102: Furnace (Natural Gas) Guest Room 103: Electric Guest Room 104: Electric All other Guest Rooms: Hot Water Zone-KitchenFlr1: Furnace (Natural Gas) | Same as user model | Common Areas: Hot Water Guest Rooms: Hot Water Zone-KitchenFlr1: Hot Water (Natural Gas)
| Cooling Type | Common Areas: DX Guest Rooms: Chilled Water |  | Common Areas: DX Guest Rooms: Chilled Water DOAS system (2nd Floor): DX | Same as user model | Common Areas: DX Guest Rooms: Chilled Water | Common Areas: DX Guest Rooms: Guest Room 101: DX Guest Room 102: DX Guest Room 103: DX Guest Room 104: DX All other Guest Rooms: Chilled Water Zone-KitchenFlr1: DX | Same as user model | Common Areas: DX Guest Rooms: Chilled Water Zone-KitchenFlr1: DX
| Cooling Efficiency | BaseAirSys5: EER - 9.8 BaseAirSys5-2 to 5-4: EER - 10.8 |  | BaseAirSys5: EER - 9.8, IEER - 11.4 BaseAirSys5-2 to 5-3: EER - 10.8 (SEER - 13) BaseAirSys5-4: EER - 11, IEER - 12.7 Guest Rooms: NA DOAS system (2nd Floor): EER - 10.8 (SEER - 13) | Same as user model | BaseAirSys5, BaseAirSys5-2, BaseAirSys5-3, BaseAirSys5-4 and BaseSys13: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat) | BaseAirSys5: EER - 9.8 BaseAirSys5-2 to 5-3: EER - 10.8 (SEER - 13) BaseAirSys5-4: EER - 11 Guest Rooms: Guest Room 101: EER - 10.8 Guest Room 102: EER - 12.2 Guest Room 103: EER - 11.41 Guest Room 104: EER - 11.41 All other Guest Rooms: NA Zone-KitchenFlr1: EER - 10.8 (SEER - 13) | Same as user model | BaseAirSys5, BaseAirSys5-2, BaseAirSys5-3, BaseAirSys5-4 and BaseSys13: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
| Heating Efficiency | NA |  | Common Areas - PVAV: NA Guest Rooms: FPFC: NA DOAS system (2nd Floor): 80% Thermal Efficiency 78% AFUE | Same as user model | NA | Common Areas - PVAV: NA Guest Rooms: Guest Room 101: 80% Thermal Efficiency 78% AFUE Guest Room 102: 80% Thermal Efficiency 78% AFUE Guest Room 103: NA Guest Room 104: NA All other Guest Rooms: FPFC: NA Zone-KitchenFlr1 - SZAC: 80% Thermal Efficiency 78% AFUE | Same as user model | NA
| System Oversizing Factor | NA |  | NA | Same as user model | Heating- 1.25 Cooling- 1.15 | NA | Same as user model | Heating- 1.25 Cooling- 1.15
| System Capacity | Heating Capacity - default Cooling Capacity - default |  | NA | Same as user model | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat | NA | Same as user model | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat
| Design Supply Air Temperature | Heating - 70F Cooling - 55F |  | Common Areas - PVAV: Heating 60F Cooling 58F Guest Rooms - FPFC: Heating 95F Cooling 58F DOAS system (2nd Floor): NA | Same as user model | Common Areas - PVAV: Heating 60F Cooling 58F Guest Rooms - FPFC: Heating 95F Cooling 58F | Common Areas - PVAV: Heating 60F Cooling 58F Guest Rooms - FPFC: Heating 95F Cooling 58F Zone-KitchenFlr1 - SZAC: Heating 95F Cooling 55F | Same as user model | Common Areas - PVAV: Heating 60F Cooling 58F Guest Rooms - FPFC: Heating 95F Cooling 58F Zone-KitchenFlr1 - SZAC: Heating 95F Cooling 55F
| SAT Reset Control | WarmestResetFlowFirst High - 70 F Low - 55 F |  | Common Areas - PVAV: WarmestResetFlowFirst Guest Rooms - FPFC: NOSATControl | Same as user model | Common Areas - PVAV: WarmestResetFlowFirst Guest Rooms - FPFC: NOSATControl | Common Areas - PVAV: WarmestResetFlowFirst Guest Rooms - FPFC: NOSATControl Zone-KitchenFlr1 - SZAC: NOSATControl | Same as user model | Common Areas - PVAV: WarmestResetFlowFirst Guest Rooms - FPFC: NOSATControl Zone-KitchenFlr1 - SZAC: NOSATControl
| Economizer | Integrated |  | Common Areas - PVAV: Integrated Guest Rooms: NA DOAS system (2nd Floor): NA | Same as user model | Common Areas - PVAV: Integrated if load over 54 kBtu/h (If Economizer is specified) Guest Rooms - FPFC: NA | Common Areas - PVAV: Integrated Guest Rooms: NA Zone-KitchenFlr1 - SZAC: Integrated | Same as user model | Common Areas - PVAV: Integrated if load over 54 kBtu/h (If Economizer is specified) Guest Rooms - FPFC: NA Zone-KitchenFlr1 - SZAC: Integrated if load over 54 kBtu/h (If Economizer is specified)
| Economizer Limits | Differential Dry Bulb, Default limits |  | Common Areas - PVAV: Differential Dry Bulb Guest Rooms: NA DOAS system (2nd Floor): NA | Same as user model | Common Areas - PVAV: Differential Dry-Bulb (If Economizer is specified) Guest Rooms - FPFC: NA | Common Areas - PVAV: Differential Dry Bulb Guest Rooms: NA Zone-KitchenFlr1 - SZAC: Differential Dry Bulb | Same as user model | Common Areas - PVAV: Differential Dry-Bulb (If Economizer is specified) Guest Rooms - FPFC: NA Zone-KitchenFlr1 - SZAC: Differential Dry-Bulb (If Economizer is specified)
| Fan Power Specification | Brake Horsepower BaseAirSys5: 8.166 BaseAirSys5-2: 1.961 BaseAirSys5-3: 1.961 BaseAirSys5-4: 1.961 |  | Common Areas - PVAV: Static Pressure BaseAirSys5: 4 in H2O 0.62 Fan Eff 0.924 Motor Eff 12.60 bhp (For Reference only) BaseAirSys5-2: 3 in H2O 0.5 Fan Eff 0.865 Motor Eff 1.56 bhp (For Reference only) BaseAirSys5-3: 3 in H2O 0.5 Fan Eff 0.865 Motor Eff 1.58 bhp (For Reference only) BaseAirSys5-4: 3 in H2O 0.5 Fan Eff 0.865 Motor Eff 1.63 bhp (For Reference only) Guest Rooms: Static Pressure 0.14 - 0.15 bhp 0.855 Motor Eff Guest Rooms (4th Floor only): Static Pressure 2.11 in H2O 0.5 Fan Eff 0.855 Motor Eff 0.02 bhp (For Reference only) | Same as user model | BaseAirSys5, BaseAirSys5-2, BaseAirSys5-3 and BaseAirSys5-4: Common Areas - PVAV: Static Pressure The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Guest Rooms - FPFC: PowerPerUnitFlow 0.35 W/cfm The Supply Fan Power Index for FPFC systems is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | Common Areas - PVAV: Static Pressure BaseAirSys5: 4 in H2O 0.62 Fan Eff 0.924 Motor Eff 12.60 bhp (For Reference only) BaseAirSys5-2: 3 in H2O 0.5 Fan Eff 0.865 Motor Eff 1.56 bhp (For Reference only) BaseAirSys5-3: 3 in H2O 0.5 Fan Eff 0.865 Motor Eff 1.58 bhp (For Reference only) BaseAirSys5-4: 3 in H2O 0.5 Fan Eff 0.865 Motor Eff 1.63 bhp (For Reference only) Guest Rooms: Static Pressure 0.14 - 0.15 bhp 0.855 Motor Eff Zone-KitchenFlr1 - SZAC: Static Pressure Kitchen Fan: 0.855 Motor Eff 0.68 bhp (For Reference only) KitchExh Fan: 0.855 Motor Eff 0.50 bhp (For Reference only) | Same as user model | BaseAirSys5, BaseAirSys5-2, BaseAirSys5-3 and BaseAirSys5-4: Common Areas - PVAV: Static Pressure The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Guest Rooms - FPFC: PowerPerUnitFlow 0.35 W/cfm The Supply Fan Power Index for FPFC systems is dictated by the ACM section 5.7.3.2 Zone-KitchenFlr1 - SZAC: Static Pressure Kitchen Fan: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 KitchExh Fan: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3
| Motor Horsepower | BaseAirSys5: 10 BaseAirSys5-2: 2 BaseAirSys5-3: 2 BaseAirSys5-4: 2 |  | Common Areas - PVAV: Brake Horsepower BaseAirSys5: 15 HP BaseAirSys5-2: 2 HP BaseAirSys5-3: 2 HP BaseAirSys5-4: 2 HP Guest Rooms: 0.25 HP Guest Rooms (4th Floor only): 0.083 HP | Same as user model | Common Areas - PVAV: Static Pressure BaseAirSys5, BaseAirSys5-2, BaseAirSys5-3 and BaseAirSys5-4: Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | Common Areas - PVAV: Brake Horsepower BaseAirSys5: 15 HP BaseAirSys5-2: 2 HP BaseAirSys5-3: 2 HP BaseAirSys5-4: 2 HP Guest Rooms: 0.25 HP Zone-KitchenFlr1 - SZAC: Static Pressure Kitchen Fan: 0.75 HP KitchExh Fan: 0.5 HP | Same as user model | Common Areas - PVAV: Static Pressure BaseAirSys5, BaseAirSys5-2, BaseAirSys5-3 and BaseAirSys5-4: Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Zone-KitchenFlr1 - SZAC: Static Pressure Kitchen Fan: Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 KitchExh Fan: Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3
| Fan Control Method | Variable Speed Drive |  | Constant Volume | Same as user model | Constant Volume | BaseAirSys5, BaseAirSys5-2, BaseAirSys5-3 and BaseAirSys5-4: VariableSpeedDrive All other Fans: Constant Volume | Same as user model | BaseAirSys5, BaseAirSys5-2, BaseAirSys5-3 and BaseAirSys5-4: VariableSpeedDrive All other Fans: Constant Volume
| Cooling Coil Curve(s) | Not Input (DXEIR_fTempCrvRef) (DXEIR_fPLFCrvRef) (DXEIR_fFlowCrvRef) |  | Not Input | Curve Selection Dependent On Coil Capacity: Common Areas - DX: BaseAirSys5: CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio BaseAirSys5-2 to 5-3: EER - 10.8 (SEER - 13) For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio BaseAirSys5-4: EER - 11 CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio DOAS system (2nd Floor): EER - 10.8 (SEER - 13) For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Curve Selection Dependent On Coil Capacity: Common Areas - DX: BaseAirSys5: EER - 9.8 CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio BaseAirSys5-2 to 5-3: EER - 10.8 (SEER - 13) For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio BaseAirSys5-4: EER - 11 CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio Guest Rooms - Chilled Water: NA | Not Input | Curve Selection Dependent On Coil Capacity: Common Areas - DX: BaseAirSys5: CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio BaseAirSys5-2 to 5-3: EER - 10.8 (SEER - 13) For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio BaseAirSys5-4: EER - 11 CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio Guest Rooms: Guest Rooms 101-104: CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio All other Guest Rooms: NA Zone-KitchenFlr1 - DX: For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Curve Selection Dependent On Coil Capacity: Common Areas - DX: BaseAirSys5: CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio BaseAirSys5-2 to 5-3: EER - 10.8 (SEER - 13) For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio BaseAirSys5-4: CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXDblEIRRatio_fCFMRatio Guest Rooms - Chilled Water: NA Zone-KitchenFlr1 - DX: For SEER Rated Coils (< 65,000 Bth/h): CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI CoilClgDXSEEREIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio
| Heating Coil Curve(s) | Not Input (FurnHIR_fPLRCrvRef) |  | Not Input | Common Areas - Hot Water: NA Guest Rooms - Hot Water: NA | Common Areas - Hot Water: NA Guest Rooms - Hot Water: NA | Not Input | Common Areas - Hot Water: NA Guest Rooms: Guest Rooms 101-102: CoilHtgFurnFIRRatio_fQRatio All other Guest Rooms: NA Zone-KitchenFlr1: Furnace (Natural Gas) CoilHtgFurnFIRRatio_fQRatio | Common Areas - Hot Water: NA Guest Rooms - Hot Water: NA Zone-KitchenFlr1 - Hot Water (Natural Gas): NA
| Fan Part-load Performance Curve | Not Input
| HVAC(Availability/Fan) Schedule | Not Input |  | Not Input | Common Areas: OfficeHVACAvail Guest Rooms: ResidentialLivingHVACAvail | Common Areas: OfficeHVACAvail Guest Rooms: ResidentialLivingHVACAvail | Not Input | Common Areas: OfficeHVACAvail Guest Rooms: ResidentialLivingHVACAvail Zone-KitchenFlr1: RestaurantHVACAvail | Common Areas: OfficeHVACAvail Guest Rooms: ResidentialLivingHVACAvail Zone-KitchenFlr1: RestaurantHVACAvail
| Cooling Thermostat Schedule | Not Input |  | Not Input | Common Areas: OfficeClgSetpt Guest Rooms: ResidentialLivingClgSetpt | Common Areas: OfficeClgSetpt Guest Rooms: ResidentialLivingClgSetpt | Not Input | Common Areas: OfficeClgSetpt Guest Rooms: ResidentialLivingClgSetpt Zone-KitchenFlr1: RestaurantClgSetpt | Common Areas: OfficeClgSetpt Guest Rooms: ResidentialLivingClgSetpt Zone-KitchenFlr1: RestaurantClgSetpt
| Heating Thermostat Schedule | Not Input |  | Not Input | Common Areas: OfficeHtgSetpt Guest Rooms: ResidentialLivingHtgSetpt | Common Areas: OfficeHtgSetpt Guest Rooms: ResidentialLivingHtgSetpt | Not Input | Common Areas: OfficeHtgSetpt Guest Rooms: ResidentialLivingHtgSetpt Zone-KitchenFlr1: RestaurantHtgSetpt | Common Areas: OfficeHtgSetpt Guest Rooms: ResidentialLivingHtgSetpt Zone-KitchenFlr1: RestaurantHtgSetpt
| Terminal Heat Type | Hot Water |  | Hot Water | Same as user model | Hot Water | Hot Water | Same as user model | Hot Water
| Terminal Heat Capacity | Default |  | NA | Same as user model | NA | NA | Same as user model | NA
| Terminal Unit Fan Power | NA |  | NA | Same as user model | NA | NA | Same as user model | NA
| Reheat Delta T | NA |  | NA | Same as user model | NA | NA | Same as user model | NA
Boiler Components
| Number of boilers | 2 |  | 2 | Same as user model | 2 | 2 | Same as user model | 2
| Boiler Capacity | 363000 |  | 363,000 btu/h | Same as user model | Autosized with 1.25 sizing factor | 363,000 btu/h | Same as user model | Autosized with 1.25 sizing factor
| Boiler Efficiency | 80% |  | 80% Et | Same as user model | Based on capacity, Table 110.2-K | 80% Et | Same as user model | Based on capacity, Table 110.2-K
| Boiler Type | Hot Water Boiler |  | NA | Same as user model | NA | NA | Same as user model | NA
| Boiler Heat Loss | 0 |  | 0% | Same as user model | NA | 0% | Same as user model | NA
| Boiler Performance Curve | Not Input |  | default | BlrHWBlrFIRRatio_fQRatioSI | BlrHWBlrFIRRatio_fQRatioSI | default | BlrHWBlrFIRRatio_fQRatioSI | BlrHWBlrFIRRatio_fQRatioSI
| Boiler Min. Unloading Ratio | 25% |  | 25% | Same as user model | 25% | 25% | Same as user model | 25%
| Hot Water Supply Temperature | 180F |  | 180F | Same as user model | 180F | 180F | Same as user model | 180F
| Hot Water Return Temperature | 140F |  | 140F | Same as user model | 140F | 140F | Same as user model | 140F
| Pump Control Type | Constant Speed |  | NA | Same as user model | NA | NA | Same as user model | NA
| Pump Power | (19 W/gpm) |  | 0.34 kW (19 W/gpm) (For Reference only, Not specified in the ACM) Design Flow Rate: 18.14 gpm Pump Head: 60.39 ft H20 Impeller Efficiency: 0.7 Name Plate HP: 0.5 hp | Same as user model | (19 W/gpm) | 0.34 kW (19 W/gpm) (For Reference only, Not specified in the ACM) Design Flow Rate: 18.14 gpm Pump Head: 60.39 ft H20 Impeller Efficiency: 0.7 Name Plate HP: 0.5 hp | Same as user model | (19 W/gpm)
| Pump Motor Efficiency | 85.5% |  | 85.5% | Same as user model | Based on ACM Minimum Nominal Efficiency for Electric Motors table and Standard Design hp 85.5% | 85.5% | Same as user model | Based on ACM Minimum Nominal Efficiency for Electric Motors table and Standard Design hp 85.5%
| Pump Part Load Curve | Not Input |  | Not input | Default | Default | Not input | Default | Default
Chiller Components
| Chiller Type | Screw |  | Screw | Same as user model | The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller, sized equally >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons | Screw | Same as user model | The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller, sized equally >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons
| Number of Chillers | 1 |  | 1 | Same as user model | Based on cooling capacity | 1 | Same as user model | Based on cooling capacity
| Chiller Fuel | Electrtic |  | Electric | Same as user model | Electric | Electric | Same as user model | Electric
| Chiller Oversizing Factor | NA |  | NA | Same as user model | 1.15 | NA | Same as user model | 1.15
| Chiller Capacity (Btu/hr) | 348,000 Btu/hr |  | 348,000 Btu/hr | Same as user model | Autosized | 348,000 Btu/hr | Same as user model | Autosized
| Chiller Efficiency (kW/ton) | 0.8 |  | COP=4.51 (0.78 kW/ton, 15.38 EER) | Same as user model | Based on capacity, Table 110.2-D | COP=4.51 (0.78 kW/ton, 15.4 EER) | Same as user model | Based on capacity, Table 110.2-D
| Chiller Part-Load Efficiency (IPLV) | 0.6 |  | IPLV=0.5 | Same as user model | NA | IPLV=0.5 | Same as user model | NA
| Chiller Min. Unloading Ratio | 0.15 |  | 15% | Same as user model | Based on system type 15% | 15% | Same as user model | Based on system type 15%
| Chiller Cooling Capacity Adjustment Curve | Not Input |  | Not input | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI | Path B curve from Appendix 5.7 based on chiller size | Not input | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI | Path B curve from Appendix 5.7 based on chiller size
| Chiller Cooling Efficiency Adjustment Curve | Not Input |  | Not input | ChlrWtrPosDispPathBAllEIRRatio_fQRatio ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI | Path B curve from Appendix 5.7 based on chiller size | Not input | ChlrWtrPosDispPathBAllEIRRatio_fQRatio ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI | Path B curve from Appendix 5.7 based on chiller size
| Chilled Water Supply Temperature | 44 F |  | 44 | Same as user model | 44 | 44 | Same as user model | 44
| Chilled Water ReturnTemperature | 64 F |  | 64 | Same as user model | 64 | 64 | Same as user model | 64
| Condensor Type | Fluid |  | Fluid | Same as user model | Fluid | Fluid | Same as user model | Fluid
| Cooling tower Fan Control Type | Axial |  | VariableSpeedDrive, VSD | Same as user model | VariableSpeedDrive, VSD | VariableSpeedDrive, VSD | Same as user model | VariableSpeedDrive, VSD
| Cooling Tower Fan Horse Power | 2 |  | 60 gpm/hp 1.42 HP 85.00 gpm | Same as user model | 60 gpm/hp 1.24 HP 73.93 gpm | 60 gpm/hp 1.42 HP 85.0 gpm | Same as user model | 60 gpm/hp 1.21 HP 72.39 gpm
| Cooling Tower Set Point Control | 85 F |  | 85F | Same as user model | 70F Fixed at the 0.4% design wet-bulb temperature, prescribed and specified for each of the 86 weather data files | 85F | Same as user model | 70F Fixed at the 0.4% design wet-bulb temperature, prescribed and specified for each of the 86 weather data files
| Chiller, Condenser Pump Control Type | OnDemand |  | CHW: Variable speed, Variable Flow CW: Flow Constant Speed, Fixed Flow | Same as user model | CHW: Variable speed, Variable flow CW: Constant speed, Fixed flow | CHW: Variable speed, Variable Flow CW: Flow Constant Speed, Fixed Flow | Same as user model | CHW: Variable speed, Variable flow CW: Constant speed, Fixed flow
| Chiller, Condenser Pump Motor Power | Chiller: 0.522 kW Condenser: 1.395 kW |  | CHW: 12.9 W/gpm CW: 14 W/gpm | Same as user model | CHW: 12.8 W/gpm CW: 14 W/gpm | CHW: 12.9 W/gpm CW: 14 W/gpm | Same as user model | CHW: 12.8 W/gpm CW: 14 W/gpm
| Chiller, Condenser Pump Motor Efficiency | Chiller: 0.865 Condenser: 0.855 |  | CHW: 85.5% CW: 86.5% | Same as user model | Based on ACM Minimum Nominal Efficiency for Electric Motors table and Standard Design hp CHW: 85.5% CW: 86.5% | CHW: 85.5% CW: 86.5% | Same as user model | Based on ACM Minimum Nominal Efficiency for Electric Motors table and Standard Design hp CHW: 85.5% CW: 86.5%
| Chiller, Condenser Pump Design Flow | Chiller: 34.8 gpm Condenser: 85.4 gpm |  | Chiller (CHW) - 1.2 gpm/ton Condenser (CW) - 2.4 gpm/ton | Same as user model | Chiller (CHW) - 1.2 gpm/ton Condenser (CW) - 2.4 gpm/ton | Chiller (CHW) - 1.2 gpm/ton Condenser (CW) - 2.4 gpm/ton | Same as user model | Chiller (CHW) - 1.2 gpm/ton Condenser (CW) - 2.4 gpm/ton
Service Hot Water
| SWH type | SHWFluidSys1-4: Storage | WtrHtr:Type
| Fuel type | SHWFluidSys1-4: NaturalGas | WtrHtr:FuelSrc
| Thermal Efficiency | SHWFluidSys1-4: 0.85 | WtrHtr:ThrmlEff
| Energy Factor | SHWFluidSys1-4: NA | WtrHtr:EF
| Hot Water Load/person (gal/h-person) | Guest Room: 4.48 gal/h/person Hotel Function Areas: 0.10 gal/h/person Office: 0.18 gal/h/person Corridor/Stariwell/Support: 0.0 gal/h/person Electrical, Mechanical, Telephone : 0.0 gal/h/person Unoccupied: 0.0 gal/h/person | Spc:HotWtrHtgRt
| SHW Schedule |  | Spc:HotWtrHtgSchRef
| Tank Volume (gal) | SHWFluidSys1: 143 gal SHWFluidSys2: 217 gal SHWFluidSys3: 273 gal SHWFluidSys4: 273 gal | WtrHtr:StorCap
| Availability Schedule | Not Input | FluidSys:AvailSchRef
| Water temperature setpoint control/schedule | Fixed | FluidSys:TempCtrl
| Water temperature setpoint | 120 | FluidSys:FixedSupTemp
| Water Heater Max Capacity (Btuh) | SHWFluidSys1: 76 kBtu/hr SHWFluidSys2: 96 kBtu/hr SHWFluidSys3: 121 kBtu/hr SHWFluidSys4: 121 kBtu/hr | WtrHtr:CapRtd
| Performance Curve | Default | WtrHtr:HIR_fPLRCrvRef
| Standby Loss (Btuh) | SHWFluidSys1: 1298 Btu/hr SHWFluidSys2: 1969 Btu/hr SHWFluidSys3: 2477 Btu/hr SHWFluidSys4: 2477 Btu/hr | WtrHtr:StbyLoss

## Warehouse (hidden)
Key:
| Base PrototypeTest Parameters | Most General parameters of prototype building. Specific test instances to be generated based on this model. | [7 empty] | 46945.5
| Not Part of Test Case | Not Specified - Not Part of Test Case | [7 empty] | 45032.38
| Test Instance Specification Incomplete | Updates to test instance specfication in progress | [7 empty] | 95.92%
| Test Instance Specification Complete | Updates to test instance specification have been completed
| Daylighting (Detailed Geometry Models Only) | Exclude Testing/Verification of Daylighting Parameters in Simplified Geometry Models
|  | Warehouse General Prototype | Relevant SDD Properties | 080006-Whse-Run07 |  |  | 080006-Whse-Run08 |  |  | Run09 - INCOMPLETE |  |  | 080006-Whse-Run15 |  |  | 080006-Whse-Run21
|  | User model |  | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model
Building Type |  |  |  | Warehouse |  | Small Hotel | Warehouse |  | Small Hotel | Warehouse |  | Small Hotel | Warehouse | Warehouse | Warehouse | Warehouse
Vintage |  |  |  | New Construction |  |  | New Construction
Climate Zone |  |  |  | CZ-6 |  | CZ-15 | CZ-6 |  | CZ-15 | CZ-6 |  | CZ-15 | CZ-6 | CZ-6 | CZ-6 | CZ-6
Geometry
| Total Floor Area (sq feet) | 49,495 (330 ft x 150 ft)
| Aspect Ratio | 2.2
| Number of Floors | 1
| Azimuth | 0
| Thermal Zoning | Three zones: Bulk Storage, Fine Storage, and Office. The Office zone is enclosed on two sides and at the top by the Fine Storage zone.
| Floor to floor height (feet) | 28
| Floor to ceiling height (feet) | 14 (office)
| Roof Dimensions | Based on floor area and aspect ratio
| Roof Tilt and Orientation | Horizontal
| Foundation Dimensions | Based on floor area and aspect ratio
| Window Fraction (Window to Wall Ratio) | Total - 0.7% South - 0% East - 0% North - 0.76% West - 0.29% | Bldg:CondWWR Bldg:SouthCondWWR Bldg:EastCondWWR Bldg:NorthCondWWR Bldg:WestCondWWR
Window Dimensions
| Glazing Sill Height (feet) | 3
| Window Location | Top of the window is 8 ft high with 5 ft high glass
| Skylight Fraction (Skylight to Roof Ratio) | Total: 5% |  | Total: 7% | Total: 7% | Total: 5% | Total: 14% | Total: 14% | Total: 5%
| Skylight Dimensions | Zone-2_Fine Storage - 464 ft2 (29 skylights @16ft2) Zone-3_Bulk Storage - 2016 ft2 (126 skylights @16ft2) |  | Zone-2_Fine Storage - 640 Ft2 (40 skylights @16 Ft2) Zone-3_Bulk Storage - 2848 Ft2 (178 skylights @16 Ft2) | Zone-2_Fine Storage - 640 Ft2 (40 skylights @16 Ft2) Zone-3_Bulk Storage - 2848 Ft2 (178 skylights @16 Ft2) | Zone-2_Fine Storage - 454 Ft2 (40 skylights @11.35 Ft2) Zone-3_Bulk Storage - 2020.3 Ft2 (178 skylights @11.35 Ft2) | Zone-2_Fine Storage - 2176 Ft2 (136 skylights @16 Ft2) Zone-3_Bulk Storage - 4800 Ft2 (300 skylights @16 Ft2) | Zone-2_Fine Storage - 2176 Ft2 (136 skylights @16 Ft2) Zone-3_Bulk Storage - 4800 Ft2 (300 skylights @16 Ft2) | Zone-2_Fine Storage - 772 Ft2 (136 skylights @5.68 Ft2) Zone-3_Bulk Storage - 1702 Ft2 (300 skylights @5.68 Ft2)
| Skylight Locations | Bulk Storage, Fine Storage
Envelope Components
| Roof Construction Assembly Type Slope Category | Metal Frame Roof (Wood Frame and Other), horizontal | Roof:ConsType
| Roof Construction Assembly overall U value | 0.075 | Roof:OverallUFactor
| Roof Construction Assembly layers | WoodFramingAndOtherRoofU075: 1. Metal Standing Seam - 1/16 in. 2. Expanded Polystyrene - EPS -3 in. | ConsAssm:MatRef[X]
| Roof Aged Solar Reflectance (Solar Absorptance) | 0.63 | ConsAssm:CRRCAgedRefl (ConsAssm:ExtSolAbs)
| Roof Aged Thermal emittance (Thermal Absorptance) | 0.75 | ConsAssm:CRRCAgedEmittance (ConsAssm:ExtThrmlAbs)
| Exterior Wall Construction Assembly Type | Metal Framed | ExtWall:ConsType
| Exterior Wall Construction Assembly overall U value | 0.098 | ExtWall:OverallUFactor
| Exterior Wall Construction Assembly layers | MetalFrameWallU098: 1. Stucco - 7/8 in. 2. Expanded Polystyrene - EPS - 1 15/16 in. 3. Air - Metal Wall Framing - 16 or 24 in. OC 4. Gypsum Board - 1/2 in. | ConsAssm:MatRef[X]
| Above-grade Floor Construction Assembly Type | NA | ExtFlr:ConsType
| Above-grade Floor Construction Assembly overall U value | NA | ExtFlr:OverallUFactor
| Above-grade Floor Construction Assembly layers | NA | ConsAssm:MatRef[X]
| On/Below Grade Floor F-factor Total Perimeter length Total Perimeter exposed | 0.7 960 ft 960 ft | UndgrFlr:OverallFFactor
| Vertical Window Type | Fixed | FenCons:FenProdType
| Window assembly U value | CZ-6 Standard Design "Fixed Window" U-0.26 | FenCons:UFactor
| Window SHGC | CZ-6 Standard Design "Fixed Window" SHGC-0.25 | FenCons:SHGC
| Window VT | CZ-6 Standard Design "Fixed Window" VT-0.42 | FenCons:VT
| Window overhang | NA | Win:ExtShdgObj
| Skylight overall U value | 0.55 | FenCons:UFactor | 0.55 | 0.55 | 0.58
| Skylight SHGC | 0.2 | FenCons:SHGC | 0.2 | 0.2 | 0.25
| Skylight VT | 0.4 | FenCons:VT | 0.4 | 0.4 | 0.49
| Daylit Area (calculated value) | Calculated by Software According to ACM section 5.4.5 |  |  |  |  | Zone 1 Office: Floor Area: 2550 ft2 Skylit Daylit Area: 0 ft2 (0%) Zone 2 Fine Storage: Floor Area: 12,449 ft2 Skylit Daylit Area: 12,300 ft2 (99%) Zone 3 Bulk Storage: Floor Area: 34,497 ft2 Skylit Daylit Area: 34,324 ft2 (99%) | Zone 1 Office: Floor Area: 2550 ft2 Skylit Daylit Area: 0 ft2 (0%) Zone 2 Fine Storage: Floor Area: 12,449 ft2 Skylit Daylit Area: 12,300 ft2 (99%) Zone 3 Bulk Storage: Floor Area: 34,497 ft2 Skylit Daylit Area: 34,324 ft2 (99%) | Zone 1 Office: Floor Area: 2550 ft2 Skylit Daylit Area: 0 ft2 (0%) Zone 2 Fine Storage: Floor Area: 12,449 ft2 Skylit Daylit Area: 12,441 ft2 (99%) Zone 3 Bulk Storage: Floor Area: 34,497 ft2 Skylit Daylit Area: 34,176 ft2 (99%) | 55% 96% Zone 2 Fine Storage: Floor Area: 12,448.8 Skylit Daylit Area: 10,730.42 ft2 Zone 3 Bulk Storage: Floor Area: 34,496.7 Skylit Daylit Area: 34,301.96 ft2 | 55% 96% Zone 2 Fine Storage: Floor Area: 12,448.8 Skylit Daylit Area: 10,730.42 ft2 Zone 3 Bulk Storage: Floor Area: 34,496.7 Skylit Daylit Area: 34,301.96 ft2 | 75% Zone 2 Fine Storage: Floor Area: 12,448.8 Skylit Daylit Area: 10,730.42 ft2 Zone 3 Bulk Storage: Floor Area: 34,496.7 Skylit Daylit Area: 34,301.96 ft2
Internal Load Components
| Occupancy Type | Office: Office (Greater than 250 square feet in floor area) Storage Areas: Commercial and Industrial storage Areas (conditioned or unconditioned)
| People Density | Office: 100 ft2/person Storage Areas: 333.33 ft2/person
| Sensible Heat/person | Office: 250 Btu/h-person Storage Areas: 275 Btu/h-person
| Latent Heat/person | Office: 200 Btu/h-person Storage Areas: 475 Btu/h-person
| Equipment Power Density | Office: 1.5 W/ft2 Storage Areas: 0.2 W/ft2
| Lighting Power Density | Office: 0.8 W/ft2 Storage Areas: 0.6 W/ft2 | Spc:IntLPDReg Spc:IntLtgSpecMthd Spc:IntLtgSys:TailoredMthdAllowType Spc:TMGenLPD Spc:TMTotAllowLPD
| Ventilation Rate Per Person | Office: 0.15 cfm/ft2 Storage Areas: 0.15 cfm/ft2
Ventilation Rate Per Area
Simulated Ventilation Rate
| Infiltration Rate | 0.0448
| Infiltration Schedule | Office/Warehouse infiltration
| Infiltration Method | FlowExteriorWallArea
| Elevator Power | NA
Occupancy Schedule
Equipment Schedule
| Lighting Schedule |  | Spc:IntLtgRegSchRef
Elevator Schedule
Daylighting
| Illuminance Setpoint (Adjusted Illuminance Setpoint) | Office: -Skylit: none -Primary Sidelit: 287.5 lux -Secondary Sidelit: none Fine Storage: -Skylit: 175 lux -Primary Sidelit: none -Secondary Sidelit: none Bulk Storage: -Skylit: 175 lux -Primary Sidelit: none -Secondary Sidelit: none | Spc:PriSideDayltgIllumSetPt | [9 empty] | Office: -Skylit: none -Primary Sidelit: 400 lux (400 lux Adj.) -Secondary Sidelit: none Fine Storage: -Skylit: 250 lux (250 lux Adj.) -Primary Sidelit: none -Secondary Sidelit: none Bulk Storage: -Skylit: 250 lux (250 lux Adj.) -Primary Sidelit: none -Secondary Sidelit: none | Same as user input | Office: -Skylit: none -Primary Sidelit: 400 lux (400 lux Adj.) -Secondary Sidelit: 287.5 lux (1150 Adj.) Fine Storage: -Skylit: 250 lux (250 lux Adj.) -Primary Sidelit: none -Secondary Sidelit: none Bulk Storage: -Skylit: 250 lux (250 lux Adj.) -Primary Sidelit: none -Secondary Sidelit: none
| Daylight Control Type | All Spaces: ContinuousDimming | ThrmlZn:DayltgCtrlType | [9 empty] | All Spaces: ContinuousDimming | Same as user input | All Spaces: ContinuousDimming
| Controlled General Lighting Power In Primary Daylit Area | Defaulted: Lighting Power Density*(Daylit Area/Total Area) | ThrmlZn:PriSideDayltgCtrlLtgPwr | [9 empty] | Office: 150 W Fine Storage: NA Bulk Storage: NA | Same as user input | Office: 404 W Fine Storage: NA Bulk Storage: NA
| Controlled General Lighting Power In Secondary Daylit Area | 0 | ThrmlZn:SecSideDayltgCtrlLtgPwr | [9 empty] | Office: none Fine Storage: NA Bulk Storage: NA | Same as user input | Office: 316 W Fine Storage: NA Bulk Storage: NA
| Controlled General Lighting Power In Skylit Daylit Area | Defaulted: Lighting Power Density*(Daylit Area/Total Area) | ThrmlZn:SkylitDayltgCtrlLtgPwr | [9 empty] | Office: NA Fine Storage: 5000 W Bulk Storage: 15000 W | Same as user input | Lighting Power Density*(Daylit Area/Total Area) Office: NA Fine Storage: 6438.25 W Bulk Storage: 20632.5 W
| Reference Position 1 | Calculated by Software According to ACM section 5.4.5 | [10 empty] | Calculated by Software According to ACM section 5.4.5 | Same as user input | Office: 8 ft from exterior wall; midpoint of SW corner window on south façade Fine Storage: Positioned on any edge and aligned with center of one skylight. Bulk Storage: Positioned on any edge and aligned with center of one skylight.
| Reference Position 2 | Calculated by Software According to ACM section 5.4.5 | [10 empty] | None | Same as user input | Office: 16 ft from exterior wall; midpoint of SE corner window on south façade Fine Storage: None Bulk Storage: None
HVAC Components
| HVAC System Type | SZAC | [13 empty] | Office Spaces: SZAC Warehouse: SZAC (no cooling) | Same as User Model | Office Spaces: SZAC Warehouse: HV (System 9)
| Heating Type | Gas Furnace | [13 empty] | All: Gas Furnace | Same as User Model | All: Gas Furnace
| Cooling Type | DX | [13 empty] | Office Spaces: DX Warehouse: NA | Same as User Model | Office Spaces: DX Warehouse: NA
| Cooling Efficiency | Office: EER 11.2 FineStorage Area: EER 10 BulkStorage Area: EER 10 | [13 empty] | Office Spaces: EER 11.2, IEER 12.9 Warehouse: NA | Same as User Model | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
| Heating Efficiency | 81% Thrml, 78% AFUE | [13 empty] | Office and Fine Storage: 79% AFUE (80.05% Thermal Efficiency for reference, not input) Bulk Storage: 81.0% Thermal Efficiency | Same as User Model | Min Req. Based on Coil Capacity < 225,000 Btu/hr: 78% AFUE or 80% Thrml >=225,000 Btu/hr: 80% Thrml
| System Oversizing Factor | na | [13 empty] | na | na | Heating- 1.25 Cooling- 1.15
| System Capacity | Heating Capacity - default Cooling Capacity - default | [13 empty] | Heating Capacity - default Cooling Capacity - default | Same as User Model | Heating Coil Capaicty to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat
| Design Supply Air Temperature | Office Heating - 95F Office Cooling - 55F Warehouse Heating - 95F Warehouse Cooling - 60F | [13 empty] | Office Heating - 95F Office Cooling - 55F Warehouse Heating - 95F Warehouse Cooling -NA | Same as User Model | Office Heating - 95F Office Cooling - 55F Warehouse Heating - 95F Warehouse Cooling -NA
| SAT Reset Control | Fixed | [13 empty] | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Same as user model | No SAT Control (Htg/clg cycles on/off based on call from thermostat)
| Economizer | None | [13 empty] | None | None | None
| Economizer Limits | NA | [13 empty] | NA | NA | NA
| Fan Power Specification | Brake Horsepower Method: Office: 0.9 bhp FineStorage Area: 0.9 bhp BulkStorage Area: 0.9 bhp | [13 empty] | Brake Horsepower Method: Office: 2 bhp 0.890 Motor Eff FineStorage Area: 5.5 bhp 0.920 Motor Eff BulkStorage Area: 20 bhp 0.920 Motor Eff | Same as User Model | Static Pressure Method: Office Zone, Fine Storage and Bulk Storage: The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3
| Motor Horsepower | Office: 1 hp FineStorage Area: 1 hp BulkStorage Area: 1 hp | [13 empty] | Office: 5 hp FineStorage Area: 10 hp BulkStorage Area: 30 hp | Same as User Model | Office Zone, Fine Storage and Bulk Storage: Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3
| Fan Control Method | ConstantVolume | [13 empty] | Constant Volume | Same as User Model | Constant Volume
| Cooling Coil Curve(s) | Default (Cap_fTempCrvRef) (Cap_fFlowCrvRef) (DXEIR_fTempCrvRef) (DXEIR_fPLFCrvRef) (DXEIR_fFlowCrvRef) | [13 empty] | Default | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio
| Heating Coil Curve(s) | Default (FurnHIR_fPLRCrvRef) | [13 empty] | Not Input | CoilHtgFurnFIRRatio_fQRatio | CoilHtgFurnFIRRatio_fQRatio
| Fan Part-load Performance Curve | Default
| HVAC(Availability/Fan) Schedule | Default | [13 empty] | Not Input | WarehouseHVACAvail | WarehouseHVACAvail
| Cooling Thermostat Schedule | Not Input | [13 empty] | Not Input | Office: WarehouseClgSetPt Warehouse: NA | Office: WarehouseClgSetPt Warehouse: NA
| Heating Thermostat Schedule | Not Input | [13 empty] | Not Input | Office: WarehouseHtgSetPt Warehouse: WarehouseHtgSetPt | Office: WarehouseHtgSetPt Warehouse: WarehouseHtgSetPt
| Terminal Heat Type | NA | [13 empty] | NA | NA | NA
| Terminal Heat Capacity | NA | [13 empty] | NA | NA | NA
| Terminal Unit Fan Power | NA | [13 empty] | NA | NA | NA
| Reheat Delta T | NA | [13 empty] | NA | NA | NA
Boiler Components
| Number of boilers | NA
| Boiler Capacity | NA
| Boiler Efficiency | NA
| Boiler Type | NA
| Boiler Heat Loss | NA
| Boiler Performance Curve | NA
| Boiler Min. Unloading Ratio | NA
| Hot Water Supply Temperature | NA
| Hot Water Return Temperature | NA
| Pump Control Type | NA
| Pump Power | NA
| Pump Motor Efficiency | NA
| Pump Part Load Curve | NA
Chiller Components
| Chiller Type | NA
| Number of Chillers | NA
| Chiller Fuel | NA
| Chiller Oversizing Factor | NA
| Chiller Capacity (tons) | NA
| Chiller Efficiency | NA
| Chiller Part-Load Efficiency (IPLV) | NA
| Chiller Min. Unloading Ratio | NA
| Chiller Cooling Capacity Adjustment Curve | NA
| Chiller Cooling Efficiency Adjustment Curve | NA
| Chilled Water Supply Temperature | NA
| Chilled Water ReturnTemperature | NA
| Condensor Type | NA
| Cooling tower Fan Control Type | NA
| Cooling Tower Fan Horse Power | NA
| Cooling Tower Set Point Control | NA
| Chiller, Condenser Pump Control Type | NA
| Chiller, Condenser Pump Motor Power | NA
| Chiller, Condenser Pump Motor Efficiency | NA
| Chiller, Condenser Pump Design Flow | NA
Service Hot Water
| SWH type | Storage | WtrHtr:Type
| Fuel type | Natural Gas | WtrHtr:FuelSrc
| Thermal Efficiency | 80% | WtrHtr:ThrmlEff
| Energy Factor | NA | WtrHtr:EF
| Hot Water Load/person (gal/h-person) | 18% | Spc:HotWtrHtgRt
| SHW Schedule |  | Spc:HotWtrHtgSchRef
| Tank Volume (gal) | 43 gal | WtrHtr:StorCap
| Availability Schedule | Not Input | FluidSys:AvailSchRef
| Water temperature setpoint Schedule | Not Input | FluidSys:TempCtrl
| Water temperature setpoint | 120 | FluidSys:FixedSupTemp
| Water Heater Max Capacity (Btuh) | 21,000 Btu/hr | WtrHtr:CapRtd
| Performance Curve | Not Input | WtrHtr:HIR_fPLRCrvRef
| Tank Off Cycle Loss Coeff | 1.345 Btu/hr.F
Note on K54: Sandeep: NEEDS REVIEW: After the rules have been implementted in full.
Note on L54: Sandeep: NEEDS REVIEW: After the rules have been implementted in full.
Note on M54: Sandeep: NEEDS REVIEW: After the rules have been implementted in full.
Note on B113: Nambiar, Chitra: This input is not an option in E+ HVAc Template:Plant:Boiler object.
Note on D151: Jason Acosta: this varies based on temp control

## Retail Medium
Key:
| Base PrototypeTest Parameters | Most General parameters of prototype building. Specific test instances to be generated based on this model.
| Not Part of Test Case | Not Specified - Not Part of Test Case
| Test Instance Specification Incomplete | Updates to test instance specfication in progress
| Test Instance Specification Complete | Updates to test instance specification have been completed
| Daylighting (Detailed Geometry Models Only) | Exclude Testing/Verification of Daylighting Parameters in Simplified Geometry Models
|  | Retail Medium General Prototype | Relevant SDD Properties | 050006-RetlMed- Run16 |  |  | 050006-RetlMed- Run27 - Existing Addition |  |  | 050006-RetlMed- Run28 - Existing Addition and Alteration
|  | User model |  | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model | User Model | Proposed Model | Baseline model
Building Type |  |  |  | Retail Medium |  |  | Retail Medium |  |  | Retail Medium
Vintage |  |  |  | New Construction |  |  | New Construction |  |  | New Construction |  |  | 050006-RetlMed- Run28 |  | Proposed |  |  | Baseline
Climate Zone |  |  |  | CZ-6 |  |  | CZ-6 |  |  | CZ-6 |  |  | Wall Name | Status | Construction Name | Construction Type | U-Value | Construction Name | Construction Type
Geometry | [12 empty] | Back_Space_Wall_East | Altered | Altered metal frame wall | MetalFrameWall | 0.053 | MetalFrameWallU098 | MetalFrameWall
| Total Floor Area (sq feet) | 24,692 ft2 (178.05 ft X 138.68 ft ) | [10 empty] | Back_Space_Wall_North | Altered | Altered metal building wall | MetalBuildingWall | 0.052 | MetalBldgWallU113 | MetalBuildingWall
| Aspect Ratio | 1.29 | [10 empty] | Back_Space_Wall_West | New | New heavy mass wall | MassHeavyWall | 0.051 | MetalFrameWallU098 | MetalFrameWall
| Number of Floors | 1 | [10 empty] | Core_Retail_Wall_East_2 | Altered | Altered light mass wall | MassLightWall | 0.046 | MassLightWallU440 | MassLightWall
| Azimuth | 0 | [10 empty] | Core_Retail_Wall_West_2 | Altered | Altered heavy mass wall | MassHeavyWall | 0.051 | MassHeavyWallU690 | MassHeavyWall
| Thermal Zoning | Five zones: Back Space, Core Retail, Front Entry, Front Retail, Point of Sale |  |  |  |  | Three south facing zones are modeled as an addition - alone |  |  | Three south facing zones are modeled as an addition |  |  | Front_Entry_Wall_South | New | Base_CZ12-NonresMetalFrameWallU062 | MetalFrameWall | 0.062 | MetalFrameWallUnconditioned | MetalFrameWall
| Floor to floor height (feet) | 20 | [10 empty] | Front_Retail_Walll_East | New | Base_CZ12-NonresMetalFrameWallU062 | MetalFrameWall | 0.062 | MetalFrameWallU098 | MetalFrameWall
| Floor to ceiling height (feet) | 20 | [10 empty] | Front_Retail_Wall_South | New | Base_CZ12-NonresMetalFrameWallU062 | MetalFrameWall | 0.062 | MetalFrameWallU098 | MetalFrameWall
| Roof Dimensions | Based on floor area and aspect ratio | [10 empty] | Point_Of_Sale_Wall_South | New | Base_CZ12-NonresMetalFrameWallU062 | MetalFrameWall | 0.062 | MetalFrameWallU098 | MetalFrameWall
| Roof Tilt and Orientation | horizontal | [10 empty] | Point_Of_Sale_Wall_West | New | Base_CZ12-NonresMetalFrameWallU062 | MetalFrameWall | 0.062 | MetalFrameWallU098 | MetalFrameWall
| Foundation Dimensions | Based onfloor area and aspect ratio | [10 empty] | Roof Name | Status | Construction Name | Construction Type | U-Value | Construction Name | Construction Type
| Window Fraction (Window to Wall Ratio) | [5 empty] | Overall: 37% North: NA East: NA Window Compliance status: New South: 46% West: NA | Overall: 37% North: NA East: NA Window Compliance status: New South: 46% West: NA | Overall: 37% North: NA East: NA Window Compliance status: New South: 46% West: NA | Overall: 07% North: NA East: NA Window Compliance status: New South: 25% West: NA | Overall: 07% North: NA East: NA Window Compliance status: New South: 25% West: NA | Overall: 07% North: NA East: NA Window Compliance status: New South: 25% West: NA | Back_Space_Roof | Altered | Altered metal bldg roof | MetalBuildingRoof | 0.03 | FlatNonresMetalBuildingRoofU065 | MetalBuildingRoof
| Window Dimensions | 82.14 ft x 4.98 ft on the long side of 'Front Retail' and 'Point of Sale' spaces | [10 empty] | Core_Retail_Roof | Altered | Other Altered Roof | WoodFramingAndOtherRoof | 0.021 | FlatNonresWoodFramingAndOtherRoofU075 | WoodFramingAndOtherRoof
| Glazing Sill Height (feet) | 3.74 ft | [10 empty] | Front_Entry_Roof | New | Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned | WoodFramingAndOtherRoof | 1.282 | FlatNonresWoodFramingAndOtherRoofUnconditioned | WoodFramingAndOtherRoof
| Window Location | long side of 'Front Retail' and 'Point of Sale' spaces | [10 empty] | Front_Retail_Roof | New | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039 | WoodFramingAndOtherRoof | 0.039 | FlatNonresWoodFramingAndOtherRoofU075 | WoodFramingAndOtherRoof
| Skylight Fraction (Skylight to Roof Ratio) | 2.97% | [7 empty] | Total: 2% | Total: 2% | Total: 2% | Point_Of_Sale_Roof | New | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039 | WoodFramingAndOtherRoof | 0.039 | FlatNonresWoodFramingAndOtherRoofU075 | WoodFramingAndOtherRoof
| Skylight Dimensions | Core_Retail- 17227.4 ft2 (32 skylights @16ft2)
| Skylight Locations | Core Retail
Envelope Components
| Roof Construction Assembly Type Slope Category | Metal Frame Roof (Wood Frame and Other), horizontal | Roof:ConsType | [6 empty] | Front Retail and Point Of Sale, Front Entry Roof Compliance Status: New WoodFramingAndOtherRoof Low Core Retail Roof Compliance Status: Altered WoodFramingAndOtherRoof Low Back Space Roof Compliance Status: Altered MetalBuildingRoof Low | Front Retail and Point Of Sale, Front Entry Roof Compliance Status: New WoodFramingAndOtherRoof Low Core Retail Roof Compliance Status: Altered WoodFramingAndOtherRoof Low Back Space Roof Compliance Status: Altered MetalBuildingRoof Low | Front Retail and Point Of Sale, Front Entry Roof Compliance Status: New WoodFramingAndOtherRoof Low Core Retail Roof Compliance Status: Altered WoodFramingAndOtherRoof Low Back Space MetalBuildingRoof Low
| Roof Construction Assembly overall U value | 0.039, 1.282 | Roof:OverallUFactor | [6 empty] | Front Retail and Point Of Sale Roof Compliance Status: New Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039: 0.039 Front Entry Roof Compliance Status: New Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned: 1.282 Core Retail Roof Compliance Status: Altered Other Altered Roof: 0.021 Back Space Roof Compliance Status: Altered Altered metal bldg roof: 0.034 | Front Retail and Point Of Sale Roof Compliance Status: New Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039: 0.039 Front Entry Roof Compliance Status: New Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned: 1.282 Core Retail Roof Compliance Status: Altered Other Altered Roof: 0.021 Back Space Roof Compliance Status: Altered Altered metal bldg roof: 0.034 | Front Retail and Point Of Sale Roof Compliance Status: New FlatNonresWoodFramingAndOtherRoofU049: 0.049 Front Entry Roof Compliance Status: New FlatNonresWoodFramingAndOtherRoofUnconditioned: 1.282 Core Retail Roof Compliance Status: Altered FlatNonresWoodFramingAndOtherRoofU049: 0.049 Back Space Roof Compliance Status: Altered FlatNonresMetalBuildingRoofU041: 0.041
| Roof Construction Assembly layers | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039: 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R24.86 Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned: 1. Metal Standing Seam - 1/16 in. | ConsAssm:MatRef[X] | [6 empty] | Front Retail and Point Of Sale Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039: 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R24.86 Front Entry Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned: 1. Metal Standing Seam - 1/16 in. Core Retail Other Altered Roof 1. Built-up roofing - 3/8 in. 2. Expanded Polystyrene - EPS - 6 1/10 in. R25 3. Wood, Roof24in OC, 2x6, cav. R-19 4. Air - Cavity - Wall Roof Ceiling - 4 in. or more 5. Acoustic Tile - 3/4 in. Back Space Altered metal bldg roof 1. Metal, RoofMetalStandingSeam, cav. R-20 2. Air - Cavity - Wall Roof Ceiling - 4 in. or more 3. Expanded Polystyrene - EPS - 4 1/16 in. R17 | Front Retail and Point Of Sale Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039: 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R24.86 Front Entry Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned: 1. Metal Standing Seam - 1/16 in. Core Retail Other Altered Roof 1. Built-up roofing - 3/8 in. 2. Expanded Polystyrene - EPS - 6 1/10 in. R25 3. Wood, Roof24in OC, 2x6, cav. R-19 4. Air - Cavity - Wall Roof Ceiling - 4 in. or more 5. Acoustic Tile - 3/4 in. Back Space Altered metal bldg roof 1. Metal, RoofMetalStandingSeam, cav. R-20 2. Air - Cavity - Wall Roof Ceiling - 4 in. or more 3. Expanded Polystyrene - EPS - 4 1/16 in. R17 | Front Retail and Point Of Sale FlatNonresWoodFramingAndOtherRoofU049: 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R19.63 Front Entry FlatNonresWoodFramingAndOtherRoofUnconditioned: 1. Metal Standing Seam - 1/16 in. Core Retail FlatNonresWoodFramingAndOtherRoofU049: 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R19.63 Back Space FlatNonresMetalBuildingRoofU065: 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R20.05 3. Compliance Insulation R2.00 4. Compliance Insulation R1.00 5. Compliance Insulation R0.50 6. Compliance Insulation R0.05 7. Compliance Insulation R0.01
| Roof Aged Solar Reflectance (Solar Absorptance) | 0.63 (0.37) | ConsAssm:CRRCAgedRefl (ConsAssm:ExtSolAbs)
| Roof Aged Thermal emittance (Thermal Absorptance) | 0.85 (0.85) | ConsAssm:CRRCAgedEmittance (ConsAssm:ExtThrmlAbs)
| Exterior Wall Construction Assembly Type | WoodFramingAndOtherWall | ExtWall:ConsType |  |  |  | Walls between addition and the existing building are modeled as adiabatic. |  |  | Front Entry, Front Retail and Point Of Sale Exterior Wall Compliance Status: New New Walls: MetalFrameWall Core Retail Exterior Wall Compliance Status: Altered MassLightWall (Core Retail East Wall) MassHeavyWall (Core Retail West Wall) Back Space Exterior Wall Compliance Status: Altered MetalFrameWall (Back Space East Wall) MetalBuildingWall (Back Space North Wall) Exterior Wall Compliance Status: New MassHeavyWall (Back Space West Wall) | Front Entry, Front Retail and Point Of Sale Exterior Wall Compliance Status: New New Walls: MetalFrameWall Core Retail Exterior Wall Compliance Status: Altered MassLightWall (Core Retail East Wall) MassHeavyWall (Core Retail West Wall) Back Space Exterior Wall Compliance Status: Altered MetalFrameWall (Back Space East Wall) MetalBuildingWall (Back Space North Wall) Exterior Wall Compliance Status: New MassHeavyWall (Back Space West Wall) | Front Entry, Front Retail and Point Of Sale Exterior Wall Compliance Status: New New Walls: MetalFrameWall Core Retail Exterior Wall Compliance Status: Altered MassLightWall (Core Retail East Wall) MassHeavyWall (Core Retail West Wall) Back Space Exterior Wall Compliance Status: Altered MetalFrameWall (Back Space East Wall) MetalBuildingWall (Back Space North Wall) Exterior Wall Compliance Status: New MassHeavyWall (Back Space West Wall)
| Exterior Wall Construction Assembly overall U value | 0.062 | ExtWall:OverallUFactor | [6 empty] | Front Entry, Front Retail and Point Of Sale Exterior Wall Compliance Status: New Base_CZ12-NonresMetalFrameWallU062: 0.62 Core Retail Exterior Wall Compliance Status: Altered Altered Light Mass Wall (Core Retail East Wall): 0.046 Altered Heavy Mass Wall (Core Retail West Wall): 0.051 Back Space Exterior Wall Compliance Status: Altered Altered Metal Frame Wall (Back Space East Wall): 0.053 Altered Metal Building Wall (Back Space North Wall): 0.052 Back Space Exterior Wall Compliance Status: New New Heavy Mass Wall (Back Space West Wall): 0.051 | Front Entry, Front Retail and Point Of Sale Exterior Wall Compliance Status: New Base_CZ12-NonresMetalFrameWallU062: 0.62 Core Retail Exterior Wall Compliance Status: Altered Altered Light Mass Wall (Core Retail East Wall): 0.046 Altered Heavy Mass Wall (Core Retail West Wall): 0.051 Back Space Exterior Wall Compliance Status: Altered Altered Metal Frame Wall (Back Space East Wall): 0.053 Altered Metal Building Wall (Back Space North Wall): 0.052 Back Space Exterior Wall Compliance Status: New New Heavy Mass Wall (Back Space West Wall): 0.051 | Front Entry, Front Retail and Point Of Sale Exterior Wall Compliance Status: New MetalFrameWallU098: 0.098 Core Retail Exterior Wall Compliance Status: Altered MassLightWallU440: 0.440 MassHeavyWallU690: 0.690 Back Space Exterior Wall Compliance Status: Altered MetalFrameWallU098: 0.098 MetalBldgWallU113: 0.113 Back Space Exterior Wall Compliance Status: New MetalFrameWallU098: 0.098
| Exterior Wall Construction Assembly layers | Base_CZ12-NonresMetalFrameWallU062: 1. Stucco - 7/8 in. 2. Compliance Insulation R13.99 3. Air - Metal Wall Framing 16-24 in. OC 4. Gypsum Board - 1/2 in. | ConsAssm:MatRef[X] | [6 empty] | Front Entry, Front Retail, Point Of Sale and Back Space Base_CZ12-NonresMetalFrameWallU062 (MetalFrameWall) 1. Stucco - 7/8 in. 2. Compliance Insulation R13.99 3. Air - Metal Wall Framing 16-24 in. OC 4. Gypsum Board - 1/2 in. Core Retail Altered light mass wall (MassLightWall) 1. Stucco - 7/8 in. 2. Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. 3. Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. 4. Expanded Polystyrene - EPS - 4 1/16 in. R17 5. Air - Metal Wall Framing 16-24 in. OC 6. Gypsum Board - 1/2 in. Core Retail and Back Space Altered/New heavy mass wall (MassHeavyWall) 1. Stucco - 7/8 in. 2. Concrete - 140 lb/ft3 - 6in 3. Expanded Polystyrene - EPS - 4 1/16 in. R17 4. Air - Metal Wall Framing 16-24 in. OC 5. Gypsum Board - 1/2 in. Back Space Altered metal building wall (MetalBuildingWall) 1. Metal Siding - 1/16 in. 2. Expanded Polystyrene - EPS - 4 1/16 in. R17 3. Air - Metal Wall Framing 16-24 in. OC 4. Plywood - 3/4 in. Altered metal frame wall (MetalBuildingWall) 1. Stucco - 7/8 in. 2. Expanded Polystyrene - EPS - 4 1/16 in. R17 3. Air - Metal Wall Framing 16-24 in. OC 4. Gypsum Board - 1/2 in. | Front Entry, Front Retail, Point Of Sale and Back Space Base_CZ12-NonresMetalFrameWallU062 (MetalFrameWall) 1. Stucco - 7/8 in. 2. Compliance Insulation R13.99 3. Air - Metal Wall Framing 16-24 in. OC 4. Gypsum Board - 1/2 in. Core Retail Altered light mass wall (MassLightWall) 1. Stucco - 7/8 in. 2. Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. 3. Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. 4. Expanded Polystyrene - EPS - 4 1/16 in. R17 5. Air - Metal Wall Framing 16-24 in. OC 6. Gypsum Board - 1/2 in. Core Retail and Back Space Altered/New heavy mass wall (MassHeavyWall) 1. Stucco - 7/8 in. 2. Concrete - 140 lb/ft3 - 6in 3. Expanded Polystyrene - EPS - 4 1/16 in. R17 4. Air - Metal Wall Framing 16-24 in. OC 5. Gypsum Board - 1/2 in. Back Space Altered metal building wall (MetalBuildingWall) 1. Metal Siding - 1/16 in. 2. Expanded Polystyrene - EPS - 4 1/16 in. R17 3. Air - Metal Wall Framing 16-24 in. OC 4. Plywood - 3/4 in. Altered metal frame wall (MetalBuildingWall) 1. Stucco - 7/8 in. 2. Expanded Polystyrene - EPS - 4 1/16 in. R17 3. Air - Metal Wall Framing 16-24 in. OC 4. Gypsum Board - 1/2 in. | Front Entry, Front Retail and Point Of Sale MetalFrameWallU069 (MetalBuildingWall) 1. Stucco - 7/8 in. 2. Compliance Insulation R10.06 3. Compliance Insulation R2.00 4. Compliance Insulation R0.20 5. Compliance Insulation R0.10 6. Air - Metal Wall Framing - 16 or 24 in. OC 7. Gypsum Board - 1/2 in. Core Retail MassLightWallU440 (MassLightWall) 1. Concrete - 140 lb/ft3 - 4 in. 2. Compliance Insulation R0.02 3. Air - Metal Wall Framing - 16 or 24 in. OC 4. Gypsum Board - 1/2 in. MassHeavyWallU690 (MassHeavyWall) 1. Concrete - 140 lb/ft3 - 8 in. 2. Compliance Insulation R0.01 Back Space MetalBldgWallU113 (MetalBuildingWall) 1. Metal Standing Seam - 1/16 in. 2. Compliance Insulation R8.00 MetalFrameWallU069 (MetalBuildingWall) 1. Stucco - 7/8 in. 2. Compliance Insulation R10.06 3. Compliance Insulation R2.00 4. Compliance Insulation R0.20 5. Compliance Insulation R0.10 6. Air - Metal Wall Framing - 16 or 24 in. OC 7. Gypsum Board - 1/2 in.
| Above-grade Floor Construction Assembly Type | NA (Slab-on grade) | ExtFlr:ConsType
| Above-grade Floor Construction Assembly overall U value | NA | ExtFlr:OverallUFactor
| Above-grade Floor Construction Assembly layers | NA | ConsAssm:MatRef[X]
| On/Below Grade Floor F-factor Total Perimeter Area Total Perimeter exposed | 0.73 24,692 ft2 633.46 | UndgrFlr:OverallFFactor
| Vertical Window Type | Fixed | FenCons:FenProdType |  |  |  | Fixed | Fixed | Fixed
| Window assembly U value | 0.36 | FenCons:UFactor |  |  |  | Window Compliance status: New 0.35 | Window Compliance status: New 0.35 | Window Compliance status: New 0.36
| Window SHGC | 0.25 | FenCons:SHGC |  |  |  | Window Compliance status: New 0.32 | Window Compliance status: New 0.32 | Window Compliance status: New 0.25
| Window VT | 0.42 | FenCons:VT |  |  |  | Window Compliance status: New 0.53 | Window Compliance status: New 0.53 | Window Compliance status: New 0.42
| Window overhang | NA | Win:ExtShdgObj
| Skylight overall U value | 0.58
| Skylight SHGC | 0.25
| Skylight VT | 0.49
| Daylit Area (calculated value) | Calculated by Software According to ACM section 5.4.5
Internal Load Components
| Occupancy Type | Storage Area: Commercial and Industrial Storage Areas (conditioned or unconditioned) Retail Spaces: Retail Merchandise Sales, Wholesale Showroom Front Entry: Lobby, Main Entry
| People Density | Storage Area: 333.33 ft2/person Retail Spaces: 30.30 ft2/person Front Entry: 100 ft2/person
| Sensible Heat/person | Storage Area: 275 Btu/h-person Retail Spaces: 250 Btu/h-person Front Entry: 250 Btu/h-person
| Latent Heat/person | Storage Area: 475 Btu/h-person Retail Spaces: 200 Btu/h-person Front Entry: 250 Btu/h-person
| Equipment Power Density | Storage Area: 0.2 W/ft2 Retail Spaces: 1 W/ft2 Front Entry: 0.5 W/ft2
| Lighting Power Density | Storage Area: 0.6 W/ft2 Retail Spaces: 1.2 W/ft2 Front Entry: 1.5 W/ft2 | Spc:IntLPDReg Spc:IntLtgSpecMthd Spc:IntLtgSys:TailoredMthdAllowType Spc:TMGenLPD Spc:TMTotAllowLPD | Storage Area: 0.6 W/ft2 Core Retail: 1.2 W/ft2 Front Entry: 0.95 W/ft2 Front Retail: 2.35 W/ft2 (General) - 1.6 W/ft2 (task and floor display) - 0.75 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point of Sale: 1.2 W/ft2 | Storage Area: 0.6 W/ft2 Core Retail: 1.2 W/ft2 Front Entry: 0.95 W/ft2 Front Retail: 2.35 W/ft2 (General) - 1.6 W/ft2 (task and floor display) - 0.75 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point of Sale: 1.2 W/ft2 | Storage Area: 0.6 W/ft2 Core Retail: 1.2 W/ft2 Front Entry: 0.95 W/ft2 Front Retail: 1.72 W/ft2 (General) - 1.34 W/ft2 (task and floor display) - 0.38 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point of Sale: 1.2 W/ft2 | Front Entry (new): 1.2 W/ft2 Front Retail (new): 2.35 W/ft2 (General) - 1.6 W/ft2 (task and floor display) - 0.75 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point Of Sale (new): 1.15 W/ft2 | Front Entry: 1.2 W/ft2 Front Retail: 2.35 W/ft2 (General) - 1.6 W/ft2 (task and floor display) - 0.75 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point Of Sale: 1.15 W/ft2 | Front Entry: 0.95 W/ft2 Front Retail: 1.72 W/ft2 (General) - 1.34 W/ft2 (task and floor display) - 0.38 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point Of Sale: 1.2 W/ft2 | Back Space (existing): 0.5 W/ft2 Core Retail (existing): 1.2 W/ft2 Front Entry (new): 1.2 W/ft2 Front Retail (new): 2.35 W/ft2 (General) - 1.6 W/ft2 (task and floor display) - 0.75 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point Of Sale (new): 1.15 W/ft2 | Back Space (existing): 0.5 W/ft2 Core Retail (existing): 1.2 W/ft2 Front Entry (new): 1.2 W/ft2 Front Retail (new): 2.35 W/ft2 (General) - 1.6 W/ft2 (task and floor display) - 0.75 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point Of Sale (new): 1.15 W/ft2 | Back Space (existing): 0.5 W/ft2 Core Retail (existing): 1.2 W/ft2 Front Entry (new): 0.95 W/ft2 Front Retail: 1.72 W/ft2 (General) - 1.34 W/ft2 (task and floor display) - 0.38 W/ft2 Task and floor display area - ~50% of space area closest to window (810 ft2) Point Of Sale (new): 1.2 W/ft2
| Ventilation Rate Per Person | Storage Area: 0.15 cfm/ft2 Retail Spaces: 0.20 cfm/ft2 Front Entry: 0.15 cfm/ft2
Ventilation Rate Per Area
Simulated Ventilation Rate
| Infiltration Rate | Storage Area: 0.0448 cfm/ft2 Retail Spaces: 0.0448 cfm/ft2 Front Entry: 0.0448 cfm/ft2
| Infiltration Schedule | Storage Area: AssemblyInfiltration Retail Spaces: RetailInfiltration Front Entry: AssemblyInfiltration | Spc: InfSchRef
| Infiltration Method | FlowExteriorWallArea | Spc: InfMthd
| Elevator Power | NA | Spc: DsgnInfRt
Occupancy Schedule
Equipment Schedule
| Lighting Schedule |  | Spc:IntLtgRegSchRef
Elevator Schedule
Daylighting
| Illuminance Setpoint (Adjusted Illuminance Setpoint) | Storage Area: NA Retail Spaces: 550 lux Front Entry: 125 lux | Spc:PriSideDayltgIllumSetPt | Storage Area: -Skylit: none -Primary Sidelit: none -Secondary Sidelit: none Retail Spaces: Core Retail: -Skylit: 950 lux (950 lux Adj.) -Primary Sidelit: none -Secondary Sidelit: none Front Retail -Skylit: none -Primary Sidelit: 950 lux (1425 lux Adj.) -Secondary Sidelit: 950 lux (1900 lux Adj.) Point of Sale -Skylit: none -Primary Sidelit: 950 lux (1425 lux Adj.) -Secondary Sidelit: 950 lux (1900 lux Adj.) Front Entry: -Skylit: none -Primary Sidelit: 200 lux (300 lux Adj.) -Secondary Sidelit: none | Same as user input | Storage Area: -Skylit: none -Primary Sidelit: none -Secondary Sidelit: none Retail Spaces: Core Retail: -Skylit: 950 lux (950 lux Adj.) -Primary Sidelit: none -Secondary Sidelit: none Front Retail -Skylit: none -Primary Sidelit: 950 lux (1425 lux Adj.) -Secondary Sidelit: 950 lux (1900 lux Adj.) Point of Sale -Skylit: none -Primary Sidelit: 950 lux (1425 lux Adj.) -Secondary Sidelit: 950 lux (1900 lux Adj.) Front Entry: -Skylit: none -Primary Sidelit: 200 lux (300 lux Adj.) -Secondary Sidelit: none
| Daylight Control Type | Continuos | ThrmlZn:DayltgCtrlType | Storage Area: none Retail Spaces: Continuous Front Entry: Continuous+Off | Same as user input | Storage Area: none Retail Spaces: Continuous Front Entry: none
| Controlled General Lighting Power In Primary Daylit Area | Defaulted: Lighting Power Density*(Daylit Area/Total Area) | ThrmlZn:PriSideDayltgCtrlLtgPwr | Storage Area: none Retail Spaces: Core Retail: none Front Retail: 1216 W Point of Sale: 861.69 W Front Entry: 108.58 W | Storage Area: none Retail Spaces: Core Retail: none Front Retail: 1216 W Point of Sale: 861.69 W Front Entry: 108.58 W | Storage Area: none Retail Spaces: Core Retail: none Front Retail: 1238.12 W Point of Sale: 861.69 W Front Entry: none
| Controlled General Lighting Power In Secondary Daylit Area | 0 | ThrmlZn:SecSideDayltgCtrlLtgPwr | Storage Area: none Retail Spaces: Core Retail: none Front Retail: 2592 W Point of Sale: 865.81 W Front Entry: none | Storage Area: none Retail Spaces: Core Retail: none Front Retail: 2592 W Point of Sale: 865.81 W Front Entry: none | Storage Area: none Retail Spaces: Core Retail: none Front Retail: 1244.04 W Point of Sale: 865.81 W Front Entry: none
| Controlled General Lighting Power In Skylit Daylit Area | Defaulted: Lighting Power Density*(Daylit Area/Total Area) | ThrmlZn:SkylitDayltgCtrlLtgPwr | Storage Area: none Retail Spaces: Core Retail: 20091.1 W Front Retail: none Point of Sale: none Front Entry: none | Storage Area: none Retail Spaces: Core Retail: 20091.1 W Front Retail: none Point of Sale: none Front Entry: none | Storage Area: none Retail Spaces: Core Retail: 20091.1 W Front Retail: none Point of Sale: none Front Entry: none
| Reference Position 1 | Calculated by Software According to ACM section 5.4.5 | ThrmlZn:DayltgIllumRefPt1Coord[1] ThrmlZn:DayltgIllumRefPt1Coord[2] ThrmlZn:DayltgIllumRefPt1Coord[3] | None | Calculated by Software According to ACM section 5.4.5 | Storage Area: none Retail Spaces: Core Retail: Front Retail: 8.73 ft from exterior wall; midpoint of the window on south façade Point of Sale: 8.73 ft from exterior wall; midpoint of the window on south façade Front Entry: 8.73 ft from exterior wall; midpoint of the entry door on the south façade
| Reference Position 2 | Calculated by Software According to ACM section 5.4.5 | ThrmlZn:DayltgIllumRefPt2Coord[1] ThrmlZn:DayltgIllumRefPt2Coord[2] ThrmlZn:DayltgIllumRefPt2Coord[3] | None | Calculated by Software According to ACM section 5.4.5 | Storage Area: none Retail Spaces: Core Retail: Front Retail: 17.45 ft from exterior wall; midpoint of the window on south façade Point of Sale: 17.45 ft from exterior wall; midpoint of the window on south façade Front Entry: 9.81 ft from exterior wall; .25ft from the interior wall on the west
HVAC Components
| HVAC System Type | Packaged VAV with Reheat |  |  |  |  | Air System Compliance Status: New SZAC | Same as user model | Air System Compliance Status: New Base Air System 3 (SZAC) | Air System Compliance Status: Existing PVAV with Reheat Air System Compliance Status: Existing (South Zones): SZAC | Same as user model | Existing: Same as user model Existing (South Zones): Same as user model
| Heating Type | Hot Water boiler with reheat |  |  |  |  | Coil Heating Compliance Status: New Gas Furnace | Same as user model | Coil Heating Compliance Status: New Gas Furnace | Coil Heating Compliance Status: Existing Hot Water Boiler with Reheat Coil Heating Compliance Status: Existing (South Zones): Gas Furnace | Same as user model | Existing: Same as user model Existing (South Zones): Same as user model
| Cooling Type | DX |  |  |  |  | Coil Cooling Compliance Status: New Direct Expansion (DX) | Same as user model | Coil Cooling Compliance Status: New Direct Expansion (DX) | Coil Cooling Compliance Status: Existing Direct Expansion (DX) | Same as user model | Direct Expansion (DX)
| Cooling Efficiency | EER=9.8 |  |  |  |  | Coil Cooling Compliance Status: New EER - 11.0 IEER - 12.7 | Same as user model | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat) | Coil Cooling Compliance Status: Existing (PVAV): EER - 9.8 Coil Cooling Compliance Status: Existing (South Zones): EER - 11.0 | Same as user model | Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
| Heating Efficiency | NA |  |  |  |  | Coil Heating Compliance Status: New 78% AFUE (80.0% Thermal Efficiency for reference, not input) | Same as user model | Min Req. Based on Coil Capacity < 225,000 Btu/hr: 78% AFUE or 80% Thrml >=225,000 Btu/hr: 80% Thrml | Coil Heating Compliance Status: Existing (South Zones): 78% AFUE (80.0% Thermal Efficiency for reference, not input) | Same as user model | Existing (South Zones): Min Req. Based on Coil Capacity < 225,000 Btu/hr: 78% AFUE or 80% Thrml >=225,000 Btu/hr: 80% Thrml
| System Oversizing Factor | NA |  |  |  |  | NA | Same as user model | Heating- 1.25 Cooling- 1.15 | NA | Same as user model | Heating- 1.25 Cooling- 1.15
| System Capacity | Heating Capacity - default Cooling Capacity - default |  |  |  |  | Heating Capacity - default Cooling Capacity - default | Same as user model | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat | Heating Capacity - default Cooling Capacity - default | Same as user model | Heating Coil Capacity to include: 1.25 Oversizing Sizing Factor Cooling Coil Capacity to include: 1.15 Oversizing Factor Capacity Adjustment for Fan Heat
| Design Supply Air Temperature | Cooling - 55 Heating - 70 |  |  |  |  | Cooling - 55F Heating 95F | Same as user model | Cooling - 55F Heating 95F | Air System Compliance Status: Existing PVAV with Reheat Cooling - 60F Heating 60F Air System Compliance Status: Existing (South Zones): SZAC Cooling - 55F Heating 95F | Air System Compliance Status: Existing PVAV with Reheat Cooling - 60F Heating 60F Air System Compliance Status: Existing (South Zones): SZAC Cooling - 55F Heating 95F | Air System Compliance Status: Existing PVAV with Reheat Cooling - 60F Heating 60F Air System Compliance Status: Existing (South Zones): SZAC Cooling - 55F Heating 95F
| SAT Reset Control | WarmestResetFlowFirst High - 70 F Low - 55 F |  |  |  |  | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Same as user model | No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Air System Compliance Status: Existing PVAV with Reheat WarmestResetFlowFirst High - 60 F Low - 55 F Air System Compliance Status: Existing (South Zones): SZAC No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Air System Compliance Status: Existing PVAV with Reheat WarmestResetFlowFirst High - 60 F Low - 55 F Air System Compliance Status: Existing (South Zones): SZAC No SAT Control (Htg/clg cycles on/off based on call from thermostat) | Air System Compliance Status: Existing PVAV with Reheat WarmestResetFlowFirst High - 60 F Low - 55 F Air System Compliance Status: Existing (South Zones): SZAC No SAT Control (Htg/clg cycles on/off based on call from thermostat)
| Economizer | BaseSys5 - Integrated |  |  |  |  | None | Same as user model | Integrated if load over 54 kBtu/h (If Economizer is specified) | Air System Compliance Status: Existing PVAV with Reheat Integrated Air System Compliance Status: Existing (South Zones): SZAC NA | Same as user model | Air System Compliance Status: Existing PVAV with Reheat Integrated if load over 54 kBtu/h (If Economizer is specified) Air System Compliance Status: Existing (South Zones): SZAC NA
| Economizer Limits | [5 empty] | NA | Same as user model | Differential Dry-Bulb (If Economizer is specified) | Air System Compliance Status: Existing PVAV with Reheat Differential Dry-Bulb Air System Compliance Status: Existing (South Zones): SZAC NA | Same as user model | Air System Compliance Status: Existing PVAV with Reheat Differential Dry-Bulb (If Economizer is specified) Existing (South Zones): NA
| Fan Power Specification | 24.97 |  |  |  |  | Brake Horsepower Method: Fan Compliance Status: New 3.2 bhp 0.895 Motor Eff | Same as user model | Static Pressure Method: Fan Compliance Status: New The fans are autosized. Fan Static Pressure, Fan Efficiency and Motor Efficiency are dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | Static Pressure Method: Fan Compliance Status: Existing AirSys: PVAV with Reheat 4 in H2O 0.62 Fan Eff 0.936 Motor Eff 21.67 bhp (for reference only, not input) Brake Horsepower Method: Fan Compliance Status: Existing AirSys: SZAC 3.2 bhp 0.895 Motor Eff | Same as user model | Same as user model
| Motor Horsepower | 25 |  |  |  |  | 3 | Same as user model | Motor HP is dependent on the Fan Power Specifications and is dictated by the ACM section 5.7.3.2 Base Relief Fans: The presence of the relief fan and their specifications is dictated by the ACM section 5.7.3.3 | Fan Compliance Status: Existing AirSys: PVAV with Reheat 25 Fan Compliance Status: Existing AirSys: SZAC 3.5 | Same as user model | Same as user model
| Fan Control Method | Variable flow, VSD |  |  |  |  | Constant Volume | Same as user model | Constant Volume | Fan Compliance Status: Existing AirSys: PVAV with Reheat VariableSpeedDrive Fan Compliance Status: Existing AirSys: SZAC (South Zones): Constant Volume | Same as user model | Same as user model
| Cooling Coil Curve(s) | Not Input (DXEIR_fTempCrvRef) (DXEIR_fPLFCrvRef) (DXEIR_fFlowCrvRef) |  |  |  |  | Not input | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Not input | Coil Cooling Compliance Status: Existing AirSys: PVAV with Reheat CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio Coil Cooling Compliance Status: Existing AirSys: SZAC CoilClgDXEIRRatio_fTwbToadbSI CoilClgDXEIRRatio_fQFrac CoilClgDXSnglEIRRatio_fCFMRatio | Same as proposed model
| Heating Coil Curve(s) | Not Input (FurnHIR_fPLRCrvRef) |  |  |  |  | Not input | CoilHtgFurnFIRRatio_fQRatio | CoilHtgFurnFIRRatio_fQRatio | Not input | CoilHeating Compliance Status: Existing AirSys: PVAV with Reheat NA CoilHeating Compliance Status: Existing AirSys: SZAC CoilHtgFurnFIRRatio_fQRatio | Same as proposed model
| Fan Part-load Performance Curve | Not Input
| HVAC(Availability/Fan) Schedule | Not Input |  |  |  |  | Not input | RetailHVACAvail | RetailHVACAvail | Not input | RetailHVACAvail | RetailHVACAvail
| Cooling Thermostat Schedule | Not Input |  |  |  |  | Not input | RetailClgSetPt | RetailClgSetPt | Not input | RetailClgSetPt | RetailClgSetPt
| Heating Thermostat Schedule | Not Input |  |  |  |  | Not input | RetailHtgSetPt | RetailHtgSetPt | Not input | RetailHtgSetPt | RetailHtgSetPt
| Terminal Heat Type | Hot Water
| Terminal Heat Capacity | Default
| Terminal Unit Fan Power | NA
| Reheat Delta T | NA
Boiler Components
| Number of boilers | 2 | [7 empty] | Boiler Compliance Status: Existing Qty: 2 | Same as user model | Same as user model
| Boiler Capacity | 240681 Btu/h | [7 empty] | 240681 | Same as user model | Same as user model
| Boiler Efficiency (thermal efficiency) | 82.2% | [7 empty] | 0.8225 | Same as user model | Same as user model
| Boiler Type | Mechanical Non-condensing | [7 empty] | Mechanical Non Condensing | Same as user model | Same as user model
| Boiler Heat Loss | NA
| Boiler Performance Curve | Not Input | [7 empty] | Not Input | BlrHWBlrFIRRatio_fQRatioSI | BlrHWBlrFIRRatio_fQRatioSI
| Boiler Min. Unloading Ratio | 25% | [7 empty] | 0.25 | Same as user model | Same as user model
| Hot Water Supply Temperature | 180F | [7 empty] | 180F | Same as user model | Same as user model
| Hot Water Return Temperature | 140F | [7 empty] | 140F | Same as user model | Same as user model
| Pump Control Type | ConstantSpeed | [7 empty] | ConstantSpeed | Same as user model | Same as user model
| Pump Power | 0.229 kW | [7 empty] | 0.23 kW (19.0 W/gpm) | Same as user model | Same as user model
| Pump Motor Efficiency | 89% | [7 empty] | 0.855 | Same as user model | Same as user model
| Pump Part Load Curve | Not Input
Chiller Components
| Chiller Type | NA
| Number of Chillers | NA
| Chiller Fuel | NA
| Chiller Oversizing Factor | NA
| Chiller Capacity (tons) | NA
| Chiller Efficiency | NA
| Chiller Part-Load Efficiency (IPLV) | NA
| Chiller Min. Unloading Ratio | NA
| Chiller Cooling Capacity Adjustment Curve | NA
| Chiller Cooling Efficiency Adjustment Curve | NA
| Chilled Water Supply Temperature | NA
| Chilled Water ReturnTemperature | NA
| Condensor Type | NA
| Cooling tower Fan Control Type | NA
| Cooling Tower Fan Horse Power | NA
| Cooling Tower Set Point Control | NA
| Chiller, Condenser Pump Control Type | NA
| Chiller, Condenser Pump Motor Power | NA
| Chiller, Condenser Pump Motor Efficiency | NA
| Chiller, Condenser Pump Design Flow | NA
Service Hot Water
| SWH type | Storage | WtrHtr:Type
| Fuel type | NaturalGas | WtrHtr:FuelSrc
| Thermal Efficiency | 85% | WtrHtr:ThrmlEff
| Energy Factor | 77% | WtrHtr:EF
| Hot Water Load/person (gal/h-person) | Storage Area: 0.18 gal/h-person Retail Spaces: 0.18 gal/h-person Front Entry: 0.09 gal/h-person | Spc:HotWtrHtgRt
| SHW Schedule |  | Spc:HotWtrHtgSchRef
| Tank Volume (gal) | 250 gal | WtrHtr:StorCap
| Availability Schedule | Not Input | FluidSys:AvailSchRef
| Water temperature setpoint Schedule | Fixed | FluidSys:TempCtrl
| Water temperature setpoint | 180 | FluidSys:FixedSupTemp
| Water Heater Max Capacity (Btuh) | 160000 | WtrHtr:CapRtd
| Performance Curve | Not Input | WtrHtr:HIR_fPLRCrvRef
| Standby Loss (Btuh) | 2269 | WtrHtr:StbyLoss
Note on H39: Sandeep: Checks for opaque envelope could be added at a later stage
Note on D151: Jason Acosta: this varies based on temp control

## WWR Tables (hidden)
m/ft | 0.3048
m²/ft² | 0.092903
Proposed | Total | North (315 to 45 deg) | East (45 to 135 deg) | South (135 to 225 deg) | West (225 to 315 deg)
Gross Wall Area [m2] | 11589.54 | 3476.86 | 2317.91 | 3476.86 | 2317.91
Window Opening Area [m2] | 6035.13 | 1810.54 | 1207.03 | 1810.54 | 1207.03
Window-Wall Ratio [%] | 52.07 | 52.07 | 52.07 | 52.07 | 52.07
Orientation | Gross Wall Area [ft2] | Window Opening Area [ft2] | Window-Wall Ratio [%]
Total | 124748.7703 | 64961.5987 | 52.07
North (315 to 45 deg) | 37424.6096 | 19488.4904 | 52.07
East (45 to 135 deg) | 124748.7703 | 12992.3628 | 52.07
South (135 to 225 deg) | 37424.6096 | 19488.4904 | 52.07
West (225 to 315 deg) | 124748.7703 | 12992.3628 | 52.07
| Total | North (315 to 45 deg) | East (45 to 135 deg) | South (135 to 225 deg) | West (225 to 315 deg)
Gross Wall Area [m2] | 11589.54 | 3476.86 | 2317.91 | 3476.86 | 2317.91
Window Opening Area [m2] | 4636.15 | 1390.85 | 927.23 | 1390.85 | 927.23
Window-Wall Ratio [%] | 40 | 40 | 40 | 40 | 40
Orientation | Gross Wall Area [ft2] | Window Opening Area [ft2] | Window-Wall Ratio [%]
Total | 124748.7703 | 49903.1033 | 40
North (315 to 45 deg) | 37424.6096 | 14970.9848 | 40
East (45 to 135 deg) | 24949.7756 | 9980.6207 | 40
South (135 to 225 deg) | 37424.6096 | 14970.9848 | 40
West (225 to 315 deg) | 24949.7756 | 9980.6207 | 40
Exterior Light LPD Calculation (Lighting Zone 3)
Proposed
General hardscape type | Dimensions | Area | Perimeter | a W/ft2 | b W/ft | c W | Total W
Driveway- | 20x30 | 600 | 100 | 0.075 | 0.5 | 770 | 1115
Parking Lot | 180x56 | 10080 | 472 | 0.075 | 0.5 | 770 | 6566
Sidewalk | 2(6x30) | 360 | 144 | 0.075 | 0.5 | 770 | 977
Building Entrance |  | 1 door |  |  | 90 W/door |  | 90
Hardscape Ornamental Light |  | 50 |  | 0.04 |  |  | 2
Building Façade |  | 37411 |  | 0.25 |  |  | 9352.75
Signage |  | 40 |  | 2 |  |  | 80
[6 empty] | Total | 18182.75 | W
Baseline
General hardscape type | Dimensions | Area | Perimeter | a W/ft2 | b W/ft | c W | Total W
Driveway- | 20x30 | 600 | 100 | 0.09 | 0.6 | 770 | 1184
Parking Lot | 180x56 | 10080 | 472 | 0.09 | 0.6 | 770 | 7725.2
Sidewalk | 2(6x30) | 360 | 144 | 0.09 | 0.6 | 770 | 1018.4
Building Entrance |  | 1 door |  |  | 90 W/door |  | 90
Hardscape Ornamental Light |  | 50 |  | 0.04 |  |  | 2
Building Façade |  | 37411 |  | 0.35 |  |  | 13093.85
Signage |  | 40 |  | 2.3 |  |  | 92

## Intermediate Calculations - 360 (hidden)
|  | Roof |  | Run-04 | Ext-wall |  |  | Ext-flr
| Overall Uval | 0.052994 |  |  | 0.97087 |  |  | 0.0501
| ext air film | 0.17 |  | ext air film | 0.17 |  | ext air film | 0.17
| Int air film | 0.61 |  | Int air film | 0.68 |  | Int air film | 0.92
|  | 0.18 |  |  | 0.18 |  |  | 14.58
|  | 1.03 | [5 empty] | 1.09
|  | 16.88 | [5 empty] | 0.82
2.38
SKYLIGHT AREA CALCULATIONS Warehouse Models |  | 0800-Warehouse-CECRef.cibd |  |  | Run 08 -14% |  |  |  | RUN 07 - 7% |  |  |  | RUN 09 - 5%
| Roof | 49495.9376 |  |  | 34497.2396 | 14998.6979 | 49495.9376 |  | 34497.2396 | 14998.6979 | 49495.9376 |  | 34497.2396 | 14998.6979 | 49495.9376
| Skylight (area per skylight) | 16 |  |  | 16 | 16 | 16 |  | 16 | 16 | 16 |  | 16 | 16 | 16
| Count | 46 |  |  | 300.0378 | 135.0101 | 435.0478 |  | 178.0378 | 40.0101 | 218.0478 |  | 126.0378 | 29.0101 | 155.0478
| Area | 736 |  |  | 4800.6044 | 2160.1609 | 6960.7654 |  | 2848.6044 | 640.1609 | 3488.7654 |  | 2016.6044 | 464.1609 | 2480.7654
| SRR | 1.487% |  |  | 13.92% | 14.4% | 14.06% |  | 8.257% | 4.268% | 7.049% |  | 5.846% | 3.095% | 5.012%
[5 empty] | Baseline Run 08 - 14% |  |  |  | Baseline - RUN 07 - 7% |  |  |  | Baseline RUN 09 - 5%
[5 empty] | 34497.2396 | 14998.6979 | 49495.9376 |  | 34497.2396 | 14998.6979 | 49495.9376 |  | 34497.2396 | 14998.6979 | 49495.9376
[7 empty] | 0 |  | 11.3521 | 11.3521 | 11.3521 |  |  |  | 0
[5 empty] | 300.0378 | 135.0101 | 436.0478 |  | 178.0378 | 40.0101 | 218.0478 |  | 126.0378 | 29.0101 | 156.0478
[5 empty] | 0 | 0 | 0 |  | 2021.1027 | 454.1982 | 2475.3008 |  | 0 | 0 | 0
[5 empty] | 0% | 0% | 0% |  | 5.859% | 3.028% | 5.001% |  | 0% | 0% | 0%
| Zone | Occupants/1000ft2 | Flr Ar | tot occu | Vent rt cfm/person | Vent rt - cfm/ft2 | DefDsgnVentRt-cfm | Vent Rt Cfm/ft2
| Bot_Core | 33 | 27257.7 | 899.5041 | 15 | 0.495 | 13492.6 | 0.495
| Bot_Zn1 | 10 | 3373.6 | 33.736 | 15 | 0.15 | 506.043 | 0.15
| Bot_Zn2 | 10 | 2174 | 21.74 | 15 | 0.15 | 326.106 | 0.15
| Bot_Zn3 | 33 | 3373.6 | 111.3288 | 15 | 0.495 | 1669.91 | 0.49499
| Bot_Zn4 | 33 | 2174 | 71.742 | 15 | 0.495 | 1076.15 | 0.49501
| Mid_Core | 10 | 27257.7 | 272.577 | 15 | 0.15 | 4088.66 | 0.15
| Mid_Zn1 | 10 | 3373.6 | 33.736 | 15 | 0.15 | 506.043 | 0.15
| Mid_Zn2 | 10 | 2174 | 21.74 | 15 | 0.15 | 326.106 | 0.15
| Mid_Zn3 | 10 | 3373.6 | 33.736 | 15 | 0.15 | 506.033 | 0.15
| Mid_Zn4 | 10 | 2174 | 21.74 | 15 | 0.15 | 326.106 | 0.15
| Hi_Core | 10 | 27257.7 | 272.577 | 15 | 0.15 | 4088.66 | 0.15
| Hi_Zn1 | 10 | 3373.6 | 33.736 | 15 | 0.15 | 506.043 | 0.15
| Hi_Zn2 | 10 | 2174 | 21.74 | 15 | 0.15 | 326.106 | 0.15
| Hi_Zn3 | 10 | 3373.6 | 33.736 | 15 | 0.15 | 506.033 | 0.15
| Hi_Zn4 | 10 | 2174 | 21.74 | 15 | 0.15 | 326.106 | 0.15
| Top_Core | 67 | 27257.7 | 1826.2659 | 15 | 1.005 | 27394 | 1.005
| Top_Zn1 | 10 | 3373.6 | 33.736 | 15 | 0.15 | 3390.49 | 1.005
| Top_Zn2 | 10 | 2174 | 21.74 | 15 | 0.15 | 326.106 | 0.15
| Top_Zn3 | 10 | 3373.6 | 33.736 | 15 | 0.15 | 3390.42 | 1.005
| Top_Zn4 | 10 | 2174 | 21.74 | 15 | 0.15 | 2184.91 | 1.005
| Fan Power | 360LDH
| Project | 00200-OfficeSmall_CZ6_Run18
|  | CoreZn | Perim1Zn | Perim2Zn | Perim3Zn | Perim4Zn
| Transform | User
| Modeling Method | Brake Horsepower
| CFM | 2000 | 1500 | 1000 | 1500 | 1000
| Brake Horsepower | 1.6 | 1.2 | 0.8 | 1.2 | 0.8
| Motor Efficiency | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
| Calculated Power (Watts) | 1404.2353 | 1053.1765 | 702.1176 | 1053.1765 | 702.1176
| Calculated Power (W/cfm) | 0.70212 | 0.70212 | 0.70212 | 0.70212 | 0.70212
| Transform | Baseline
| Modeling Method | Static Pressure
| CFM | 1462 | 1706 | 877 | 1242 | 950
| Supply Fan Static Pressure | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| Supply Fan Efficiency | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Motor Nominal HP | 1.5 | 1.5 | 0.75 | 1 | 0.75
| Motor Efficiency | 0.865 | 0.865 | 0.855 | 0.855 | 0.855
| Calculated Power (Watts) | 992.9769 | 1158.6994 | 602.617 | 853.4211 | 652.7778
| Calculated Power (W/cfm) | 0.67919 | 0.67919 | 0.68713 | 0.68713 | 0.68713
Run 14 - Small Office - Area Category Method, Power Adjustment Factors
| GENERAL PARMS |  | PROPOSED |  |  |  | BASELINE
|  | Area | Installed Watts | Control Credit | PAF | RegLPD | General Power
|  | Spc:FlrArea | Spc:RegInstPwr | Spc:PAFCtrlCred | WT.AVE(IntLtgSys:PAF) | Spc:IntLPDReg | Spc:RegBaseGenPwr
|  | (ft2) | (Watts) | (Watts) | (frac) | (W/ft2) | (Watts) | (W/ft2)
| Zone 1 | 1221.17 | 1152 | 57.6 | 0.05 | 0.89619 | 915.878 | 0.75
| Zone 2 | 724.411 | 640 | 32 | 0.05 | 0.8393 | 543.308 | 0.75
| Zone 3 | 1221.17 | 1152 | 57.6 | 0.05 | 0.89619 | 915.878 | 0.75
| Zone 4 | 724.411 | 640 | 32 | 0.05 | 0.8393 | 543.308 | 0.75
| Core Zone | 1610.9 | 1408 | 70.4 | 0.05 | 0.83034 | 1208.18 | 0.75
Run 01- Small Office - Envelope
| GENERAL PARMS |  | PROPOSED |  |  |  | BASELINE
|  | Area | Installed Watts | Control Credit | PAF | RegLPD | General Power
|  | Spc:FlrArea | Spc:RegInstPwr | Spc:PAFCtrlCred | WT.AVE(IntLtgSys:PAF) | Spc:IntLPDReg | Spc:RegBaseGenPwr
|  | (ft2) | (Watts) | (Watts) | (frac) | (W/ft2) | (Watts) | (W/ft2)
| Zone 1 | 1221.17 | 1099.05 | 0 | 0 | 0.9 | 915.878 | 0.75
| Zone 2 | 724.411 | 651.97 | 0 | 0 | 0.9 | 543.308 | 0.75
| Zone 3 | 1221.17 | 1099.05 | 0 | 0 | 0.9 | 915.878 | 0.75
| Zone 4 | 724.411 | 651.97 | 0 | 0 | 0.9 | 543.308 | 0.75
| Core Zone | 1610.9 | 1149.81 | 0 | 0 | 0.71377 | 1208.18 | 0.75
Run 12 - Medium Office - Tailored Method - Ornamental Allowance
| GENERAL PARMS |  |  | USER |  |  |  | PROPOSED |  | BASELINE | [5 empty] | Baseline Check
| Zone | SpcFunc | Area | IntLtgSys1 Watts | IntLtgSys2 Watts | Total Power | LPD | Installed Watts | RegLPD | General Power |  | Tailored Allowance |  | Total Power |  | Gen Ilum | Perim | Task Ht | RCR | RCRCat | General Power
|  |  | Spc:FlrArea |  |  |  |  | Spc:RegInstPwr | Spc:IntLPDReg | Spc:TMGenBasePwr |  | Spc:TMTotAllowPwr |  | Spc:RegBaseGenPwr | b:Spc:IntLPDReg
|  |  | (ft2) |  |  |  |  | (Watts) | (W/ft2) | (Watts) | (W/ft2) | (Watts) | (W/ft2) | (Watts) | (W/ft2) | (Lux)
| Core Bottom | Waiting Area | 10586.7 | 2112 | 7936 | 10048 | 0.94912 | 10048 | 0.94912 | 8469.36 | 0.8 | 2112 |  | 10582.16 | 0.99957 | 300 | 425.799 | 6 | 0.6033 | RCRCat1 | 0.64
| Perimeter_Bot_Zn _1 | Lobby, Main Entry | 2231.77 |  |  |  | 0.5 | 1115.89 | 0.5 | 1339.06 | 0.6 | 0 |  | 1339.66 | 0.60027 | 200 | 339.929 | 6 | 2.2847 | RCRCat2 | 0.6
|  |  | 10586.7 | [6 empty] | 6775.49 | 0.64 | 2112 | 0.1995 | 8888.13 | 0.83956 | 300 | 425.799 | 6 | 0.6033 | RCRCat1 | 0.8 |  | 5293.35
165.4172
Run 13 - Medium Office - Tailored Method - Task/Ornamental Allowances
| GENERAL PARMS |  |  | USER |  |  |  |  | PROPOSED |  | BASELINE | [5 empty] | Baseline Check
| Zone | SpcFunc | Area | IntLtgSys1 Watts | IntLtgSys2 Watts | IntLtgSys3 Watts | Total Power | LPD | Installed Watts | RegLPD | General Power |  | Tailored Allowance |  | Total Power |  | Gen Ilum | Perim | Task Ht | RCR | RCRCat | General Power
|  |  | Spc:FlrArea | [5 empty] | Spc:RegInstPwr | Spc:IntLPDReg | Spc:TMGenBasePwr |  | Spc:TMTotAllowPwr |  | Spc:RegBaseGenPwr | b:Spc:IntLPDReg
|  |  | (ft2) | [5 empty] | (Watts) | (W/ft2) | (Watts) | (W/ft2) | (Watts) | (W/ft2) | (Watts) | (W/ft2) | (Lux)
| Core Bottom | Waiting Area | 10586.7 | 1088 | 12704 | 6336 | 20128 | 1.9013 | 20128 | 1.9013 | 8469.36 | 0.8 | 6381.35 | 0.60277 | 14851.51 | 1.4028 | 300 | 425.799 | 6 | 0.6033 | RCRCat1 | 0.8
| Perimeter_Bot_Zn _1 | Lobby, Main Entry | 2231.77 | 1792 | 224 |  | 2016 | 0.90332 | 2016 | 0.90332 | 1339.06 | 0.6 | 224 | 0.10037 | 1563.66 | 0.70064 | 200 | 339.929 | 6 | 2.2847 | RCRCat2 | 0.6
C. Occupancy Summary Information
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Occupancy Type | Floor Area | Installed LPD | Lighting Control Credits | Allowed (Baseline) Lighting Power |  |  | Process Loads
[5 empty] | General Lighting Power | Area Category Allowances | Tailored Allowances
|  | (ft2) | (Watts) | (Watts) | (Watts) | (Watts) | (Watts) | (W/ft2)
| Spc:SpcFunc | Spc:FlrArea | Spc:RegInstPwr | Spc:PAFCtrlCred | Spc:RegBaseGenPwr | Spc:ACMTotAllowPwr | Spc:TMTotAllowPwr
030006-OffMed-Run12
| Height of space | 9 | ft
| H (Ht of luminiare abv wrk plane) | 6
Perimeter of Spc
| Zn1 | 339.929
| Zn2 | 230.763
| Zn3 | 339.929
| Zn4 | 230.762
| Core | 425.799
Area
| Zn1 | 2231.76
| Zn2 | 1412.9
| Zn3 | 2231.76
| Zn4 | 1412.8
| Core | 10586.7
RCR Irr room
| Zn1 | 2.2847
| Zn2 | 2.4499
| Zn3 | 2.2847
| Zn4 | 2.45
| Core | 0.6033
| Table 140.6-D | Gen Illumination lvl
Lobby Area: Main Entry
| Zn1 | 200
| Zn2 | 200
| Zn3 | 200
| Zn4 | 200
Waiting Area
| Core | 300
LPD of spaces from Table 140.6-G
| Zn1 | 0.8
| Zn2 | 0.8
| Zn3 | 0.8
| Zn4 | 0.8
| Core | 0.8
Note on H16: Sandeep: actuals counts of 'skylt' from Model - 436 SRR - 14.09 ~ 14%.
Note on H23: Sandeep: actuals counts of 'skylt' from Model - 436 SRR - 14.09 ~ 14%.
Note on P23: Sandeep: actuals counts of 'skylt' from Model - 436 SRR - 14.09 ~ 14%.

## Checks (hidden)
Cooling coil cap: CapTotGrossRtdSim (ab) - FanHtDsgn / CapTotGrossRtdSim (zb)
CapTotGrossRtdSim (ab) | 559512
FanHtDsgn | 52022.8
CapTotGrossRtdSim (zb) | 429209
Cooling coil cap | 1.1824
Heating coil cap: CapTotGrossRtdSim (ab) / CapTotGrossRtdSim (zb)
CapTotGrossRtdSim (ab) | 223730.5
CapTotGrossRtdSim (zb) | 178984.6
Heating coil cap | 1.25
Boiler
Pwr Per Flow | 19
Mtr Eff | 0.855
Impeller Efficiency | 0.7
Flow Cap | 14.6695
TotHd | 60.3958
bhp | 0.31962
Pump Pwr | 0.27872
| 19 | W/gpm
AFUE (Coil Heating Furnace) | 82.37 |  | 0.8225 | 0.8225
Et | 0.8225
Fan
CFM | 7186.89
Tot Static Pressure | 3
Overall Efficiency | 0.6
bhp | 5.6563
SEER TO EER
SEER | 13
EER | 10.8446
COP | 3.1784
EER | 12.96
COP | 3.7984
12.9656
Pump Power calculations
hp (One motor size less than the user Input hp) | 0.75
MHPi-1 (95% of hp - assumed to be one motor size less than user input hp) | 0.7125
gpm | 30
head | 65.86
sp grav of water | 1
mtr eff | 0.9
impeller eff | 0.7
HP | 0.79197
BHP | 0.71277
Pump Power | 0.59049