## Documentation Main Sheet (hidden)
General Details | Model/Software Details
Test Name | Model Revision no. | Rev4376
Model File Name | Version of Ruleset (Trunk rev. No.) | Rev4376
Climate Zone | CBECC Software | CBECC-Com 2016.2.1
| Date Tested | Upated 09/18/2016
Testing Performed by

## Test Status Summary
Ruleset Implementation Tests - Test Specification Status | [12 empty] | Status of Example Test Files - Detailed Geometry |  | Status of Example Test Files - Simplified Geometry
Test No | Building Type | Test Name | Compliance Type | Test Category | Test Criteria | Notes | Version 2016.1.0 | Additional notes | Version 2016.2.1 | Additional notes | Streamlined Set | Additional notes | Example Test File Status | Example Test File Path | Example Test File Status | Example Test File Path
1 | Small Office | 020006-OffSml-Run01 | NewComplete | Exterior Envelope | Envelope and window assembly performance |  | X | [5 empty] | Status: Date: Version: |  | Status: Date: Version:
2 | Small Office | 020006-OffSml-Run02 | NewComplete | Exterior Envelope | Envelope and window assembly performance |  | X | [5 empty] | Status: Date: Version: |  | Status: Date: Version:
3 | Small Hotel | 070015-HotSml-Run03 | NewComplete | Exterior Envelope, Fenestration and HVAC | Envelope and window assembly performance Ventilation strategies - OA via system, DOAS, natural ventilation and Ventilation induced via exhaust fans. |  | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na
4 | Medium Office | 030006-OffMed-Run04 | NewComplete | Exterior Envelope | Envelope minimum requirements |  | X | [5 empty] | Status: Date: Version: |  | Status: Date: Version:
5 | Large Office | 040006-OffLrg-Run05 | NewComplete | Fenestration | Window Wall Ratio (WWR) |  | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
6 | Large Office | 040006-OffLrg-Run06 | NewComplete | Fenestration | Window Wall Ratio (WWR) |  | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
7 | Warehouse | 080006-Whse-Run07 | NewComplete | Skylight | Skylight to Roof Ratio (SRR) and Skylight Performance |  | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
8 | Warehouse | 080006-Whse-Run08 | NewComplete | Skylight | Skylight to Roof Ratio (SRR) and Daylit Area | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
9 | Warehouse | 080006-Whse-Run09 | NewComplete | Skylight | SRR and Daylit Area | Adding/Enlarging Skylights to meet 140.3C daylit area requirements currently not supported | [6 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
10 | Medium Office | 030006-OffMed-Run10 | NewComplete | Space Function | Internal Loads- Complete Bldg method | Complete Building test method currently not supported | [6 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
11 | Large Office | 040006-OffLrg-Run11 | NewComplete | Space Function | Internal loads - Space-by-Space |  | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na
12 | Medium Office | 030006-OffMed-Run12 | NewComplete | Lighting | Lighting - tailored lighting method |  | X | [5 empty] | Status: Date: Version: |  | Status: Date: Version:
13 | Medium Office | 030006-OffMed-Run13 | NewComplete | Lighting | Lighting - tailored lighting method |  | X | [5 empty] | Status: Date: Version: |  | Status: Date: Version:
14 | Small Office | 020006-OffSml-Run14 | NewComplete | Lighting | Lighting - Power Adjustment Factors (PAF) rules |  | X | [5 empty] | Status: Date: Version: |  | Status: Date: Version:
15 | Warehouse | 080006-Whse-Run15 | NewComplete | Lighting Control | Daylighting | Exclude Test for Simplified Geometry: Only daylighting parameters are being tested. | X | [5 empty] | Status: Date: Version: |  | Status: Date: Version: | Test Excluded for Simplified geometry
16 | Medium Retail | 050006-RetlMed-Run16 | NewComplete | Lighting Control | Lighting and daylighting | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
17 | Large Office | 040006-OffLrg-Run17 | NewComplete | Ext.Lighting/SHW | Ext. Lighting/SHW | Prescriptive Exterior Lighting Compliance not supported | [6 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
18 | Small Office | 020006-OffSml-Run18 | NewComplete | HVAC | HVAC - SZAC |  | X | [5 empty] | Status: Date: Version: |  | Status: Date: Version:
19 | Medium Office | 030006-OffMed-Run19 | NewComplete | HVAC | HVAC - PVAV and CRAC |  | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na
20 | Large Office | 040006-OffLrg-Run20 | NewComplete | HVAC | HVAC - VAV and CRAH |  | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na
21 | Warehouse | 080006-Whse-Run21 | NewComplete | HVAC | HVAC - SZAC and HV |  | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
22 | Hotel | 070015-HotSml-Run22 | NewComplete | HVAC | HVAC - PVAV, SZAC and FPFC |  | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na
23 | Medium Office | 030006-OffMed-Run23 | ExistingAlteration | Exterior Envelope, Fenestration and HVAC | Window alteration and HVAC replacement |  | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na
24 | Small Office | 020006-OffSml-Run24 | ExistingAlteration | Fenestration and HVAC | Window alteration and HVAC replacement |  | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na
25 | Small Office | 020006-OffSml-Run25 | ExistingAlteration | Fenestration | Window alteration |  | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
26 | Small Office | 020006-OffSml-Run26 | ExistingAlteration | Fenestration | Window alteration |  | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
27 | Retail Medium | 050006-RetlMed-Run27 | ExistingAddition | Fenestration and HVAC | Addition modeled alone: Envelope performance, window assembly performance and HVAC - SZAC |  | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
28 | Retail Medium | 050006-RetlMed-Run28 | ExistingAdditionAndAlteration | Exterior Envelope, Fenestration and HVAC | Addition modeled with an altered existing building: Envelope performance, Window Wall Ratio (WWR) and HVAC - SZAC |  | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na
29 | Medium Office | 030006-OffMed-Run29 | NewEnvelope | Exterior Envelope and HVAC | Envelope and correct assignment of proposed HVAC systems. |  | X | [5 empty] | Status: Date: Version: |  | Status: Test Not Performed Date: Version: | na
30 | Medium Office | 030006-OffMed-Run30 | NewMechanicalAndPartialLighting | HVAC and Partial Lighting | New/exisiting lighting and HVAC - PVAV | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | X |  | X |  |  |  | Status: Verified Date: Version: CBECC-Com 2016.2.1 |  | Status: Test Not Performed Date: Version: | na

## 020006-OffSml-Run01 (hidden)
General Details |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 020006-OffSml-Run01 |  | Model Revision no. | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006-OffSml-Run01.cibd16 |  | Version of Ruleset (Trunk rev. No.) | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  | Testing Performed by | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [5 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof | x | Steep | WoodFramingAndOtherRoof |  | 0.044 |  | 0.78 |  | 0.78 |  | 0.75 |  | 0.25
Exterior Wall | NACM_Wood Framed Wall | - | - | WoodFramingAndOtherWall |  | 0.091 | - | - | - | -
Above-grade Floor | NACM_Conc Raised FLr | - | - | MassFloor |  | 0.039 | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit | - | - | OtherFloor |  | 0.07 | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow |  | FixedWindow | 0.25 |  | 0.2 |  | 0.45
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Wood Framed Wall |  | Stucco - 7/8 in. | Building Paper - 1/16 in. |  | Wood framed wall, 16in. OC, 4.0in., R-15 |  | Gypsum Board - 1/2 in. | - | - | - | -
Roof | NACM_Roof |  | Asphalt roll roofing - 1/4 in. | Hardboard - HDF - 50 lb/ft3 - 3/4 in. |  | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit |  | Plywood - 3/4 in. | Wood framed floor, 16in. OC, 4.0in., R-15 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Conc Raised FLr |  | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | Concrete - 80 lb/ft3 - 4 in. |  | Metal Deck - 1/16 in. |  | OSB - Oriented Strand Board - 5/8 in. |  | 5) Carpet - 3/4 in. | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | SteepNonresWoodFramingAndOtherRoofU049 |  | Steep | WoodFramingAndOtherRoof |  | 0.049 |  | 0.85 |  | 0.85 |  | 0.2 |  | 0.92
Exterior Wall | MetalFrameWallU069 | - | - | MetalFrameWall |  | 0.069 | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU071 | - | - | OtherFloor |  | 0.071 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow |  | FixedWindow | 0.36 |  | 0.25 |  | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  | CodeItem | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU069 |  | Stucco - 7/8 in. | Compliance Insulation R10.06 |  | Compliance Insulation R2.00 |  | Compliance Insulation R0.20 |  | Compliance Insulation R0.10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
Roof | SteepNonresWoodFramingAndOtherRoofU049 |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R19.63 | - | - | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU071 |  | Compliance Insulation R9.83 | Plywood - 5/8 in. |  | Carpet - 3/4 in. | - | - | - | - | - | - | - | -
Note on H40: Sandeep: Values currenlty not being reported at the construction

## 020015-OffSml-Run02 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020015-OffSml-Run02 |  | Model Revision no. |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020015-OffSml-Run02.cibd16 |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-15 |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.) |  | On/Below Grade Floor F-factor (Btu/h-°F-ft2) |  | Total Perimeter Area (ft2) |  | Total Perimeter exposed (ft)
| ConsAssmRef:Name |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs |  | ConsAssmRef:FFactor |  | UndgrFlr:Area |  | UndgrFlr:PerimExposed
Roof | NACM_Roof |  | Steep |  | WoodFramingAndOtherRoof |  | 0.053 |  | 0.7 |  | 0.7 |  | 0.6 |  | 0.4 | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | - | - |  | MetalFrameWall |  | 0.056 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit | - | - |  | OtherFloor |  | 0.07 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
On/Below Grade Floor | NACM_Slab Floor | - | - | - | NA (Slab -on grade) | - | - | - | - | - | - | - | - | - | - |  | 0.7 |  | 3891.16 |  | 302.82
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow |  | FixedWindow |  | 0.25 |  | 0.2 |  | 0.45
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Metal Framed Wall |  | Stucco - 7/8 in. |  | Building Paper - 1/16 in. |  | Expanded Polystyrene - EPS - 3 in. R13 |  | Metal framed wall, 16in. OC, 5.5in., R-19 |  | Gypsum Board - 1/2 in. | - | -
Roof | NACM_Roof |  | Asphalt roll roofing - 1/4 in. |  | Hardboard - HDF - 50 lb/ft3 - 3/4 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit |  | Plywood - 3/4 in. |  | Wood framed floor, 16in. OC, 4.0in., R-15 | - | - | - | - | - | - | - | -
Shading Objects
ExtShdgObj
Shading Objects on Windows
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.) |  | On/Below Grade Floor F-factor (Btu/h-°F-ft2) |  | Total Perimeter Area (ft2) |  | Total Perimeter exposed (ft)
| ConsAssmRef:Name |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs |  | ConsAssmRef:FFactor |  | UndgrFlr:Area |  | UndgrFlr:PerimExposed
Roof | SteepNonresWoodFramingAndOtherRoofU034 |  | Steep |  | WoodFramingAndOtherRoof |  | 0.034 |  | 0.85 |  | 0.85 |  | 0.2 |  | 0.92 | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU062 | - | - |  | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU039 | - | - |  | OtherFloor |  | 0.039 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
On/Below Grade Floor | SlabOnOrBelowGradeF073 | - | - | - | NA (Slab -on grade) | - | - | - | - | - | - | - | - | - | - |  | 0.73 |  | 3891.16 |  | 302.82
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU062 |  | Stucco 7/8 in. |  | Compliance Insulation R13.99 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Roof | SteepNonresWoodFramingAndOtherRoofU034 |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R28.63 | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU039 |  | Compliance Insulation R21.39 |  | Plywood - 5/8 in. |  | Carpet - 3/4 in. | - | - | - | - | - | -
Shading Objects
ExtShdgObj
NO - Shading Objects on Windows
Note on H43: Sandeep: Values currenlty not being reported at the construction

## 070015-HotSml-Run03
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 070015-HotSml-Run03 |  |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 070015-HotSml-Run03.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-15 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Hotel |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof |  |  | Low |  | WoodFramingAndOtherRoof |  | 0.055 |  | 0.7 |  | 0.7 |  | 0.6 |  | 0.4
Exterior Wall | NACM_Mtl Framed Wall |  | - | - |  | MetalFrameWall |  | 0.082 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Ext.Conc Raised FLr |  | - | - |  | MassFloor |  | 0.058 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
| Window Non-res Fixed |  |  | FixedWindow |  | 0.25 |  | 0.2 |  | 0.47
| Window Res Operable |  |  | OperableWindow |  | 0.42 |  | 0.18 |  | 0.35
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | NACM_Roof | New |  | Metal Standing Seam - 1/16 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Wall | NACM_Mtl Framed Wall | New |  | Stucco - 7/8 in. |  | Expanded Polystyrene - EPS - 2 7/16 in. R10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 3/8 in. | - | - | - | -
Above-grade Floor | NACM_Ext.Conc Raised FLr | New |  | Metal Deck - 1/16 in. |  | Concrete - 80 lb/ft3 - 4 in. |  | Expanded Polystyrene - EPS - 1 7/8 in. R8.0 |  | Expanded Polyurethane - 3/4 in. R4.7 |  | Carpet - 3/4 in. | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low) |  | Fixed Temperature
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
None | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55 | - | -
None | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55 | - | -
None | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55 | - | -
None | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55 | - | -
GuestRoom202_205 Thermal Zone | 2nd Floor DOAS | New |  | Guest Rooms: Floor 2 |  | SZAC |  | ResidentialLivingHVACAvail | - | - | - | - |  | FixedDualSetpoint | - | - | - | - |  | 72
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl
Residential Units: Levels 1-3 | Residential Units: FPFC (All) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
Residential Units: Level 4 | Residential Units: Zonal Exhaust Systems | New |  | Residential Units: Floor 4 |  | Exhaust |  | ResidentialLivingHVACAvail | - | - | - | - |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 11.4 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 11 |  | 12.7 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Residential Units: FPFC (All) | Residential Units: FPFC CoilClg (All) | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
2nd Floor DOAS | DOAS CoilClg | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
Residential Units: FPFC (All) | Residential Units: FPFC CoilHtg (All) | New |  | HotWater | - | - | - | - | - | -
2nd Floor DOAS | DOAS CoilHtg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 14146.3 |  | 14.3828 |  | 0.62 |  | 4 |  | 15 |  | 0.924
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1646.78 |  | 1.5571 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1674.51 |  | 1.5833 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1721.44 |  | 1.6277 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Residential Units: Floor1 | GuestRoom101_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom102_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom103_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom104_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom105_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom201_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom202_205_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom206_208_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom209_212_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom213_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom214_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom215_218_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom219_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom220_223_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom224_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom301_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom302_305_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom306_308_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom309_312_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom313_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom314_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom315_318_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom319_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom320_323_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom324_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom401_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom402_405_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom406_408_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom409_412_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom413_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom414_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom415_418_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom419_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom420_423_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom424_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom401-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 50 |  | 0.033255 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom402_405-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom406_408-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom409_412-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom413-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom414-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom415_418-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom419-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom420_423-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom424-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor2 | DOAS SupFan | New |  | ConstantVolume |  | StaticPressure |  | 720 |  | 0.56733 |  | 0.5 |  | 2.5 |  | 0.75 |  | 0.855
AirSystem - Name | OA - Control Name | Status |  | Economizer Control |  | Economizer Integration
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
2nd Floor DOAS | DOAS OACtrl | New |  | NoEconomizer |  | Undefined
Ventilation and Thermostat schedules
Thermal Zone - Name | Conditioning Type | Status |  | Space Floor Area (ft2) |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  |  |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
CorridorFlr1 Thermal Zone | Conditioned | New |  | 1620 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 8.1 |  | 0 |  | 0.15 |  | 243 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr2 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr3 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr4 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
EmployeeLoungeFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
ExerciseCenterFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontLoungeFlr1 Thermal Zone | Conditioned | New |  | 1755.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 125.4 |  | 15 |  | 0.15 |  | 1881 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontOfficeFlr1 Thermal Zone | Conditioned | New |  | 1404 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 7.02 |  | 0 |  | 0.15 |  | 211 |  | OfficeClgSetpt |  | OfficeHtgSetpt
LaundryRoomFlr1 Thermal Zone | Conditioned | New |  | 1053 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 5.27 |  | 0 |  | 0.15 |  | 158 |  | OfficeClgSetpt |  | OfficeHtgSetpt
MechanicalRoomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 3 |  | 0.53 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
MeetingRoomFlr1 Thermal Zone | Conditioned | New |  | 864.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 61.74 |  | 15 |  | 0.15 |  | 926 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr1 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr2 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr3 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr4 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr1 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr2 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr3 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr4 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RestroomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
Space Name | Conditioning Type | Status |  | Space Function |  | Thermal Zone - Name |  | Space Floor Area (ft2) |  | Number of Residential Living or Hotel/Motel units in a modeled space |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerArea (cfm/ft2) |  | Simulated VentFlow (cfm) |  | Infiltration Method |  | Required Ventilation - Simulated as Infiltration (cfm) |  | Infiltration Schedule |  | Exhaust Flow (cfm) | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
Spc:Name | ThrmlZn:Type |  |  | SpcFunc |  | ThrmlZn:Name |  |  |  | Spc:ResLivingUnitCnt |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerAreaSim |  | ThrmlZn:VentFlow |  | (InfMthd index="1") |  | (DsgnInfRt index="1") |  | (InfSchRef index="1") |  | ThrmlZn:VentPerAreaSim | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
GuestRoom101 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom101 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom102 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom102 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom103 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom103 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom104 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom104 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom105 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom105 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom201 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom201 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom202_205 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom202_205 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 |  | 120 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom206_208 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom206_208 Thermal Zone |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | 0.079358 |  | 90 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom209_212 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom209_212 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 |  | 120 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom213 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom213 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom214 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom214 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom215_218 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom215_218 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 |  | 120 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom219 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom219 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom220_223 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom220_223 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 |  | 120 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom224 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom224 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 |  | 30 | - | - | - | - | - | - | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom301 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom301 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom302_305 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom302_305 Thermal Zone |  | 1404.1 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.51 | - | - | - | - |  | FlowSpace |  | 120 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom306_308 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom306_308 Thermal Zone |  | 1134.1 |  | 3 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 2.84 | - | - | - | - |  | FlowSpace |  | 90 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom309_312 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom309_312 Thermal Zone |  | 1404.1 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.51 | - | - | - | - |  | FlowSpace |  | 120 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom313 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom313 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom314 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom314 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom315_318 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom315_318 Thermal Zone |  | 1404 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.51 | - | - | - | - |  | FlowSpace |  | 120 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom319 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom319 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom320_323 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom320_323 Thermal Zone |  | 1404 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.51 | - | - | - | - |  | FlowSpace |  | 120 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom324 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom324 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom401 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom401 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 50 |  | On |  | 50 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom402_405 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom402_405 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 | - | - | - | - |  | FlowSpace |  | 120 |  | On |  | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom406_408 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom406_408 Thermal Zone |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 | - | - | - | - |  | FlowSpace |  | 90 |  | On |  | 90 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom409_412 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom409_412 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 | - | - | - | - |  | FlowSpace |  | 120 |  | On |  | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom413 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom413 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On |  | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom414 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom414 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On |  | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom415_418 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom415_418 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 | - | - | - | - |  | FlowSpace |  | 120 |  | On |  | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom419 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom419 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On |  | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom420_423 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom420_423 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 | - | - | - | - |  | FlowSpace |  | 120 |  | On |  | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom424 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom424 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 | - | - | - | - |  | FlowSpace |  | 30 |  | On |  | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 363000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Electric |  | Fluid |  | 348000 |  | 4.51 (0.78 kW/ton) |  | 0.5 |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 18.14 |  | 0.34 (19.0 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 18.14 |  | 0.34 (19.0 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 85 |  | 1.19 (14 W/gpm) |  | 1.5 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 34.79 |  | 0.45 (12.9 W/gpm) |  | 0.75 |  | 40.87 |  | 0.855 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 425184 |  | 85 |  | 1.42 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Non-Residential Roof | FlatNonresWoodFramingAndOtherRoofU034 |  |  | Low |  | WoodFramingAndOtherRoof |  | 0.034 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Residential Roof | FlatResWoodFramingAndOtherRoofU028 |  |  | Low |  | WoodFramingAndOtherRoof |  | 0.028 |  | 0.85 |  | 0.85 |  | 0.55 |  | 0.45
NonResidential - Exterior Wall | MetalFrameWallU062 |  | - | - |  | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | -
Residential - Exterior Wall | MetalFrameWallU048 |  | - | - |  | MetalFrameWall |  | 0.048 | - | - | - | - | - | - | - | -
Residential and NonResidential - Above-grade Floor | OtherFloorU039 |  | - | - |  | OtherFloor |  | 0.039 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
| Window Non-res Fixed/Window Res Operable |  |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
| Window Non-res Fixed/Window Res Operable |  |  | OperableWindow |  | 0.46 |  | 0.22 |  | 0.32
Constructions/Layers
Opaque
Type | Construction Assembly Name |  |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
NonResidential - Exterior Wall | MetalFrameWallU062 |  |  | Stucco 7/8 in. |  | Compliance Insulation R13.99 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Residential - Exterior Wall | MetalFrameWallU048 |  |  | Stucco 7/8 in. |  | Compliance Insulation R14.60 |  | Compliance Insulation R2.00 |  | Compliance Insulation R2.00 |  | Compliance Insulation R0.10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
NonResidential - Roof | FlatNonresWoodFramingAndOtherRoofU034 |  |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R28.63 | - | - | - | - | - | - | - | - | - | -
Residential - Roof | FlatResWoodFramingAndOtherRoofU028 |  |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R34.93 | - | - | - | - | - | - | - | - | - | -
Residential and NonResidential - Above-grade Floor | OtherFloorU039 |  |  | Compliance Insulation R21.39 |  | Plywood - 5/8 in. |  | Carpet - 3/4 in. | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Common Areas: Floor 1 | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 2 | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 3 | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 4 | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl
Residential Units: All Floors | Residential Units: FPFC (All) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 11 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys2 | Residential Units: BaseSys2 CoilClg (All) | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys2 | Residential Units: BaseSys2 CoilHtg (All) | New |  | HotWater | - | - |  | 1.25 | - | -
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 9664.19 |  | 8.8841 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | -
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1472.18 |  | 1.392 |  | 0.5 |  | 3 |  | 1.5 |  | 0.865 | - | -
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1470.83 |  | 1.3907 |  | 0.5 |  | 3 |  | 1.5 |  | 0.865 | - | -
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1730.38 |  | 1.6362 |  | 0.5 |  | 3 |  | 2 |  | 0.865 | - | -
Residential Units: All Floors | BaseSys2 Fan | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 167.96 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-2 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 169.99 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-3 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 165 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-4 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 161.61 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-5 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 162.07 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-6 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 182.53 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-7 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 152.25 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-8 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 153.09 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-9 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 140.542 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-10 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 140.64 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-11 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 137.4 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-12 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 135.105 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-13 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 137.26 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-14 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 134.587 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-15 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 136.28 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-16 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 170.8 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-17 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 142.12 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-18 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 151.863 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-19 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 140.24 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-20 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 140.84 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-21 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 137.9 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-22 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 137.02 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-23 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 136.09 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-24 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 135.75 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-25 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 134.75 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-26 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 198.59 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-27 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 165.835 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-28 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 182.003 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-29 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 165.13 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-30 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 165.94 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-31 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 161.6 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-32 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 160.197 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-33 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 159.65 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-34 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 158.41 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-35 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 157.81 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Common Areas: Floor 1 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 9220.01 |  | 2.7244 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | -
Common Areas: Floor 2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1365.53 |  | 0.40349 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
Common Areas: Floor 3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1364.17 |  | 0.40309 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
Common Areas: Floor 4 | BaseRelief Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1623.73 |  | 0.47979 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys2 | - | New | - | - | - | -
Ventilation and Thermostat Schedules
Thermal Zone - Name | Conditioning Type | Status |  | Space Floor Area (ft2) |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  |  |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
CorridorFlr1 Thermal Zone | Conditioned | New |  | 1620 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 8.1 |  | 0 |  | 0.15 |  | 243 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr2 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr3 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr4 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
EmployeeLoungeFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
ExerciseCenterFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontLoungeFlr1 Thermal Zone | Conditioned | New |  | 1755.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 125.4 |  | 15 |  | 0.15 |  | 1881 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontOfficeFlr1 Thermal Zone | Conditioned | New |  | 1404 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 7.02 |  | 0 |  | 0.15 |  | 211 |  | OfficeClgSetpt |  | OfficeHtgSetpt
LaundryRoomFlr1 Thermal Zone | Conditioned | New |  | 1053 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 5.27 |  | 0 |  | 0.15 |  | 158 |  | OfficeClgSetpt |  | OfficeHtgSetpt
MechanicalRoomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 3 |  | 0.53 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
MeetingRoomFlr1 Thermal Zone | Conditioned | New |  | 864.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 61.74 |  | 15 |  | 0.15 |  | 926 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr1 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr2 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr3 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr4 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr1 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr2 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr3 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr4 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RestroomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
Space Name | Conditioning Type | Status |  | Space Function |  | Thermal Zone - Name |  | Space Floor Area (ft2) |  | Number of Residential Living or Hotel/Motel units in a modeled space |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Infiltration Method |  | Required Ventilation - Simulated as Infiltration (cfm) |  | Infiltration Schedule |  | Exhaust Flow (cfm) |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
Spc:Name | ThrmlZn:Type |  |  | Spc:SpcFunc |  | ThrmlZn:Name |  |  |  | Spc:ResLivingUnitCnt |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | (InfMthd index="1") |  | (DsgnInfRt index="1") |  | (InfSchRef index="1") |  | ThrmlZn:VentPerAreaSim |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
GuestRoom101 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom101 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom102 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom102 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom103 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom103 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom104 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom104 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom105 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom105 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom201 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom201 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom202_205 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom202_205 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom206_208 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom206_208 Thermal Zone |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | FlowSpace |  | 90 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom209_212 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom209_212 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom213 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom213 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom214 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom214 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom215_218 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom215_218 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom219 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom219 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom220_223 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom220_223 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom224 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom224 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom301 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom301 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom302_305 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom302_305 Thermal Zone |  | 1404.1 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom306_308 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom306_308 Thermal Zone |  | 1134.1 |  | 3 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 2.84 |  | FlowSpace |  | 90 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom309_312 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom309_312 Thermal Zone |  | 1404.1 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom313 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom313 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom314 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom314 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom315_318 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom315_318 Thermal Zone |  | 1404 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom319 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom319 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom320_323 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom320_323 Thermal Zone |  | 1404 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom324 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom324 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom401 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom401 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On |  | 50 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom402_405 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom402_405 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom406_408 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom406_408 Thermal Zone |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | FlowSpace |  | 90 |  | On |  | 90 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom409_412 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom409_412 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom413 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom413 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom414 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom414 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom415_418 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom415_418 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom419 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom419 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom420_423 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom420_423 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom424 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom424 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 250993 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Electric |  | Fluid |  | 302965 |  | 4.51 (0.78 kW/ton) | - | - |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 12.54 |  | 0.24 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 74.004 |  | 1.04 (14 W/gpm) |  | 1.5 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 30.285 |  | 0.39 (12.8 W/gpm) |  | 0.5 |  | 40.7574 |  | 0.855 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 12.54 |  | 0.24 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 370160 |  | 74 |  | 1.23 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Note on P139: Sandeep: Multiplier of 0.5 has been added.
Note on V171: Sandeep: Multiplier of 0.5 has been added.
Note on AD198: Sandeep: 151123: Exhaust flow rate increased to be more than the required ventilation rate.
Note on AH198: Sandeep: 151123: Exhaust flow rate increased to be more than the required ventilation rate.
Note on P217: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on N219: Sandeep: Chiller Type: Screw, Path B Efficiency Cap <75 Tons = 0.78 kW/Ton Cap <150 Tons = 0.75 kW/Ton Cap <300 Tons = 0.68 kW/Ton Cap >=300 Tons = 0.625 kW/Ton EER = 12 / (kW/ton) COP = EER / 3.412
Note on J222: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on H283: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H305: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on R305: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T305: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on N307: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62%
Note on P307: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N308: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62%
Note on P308: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N309: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62%
Note on P309: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N310: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62%
Note on P310: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N346: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P346: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on P347: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on P348: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on P349: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on P362: Sandeep: Multiplier of 0.5 has been added.
Note on V394: Sandeep: Multiplier of 0.5 has been added.
Note on H434: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.
Note on P439: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on R439: Sandeep: The standard design 'Chiller Min Unloading Ratio' is determined based on the 'Chiller Type'. Screw = 15% See ACM ' Default Minimum Unloading Ratios Table-48 for further details
Note on F441: Sandeep: 'The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller, equally sized >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons.
Note on H441: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on J441: Sandeep: Standard Design The baseline chiller is always assumed to have a water-cooled condenser, although the chiller type will change depending on the design capacity.
Note on L441: Sandeep: Auto-sized. The full load output of the chiller operating at rating temperatures and flows including adjustment for pump heat and the project sizing ratio.
Note on N441: Sandeep: Chiller Type: Screw, Path B Efficiency Cap <75 Tons = 0.78 kW/Ton Cap <150 Tons = 0.75 kW/Ton Cap <300 Tons = 0.68 kW/Ton Cap >=300 Tons = 0.625 kW/Ton EER = 12 / (kW/ton) COP = EER / 3.412
Note on R449: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on P451: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L179) Impeller Efficiency: 0.7
Note on R451: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on P452: Sandeep: For condenser water pumps, Head: 45 ft
Note on R452: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on P453: Sandeep: For chilled water pumps, 40 ft plus an additional allowance of 0.03 ft/ton, but not to exceed 100 ft.
Note on R453: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on P454: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L180) Impeller Efficiency: 0.7
Note on R454: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower

## 030006-OffMed-Run04 (hidden)
General Details |  |  |  | Model/Software Details |  |  |  |  | Key
Test Name |  |  | 030006-OffMed-Run04 | Model Revision no. | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name |  |  | 030006-OffMed-Run04.cibd16 | Version of Ruleset (Trunk rev. No.) | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone |  |  | CZ-06 | CBECC Software | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type |  |  | Medium Office | Date Tested | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category |  |  | Exterior Envelope | Testing Performed by | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type |  |  | NewComplete |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Building Geometry
Opaque
Type | Construction Assembly Name |  | Slope Category | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType | ConsType | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl | ConsAssmRef:ExtSolAbs
Exterior Wall | NACM_Metal Framed Wall | - | - | MetalFrameWall | 0.189 | - | - | - | -
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 | Layers -2 | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem | CodeItem | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Metal Framed Wall |  | Stucco - 7/8 in. | Building Paper - 1/16 in. | Expanded Polystyrene - EPS - 3/4 in. R3.1 |  | Wood framed wall, 16in. OC, 4.0in., R-15 |  | Gypsum Board - 1/2 in. | - | -
Simulation
Error: The area weigted average u-factor of new Metal Frame Walls in the project. '0.189', exceed the maximum allaowable value, '0.151', violating Section 120.7. evaluating rule: Set CHECKCODE Proj:MtlFrmWallUFac[7] (15:'ContructAssembly.rule' line 6413) |  |  | Simulation Aborts

## 040006-OffLrg-Run05 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 040006-OffLrg-Run05 | Model Revision no. | Rev4376 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 040006-OffLrg-Run05 .cibd16 | Version of Ruleset (Trunk rev. No.) | Rev4376 |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2016.2.1 |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office | Date Tested | Upated 09/18/2016 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration | Testing Performed by | 0 |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.52 | 0.52 | 0.52 | 0.52 |  | 0.52
Baseline
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4

## 040006-OffLrg-Run06 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 040006-OffLrg-Run06 | Model Revision no. | Rev4376 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 040006-OffLrg-Run06 .cibd16 | Version of Ruleset (Trunk rev. No.) | Rev4376 |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2016.2.1 |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office | Date Tested | Upated 09/18/2016 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration | Testing Performed by | 0 |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.46 | 0.5 | 0.45 | 0.39 |  | 0.5
Baseline
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.4 | 0.45 | 0.4 | 0.35 |  | 0.4

## 080006-Whse-Run07 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 080006-Whse-Run07 | Model Revision no. | Rev4376 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006-Whse-Run07.cibd16 | Version of Ruleset (Trunk rev. No.) | Rev4376 |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2016.2.1 |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse | Date Tested | Upated 09/18/2016 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Skylight | Testing Performed by | 0 |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Building Geometry
Fenestrations
Type | Skylight to Roof Ratio (Frac) | Skylight Curb | Skylight Glazing | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| CondSRR | FenConsRef:SkyltCurb | FenConsRef:SkyltGlz | FenConsRef:Ufactor |  | FenConsRef:SHGC | FenConsRef:VT
Skylight | 0.07 | CurbMounted | Glass | 0.55 |  | 0.2 | 0.4
Baseline
Building Geometry
Fenestrations
Type | Skylight to Roof Ratio (Frac) | Skylight Curb | Skylight Glazing | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| CondSRR | FenConsRef:SkyltCurb | FenConsRef:SkyltGlz | FenConsRef:Ufactor |  | FenConsRef:SHGC | FenConsRef:VT
Skylights | 0.05 | CurbMounted | Glass | 0.58 |  | 0.25 | 0.49

## 080006-Whse-Run08 (hidden)
General Details |  | Model/Software Details |  |  |  |  | Key
Test Name | 080006-Whse-Run08 | Model Revision no. | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006-Whse-Run08.cibd16 | Version of Ruleset (Trunk rev. No.) | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse | Date Tested | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Skylight | Testing Performed by | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Daylighting
Fenestrations
Type |  | Skylight to Roof Ratio (Frac)
CondSRR
Skylight |  | 0.14
Daylight Area | Space Function | Daylight Control Type | Total Floor Area (ft2) |  | Skylit Daylit Area (ft2) |  | Skylit Daylighting Control Lighting Fraction (frac)
|  | Spc:DayltgCtrlType | FlrArea |  | SkylitDaylitArea |  | SkylitDayltgCtrlLtgFrac
Zone1 Office | Office (Greater than 250 square feet in floor area) | Continuous | 2550 | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Continuous | 12449 |  | 12300 |  | 0.99
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Continuous | 34497 |  | 34324 |  | 0.99
Baseline
Daylighting
Fenestrations
Type |  | Skylight to Roof Ratio (Frac)
CondSRR
Skylight |  | 0.05
Daylight Area | Space Function | Daylight Control Type | Total Floor Area (ft2) |  | Skylit Daylit Area (ft2) |  | Skylit Daylighting Control Lighting Fraction (frac)
|  | Spc:DayltgCtrlType | FlrArea |  | SkylitDaylitArea |  | SkylitDayltgCtrlLtgFrac
Zone1 Office | Office (Greater than 250 square feet in floor area) | Continuous | 2550 | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Continuous | 12449 |  | 12441 |  | 0.99
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Continuous | 34497 |  | 34176 |  | 0.99

## 040006-OffLrg-Run11
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 040006-OffLrg-Run11 |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 040006-OffLrg-Run11.cibd16 |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Space Function |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed | [37 empty] | vvv Insert below | [33 empty] | vvv Insert below
Internal Load Components | [37 empty] | Space Interior Loads Electric Use Report | [33 empty] | Space Interior Loads Electric Use Report
Space | [42 empty] | Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated | [17 empty] | Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated
Space Name | Space Function |  | Space Floor Area (ft2) |  | People Density (ppl/1000ft2) |  | People (total number) |  | Occupancy Density - Schedule Name |  | Sensible Heat/person (Btu/h-person) |  | Latent Heat/person (Btu/h-person) |  | Lighting Power Density (W/ft2) |  | LPD - Schedule Name |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name |  | Hot Water Load/person (gal/h-person) |  | SHW Schedule |  | Ventilation Specification Method |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Cooling Thermostat Schedule |  | Heating Thermostat Schedule |  |  | Space |  |  |  |  | Interior Lighting |  |  |  | Interior Lighting |  |  |  | Receptacle |  |  |  | Process |  |  |  | Commercial Refrigeration | [12 empty] | Space |  |  |  |  | Interior Lighting |  |  |  | Interior Lighting |  |  |  | Receptacle |  |  |  | Process |  |  |  | Commercial Refrigeration
Spc |  |  |  |  | OccDens |  |  |  | OccSchRef:Name |  | OccSensHtRt |  | OccLatHtRt |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | RecptPwrDens |  | RecptSchRef:Name |  | Spc:HotWtrHtgRt |  | Spc:HotWtrHtgSchRef |  | (VentSpecMthd) |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZnRef:ClgTstatSchRef |  | ThrmlZnRef:HtgTstatSchRef |  |  | Name | Conditioning Type | Space Function | Floor Area | Multiplier | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | [9 empty] | Name | Conditioning Type | Space Function | Floor Area | Multiplier | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use
Basement Spc | Office (Greater than 250 square feet in floor area) | X | 38353 | X | 5 | X | 191.77 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 5753 | X | OfficeClgSetPt | X | OfficeHtgSetPt | [5 empty] | (ft2) |  | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | [12 empty] | (ft2) |  | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh)
Core_bottom | Retail Merchandise Sales, Wholesale Showroom | X | 27257.64 | X | 16.665 | X | 454.25 | X | RetailOccupancy | X | 250 | X | 200 | X | 1 | X | RetailLights | X | 1 | X | RetailReceptacle | X | 0.18 | X | RetailServiceHotWater | X | Maximum | X | 15 | X | 0.2 | X | 6814 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 38353 | 1 | 0.75 | OfficeLights | 2253.1 | 64809.8 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 164275 | [17 empty] | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 38353 | 1 | 0.75 | OfficeLights | 2253.1 | 64809.8 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 164275
GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - |  |  | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | 1 | 1 | RetailLights | 3459.4 | 94295.1 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 99118.3 | [17 empty] | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | 1 | 1.2 | RetailLights | 3459.4 | 113154 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 99118.3
Perimeter_bot_ZN_1 | Lobby, Main Entry | X | 3373.61 | X | 33.335 | X | 112.46 | X | RetailOccupancy | X | 250 | X | 250 | X | 0.95 | X | RetailLights | X | 0.5 | X | RetailReceptacle | X | 0.09 | X | RetailServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 1687 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 1 | [29 empty] | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 1
Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | X | 2174.05 | X | 5 | X | 10.87 | X | RetailOccupancy | X | 250 | X | 250 | X | 0.5 | X | RetailLights | X | 0.2 | X | RetailReceptacle | X | 0 | X | RetailServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 326 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | 3373.61 | 1 | 0.95 | RetailLights | 3459.4 | 11087.1 |  |  |  |  | 0.5 | RetailReceptacle | 3636.35 | 6133.82 | [17 empty] | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | 3373.61 | 1 | 0.95 | RetailLights | 3459.4 | 11087.1 |  |  |  |  | 0.5 | RetailReceptacle | 3636.35 | 6133.82
Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom | X | 3373.63 | X | 16.665 | X | 56.22 | X | RetailOccupancy | X | 250 | X | 200 | X | 1 | X | RetailLights | X | 1 | X | RetailReceptacle | X | 0.18 | X | RetailServiceHotWater | X | Maximum | X | 15 | X | 0.2 | X | 843 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 1 | 0.5 | RetailLights | 3459.4 | 3760.46 |  |  |  |  | 0.2 | RetailReceptacle | 3636.35 | 1581.12 | [17 empty] | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 1 | 0.6 | RetailLights | 3459.4 | 4512.55 |  |  |  |  | 0.2 | RetailReceptacle | 3636.35 | 1581.12
Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom | X | 2174.04 | X | 16.665 | X | 36.23 | X | RetailOccupancy | X | 250 | X | 200 | X | 1 | X | RetailLights | X | 1 | X | RetailReceptacle | X | 0.18 | X | RetailServiceHotWater | X | Maximum | X | 15 | X | 0.2 | X | 543 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | 1 | 1 | RetailLights | 3459.4 | 11670.8 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 12267.7 | [17 empty] | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | 1 | 1.2 | RetailLights | 3459.4 | 14004.9 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 12267.7
Core_mid | Medical and Clinical Care | X | 27257.6 | X | 5 | X | 136.29 | X | HealthOccupancy | X | 250 | X | 200 | X | 1 | X | HealthLights | X | 1.5 | X | HealthReceptacle | X | 0.24 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.2 | X | 5452 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | 1 | 1 | RetailLights | 3459.4 | 7520.86 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 7905.55 | [17 empty] | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | 1 | 1.2 | RetailLights | 3459.4 | 9025.03 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 7905.55
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - |  |  | Core_mid | DirectlyConditioned | Medical and Clinical Care | 27257.6 | 5 | 1 | HealthLights | 2806.45 | 382486 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 622660 | [17 empty] | Core_mid | DirectlyConditioned | Medical and Clinical Care | 27257.6 | 5 | 1.2 | HealthLights | 2806.45 | 458983 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 622660
Perimeter_mid_ZN_1 | Medical and Clinical Care | X | 3373.61 | X | 5 | X | 16.87 | X | HealthOccupancy | X | 250 | X | 200 | X | 1 | X | HealthLights | X | 1.5 | X | HealthReceptacle | X | 0.24 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.2 | X | 675 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 5 | [29 empty] | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 5
Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | X | 2174.05 | X | 5 | X | 10.87 | X | HealthOccupancy | X | 250 | X | 250 | X | 0.5 | X | HealthLights | X | 0.2 | X | HealthReceptacle | X | 0 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 326 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | 3373.61 | 5 | 1 | HealthLights | 2806.45 | 47339.4 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 77065.1 | [17 empty] | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | 3373.61 | 5 | 1.2 | HealthLights | 2806.45 | 56807.3 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 77065.1
Perimeter_mid_ZN_3 | Medical and Clinical Care | X | 3373.63 | X | 5 | X | 16.87 | X | HealthOccupancy | X | 250 | X | 200 | X | 1 | X | HealthLights | X | 1.5 | X | HealthReceptacle | X | 0.24 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.2 | X | 675 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 5 | 0.5 | HealthLights | 2806.45 | 15253.4 |  |  |  |  | 0.2 | HealthReceptacle | 3045.8 | 6621.72 | [17 empty] | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 5 | 0.6 | HealthLights | 2806.45 | 18304.1 |  |  |  |  | 0.2 | HealthReceptacle | 3045.8 | 6621.72
Perimeter_mid_ZN_4 | Medical and Clinical Care | X | 2174.04 | X | 5 | X | 10.87 | X | HealthOccupancy | X | 250 | X | 200 | X | 1 | X | HealthLights | X | 1.5 | X | HealthReceptacle | X | 0.24 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.2 | X | 435 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | 3373.63 | 5 | 1 | HealthLights | 2806.45 | 47339.7 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 77065.6 | [17 empty] | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | 3373.63 | 5 | 1.2 | HealthLights | 2806.45 | 56807.6 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 77065.6
Core_hi | Office (Greater than 250 square feet in floor area) | X | 27257.65 | X | 5 | X | 136.288 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Sum | X | 0 | X | 0.16197 | X | 4415 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | 2174.04 | 5 | 1 | HealthLights | 2806.45 | 30506.6 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 49662.6 | [17 empty] | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | 2174.04 | 5 | 1.2 | HealthLights | 2806.45 | 36607.9 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 49662.6
HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - |  |  | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 27257.6 | 5 | 0.75 | OfficeLights | 2253.1 | 230303 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 583756 | [17 empty] | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 27257.6 | 5 | 0.75 | OfficeLights | 2253.1 | 230303 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 583756
Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) | X | 3373.61 | X | 5 | X | 16.87 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 506 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 5 | [29 empty] | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 5
Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | X | 2174.05 | X | 5 | X | 10.87 | X | OfficeOccupancy | X | 250 | X | 250 | X | 0.5 | X | OfficeLights | X | 0.2 | X | OfficeReceptacle | X | 0 | X | OfficeServiceHotWater | X | NoVentilation | X | 0 | X | 0 | X | 0 | X | NONE | X | NONE |  |  | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.61 | 5 | 0.75 | OfficeLights | 2253.1 | 28504.1 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 72250.1 | [17 empty] | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.61 | 5 | 0.75 | OfficeLights | 2253.1 | 28504.1 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 72250.1
Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) | X | 3373.63 | X | 5 | X | 16.87 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 506 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 5 | 0.5 | OfficeLights | 2253.1 | 12245.9 |  |  |  |  | 0.2 | OfficeReceptacle | 2855.5 | 6208 | [17 empty] | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 5 | 0.6 | OfficeLights | 2253.1 | 14695.1 |  |  |  |  | 0.2 | OfficeReceptacle | 2855.5 | 6208
Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) | X | 2174.03 | X | 5 | X | 10.87 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 326 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.63 | 5 | 0.75 | OfficeLights | 2253.1 | 28504.3 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 72250.6 | [17 empty] | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.63 | 5 | 0.75 | OfficeLights | 2253.1 | 28504.3 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 72250.6
Core_top | Convention, Conference, Multipurpose and Meeting Center Areas | X | 27257.6 | X | 33.335 | X | 908.63 | X | AssemblyOccupancy | X | 245 | X | 155 | X | 1.2 | X | AssemblyLights | X | 1 | X | AssemblyReceptacle | X | 0.09 | X | AssemblyServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 13629 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 2174.04 | 5 | 0.75 | OfficeLights | 2253.1 | 18368.7 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 46559.7 | [17 empty] | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 2174.04 | 5 | 0.75 | OfficeLights | 2253.1 | 18368.7 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 46559.7
Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas | X | 3373.61 | X | 33.335 | X | 112.46 | X | AssemblyOccupancy | X | 245 | X | 155 | X | 1.2 | X | AssemblyLights | X | 1 | X | AssemblyReceptacle | X | 0.09 | X | AssemblyServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 1688 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | 1 | 1.2 | AssemblyLights | 3340.2 | 109255 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 104641 | [17 empty] | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | 1 | 1.2 | AssemblyLights | 3340.2 | 109255 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 104641
Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | X | 2174.05 | X | 5 | X | 10.87 | X | AssemblyOccupancy | X | 250 | X | 250 | X | 0.5 | X | AssemblyLights | X | 0.2 | X | AssemblyReceptacle | X | 0 | X | AssemblyServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 326 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | 1 | 1.2 | AssemblyLights | 3340.2 | 13522.2 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 12951.1 | [17 empty] | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | 1 | 1.2 | AssemblyLights | 3340.2 | 13522.2 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 12951.1
Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas | X | 3373.6 | X | 33.335 | X | 112.46 | X | AssemblyOccupancy | X | 245 | X | 155 | X | 1.2 | X | AssemblyLights | X | 1 | X | AssemblyReceptacle | X | 0.09 | X | AssemblyServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 1688 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 1 | 0.5 | AssemblyLights | 3340.2 | 3630.88 |  |  |  |  | 0.2 | AssemblyReceptacle | 3838.95 | 1669.21 | [17 empty] | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 1 | 0.6 | AssemblyLights | 3340.2 | 4357.06 |  |  |  |  | 0.2 | AssemblyReceptacle | 3838.95 | 1669.21
Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas | X | 2174.04 | X | 33.335 | X | 72.47 | X | AssemblyOccupancy | X | 245 | X | 155 | X | 1.2 | X | AssemblyLights | X | 1 | X | AssemblyReceptacle | X | 0.09 | X | AssemblyServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 1088 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | 1 | 1.2 | AssemblyLights | 3340.2 | 13522.3 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 12951.2 | [17 empty] | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | 1 | 1.2 | AssemblyLights | 3340.2 | 13522.3 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 12951.2
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - |  |  | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | 1 | 1.2 | AssemblyLights | 3340.2 | 8714.06 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 8346.01 | [17 empty] | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | 1 | 1.2 | AssemblyLights | 3340.2 | 8714.06 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 8346.01
[38 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 1 | [29 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 1
Ventilation
Building Story
Name | Floor Multiplier |  | Floor Area (ft2) |  | Ventilation (cfm)
Basement | 1 |  | 38353 | X | 5753
GroundFloor | 1 |  | 38353 | X | 10214
MidFloor | 5 |  | 191764.9 | X | 7562
HiFloor | 5 |  | 191764.9 | X | 5753
TopFloor | 1 |  | 38353 | X | 18416
Baseline
Internal Load Components | [39 empty] | Space Loads Report | [33 empty] | Space Loads Report
Space | [39 empty] | Space | [5 empty] | Occupancy |  |  |  |  | Service Hot Water |  | Ventilation | [5 empty] | Infiltration |  |  | Thermal Zone | [11 empty] | Space | [5 empty] | Occupancy |  |  |  |  | Service Hot Water |  | Ventilation | [5 empty] | Infiltration |  |  | Thermal Zone
Space Name | Space Function |  | Space Floor Area (ft2) |  | People Density (ppl/1000ft2) |  | People (total number) |  | Occupancy Density - Schedule Name |  | Sensible Heat/person (Btu/h-person) |  | Latent Heat/person (Btu/h-person) |  | Lighting Power Density (W/ft2) |  | LPD - Schedule Name |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name |  | Hot Water Load/person (gal/h-person) |  | SHW Schedule |  | Specification Method |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Cooling Thermostat Schedule |  | Heating Thermostat Schedule |  |  | Name | Conditioning Type | Space Function | Floor Area | Story Name | Multiplier | Density | Number | Schedule Name | Sensible Heat Rate | Latent Heat Rate | SHW Use | Schedule Name | Prop. DsgnVentPerArea | Prop. DsgnVentPerPerson | Code VentPerArea | Code VentPerPerson | Sim. Area Flow | Sim. Person Flow | Method | Schedule Name | Design Infiltration Rate | Clg Tstat Sch | Htg Tstat Sch | [10 empty] | Name | Conditioning Type | Space Function | Floor Area | Story Name | Multiplier | Density | Number | Schedule Name | Sensible Heat Rate | Latent Heat Rate | SHW Use | Schedule Name | Prop. DsgnVentPerArea | Prop. DsgnVentPerPerson | Code VentPerArea | Code VentPerPerson | Sim. Area Flow | Sim. Person Flow | Method | Schedule Name | Design Infiltration Rate | Clg Tstat Sch | Htg Tstat Sch
Spc |  |  |  |  | OccDens |  |  |  | OccSchRef:Name |  | OccSensHtRt |  | OccLatHtRt |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | RecptPwrDens |  | RecptSchRef:Name |  | Spc:HotWtrHtgRt |  | Spc:HotWtrHtgSchRef |  | (VentSpecMthd) |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZnRef:ClgTstatSchRef |  | ThrmlZnRef:HtgTstatSchRef | [5 empty] | (ft2) |  |  | (ppl/1000ft2) | (people) |  | (Btu/h-person) | (Btu/h-person) | (gal/min) |  | (cfm/ft2) | (cfm/person) | (cfm/ft2) | (cfm/person) | (cfm) | (cfm) |  |  | (cfm/ft2) | [15 empty] | (ft2) |  |  | (ppl/1000ft2) | (people) |  | (Btu/h-person) | (Btu/h-person) | (gal/min) |  | (cfm/ft2) | (cfm/person) | (cfm/ft2) | (cfm/person) | (cfm) | (cfm) |  |  | (cfm/ft2)
Basement Spc | Office (Greater than 250 square feet in floor area) | X | 38353 | X | 5 | X | 191.8 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 5753 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 38352.9727 | Basement | 1 | 5 | 191.765 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 30 | 0.15 | 30 | 5752.95 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 38352.9727 | Basement | 1 | 5 | 191.765 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 30 | 0.15 | 30 | 5752.95 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
Core_bottom | Retail Merchandise Sales, Wholesale Showroom | X | 27257.6387 | X | 16.665 | X | 454.2 | X | RetailOccupancy | X | 250 | X | 200 | X | 1.2 | X | RetailLights | X | 1 | X | RetailReceptacle | X | 0.18 | X | RetailServiceHotWater | X | Maximum | X | 15 | X | 0.2 | X | 6813 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 27257.6387 | GroundFloor | 1 | 16.665 | 454.249 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.24998 | 15 | 0.24998 | 15 | 5451.53 | 6813.73 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 27257.6387 | GroundFloor | 1 | 16.665 | 454.249 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.24998 | 15 | 0.24998 | 15 | 5451.53 | 6813.73 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - |  |  | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | GroundFloor | 1 | -99996 | 0 |  | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | GroundFloor | 1 | -99996 | 0 |  | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Perimeter_bot_ZN_1 | Lobby, Main Entry | X | 3373.6 | X | 33.335 | X | 112.5 | X | RetailOccupancy | X | 250 | X | 250 | X | 0.95 | X | RetailLights | X | 0.5 | X | RetailReceptacle | X | 0.09 | X | RetailServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 1688 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | 3373.6125 | GroundFloor | 1 | 33.335 | 112.459 | RetailOccupancy | 250 | 250 | 0.09 | RetailServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 506.042 | 1686.89 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | 3373.6125 | GroundFloor | 1 | 33.335 | 112.459 | RetailOccupancy | 250 | 250 | 0.09 | RetailServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 506.042 | 1686.89 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | X | 2174.1 | X | 5 | X | 10.9 | X | RetailOccupancy | X | 250 | X | 250 | X | 0.6 | X | RetailLights | X | 0.2 | X | RetailReceptacle | X | 0 | X | RetailServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 326 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.0508 | GroundFloor | 1 | 5 | 10.8703 | RetailOccupancy | 250 | 250 | 0 | RetailServiceHotWater | 0.15 | 30 | 0.15 | 30 | 326.108 | 0 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.0508 | GroundFloor | 1 | 5 | 10.8703 | RetailOccupancy | 250 | 250 | 0 | RetailServiceHotWater | 0.15 | 30 | 0.15 | 30 | 326.108 | 0 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom | X | 3373.6 | X | 16.665 | X | 56.2 | X | RetailOccupancy | X | 250 | X | 200 | X | 1.2 | X | RetailLights | X | 1 | X | RetailReceptacle | X | 0.18 | X | RetailServiceHotWater | X | Maximum | X | 15 | X | 0.2 | X | 843 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 3373.6348 | GroundFloor | 1 | 16.665 | 56.2216 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.24998 | 15 | 0.24998 | 15 | 674.727 | 843.324 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 3373.6348 | GroundFloor | 1 | 16.665 | 56.2216 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.24998 | 15 | 0.24998 | 15 | 674.727 | 843.324 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom | X | 2174 | X | 16.665 | X | 36.2 | X | RetailOccupancy | X | 250 | X | 200 | X | 1.2 | X | RetailLights | X | 1 | X | RetailReceptacle | X | 0.18 | X | RetailServiceHotWater | X | Maximum | X | 15 | X | 0.2 | X | 543 | X | RetailClgSetPt | X | RetailHtgSetPt |  |  | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 2174.0356 | GroundFloor | 1 | 16.665 | 36.2303 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.24998 | 15 | 0.24998 | 15 | 434.807 | 543.455 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 2174.0356 | GroundFloor | 1 | 16.665 | 36.2303 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.24998 | 15 | 0.24998 | 15 | 434.807 | 543.455 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
Core_mid | Medical and Clinical Care | X | 27257.6 | X | 5 | X | 136.3 | X | HealthOccupancy | X | 250 | X | 200 | X | 1.2 | X | HealthLights | X | 1.5 | X | HealthReceptacle | X | 0.24 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.15216 | X | 4147 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Core_mid | DirectlyConditioned | Medical and Clinical Care | 27257.6387 | MidFloor | 5 | 5 | 136.288 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 40 | 0.15 | 30 | 5451.53 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Core_mid | DirectlyConditioned | Medical and Clinical Care | 27257.6387 | MidFloor | 5 | 5 | 136.288 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 40 | 0.15 | 30 | 5451.53 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - |  |  | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | MidFloor | 5 | -99996 | 0 |  | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | MidFloor | 5 | -99996 | 0 |  | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Perimeter_mid_ZN_1 | Medical and Clinical Care | X | 3373.6 | X | 5 | X | 16.9 | X | HealthOccupancy | X | 250 | X | 200 | X | 1.2 | X | HealthLights | X | 1.5 | X | HealthReceptacle | X | 0.24 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.15216 | X | 513 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | 3373.6125 | MidFloor | 5 | 5 | 16.8681 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 40 | 0.15 | 30 | 674.723 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | 3373.6125 | MidFloor | 5 | 5 | 16.8681 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 40 | 0.15 | 30 | 674.723 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | X | 2174.1 | X | 5 | X | 10.9 | X | HealthOccupancy | X | 250 | X | 250 | X | 0.6 | X | HealthLights | X | 0.2 | X | HealthReceptacle | X | 0 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.11412 | X | 248 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.0508 | MidFloor | 5 | 5 | 10.8703 | HealthOccupancy | 250 | 250 | 0 | HealthServiceHotWater | 0.15 | 30 | 0.15 | 30 | 326.108 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.0508 | MidFloor | 5 | 5 | 10.8703 | HealthOccupancy | 250 | 250 | 0 | HealthServiceHotWater | 0.15 | 30 | 0.15 | 30 | 326.108 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
Perimeter_mid_ZN_3 | Medical and Clinical Care | X | 3373.6 | X | 5 | X | 16.9 | X | HealthOccupancy | X | 250 | X | 200 | X | 1.2 | X | HealthLights | X | 1.5 | X | HealthReceptacle | X | 0.24 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.15216 | X | 513 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | 3373.6348 | MidFloor | 5 | 5 | 16.8682 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 40 | 0.15 | 30 | 674.727 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | 3373.6348 | MidFloor | 5 | 5 | 16.8682 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 40 | 0.15 | 30 | 674.727 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
Perimeter_mid_ZN_4 | Medical and Clinical Care | X | 2174 | X | 5 | X | 10.9 | X | HealthOccupancy | X | 250 | X | 200 | X | 1.2 | X | HealthLights | X | 1.5 | X | HealthReceptacle | X | 0.24 | X | HealthServiceHotWater | X | Maximum | X | 0 | X | 0.15216 | X | 331 | X | HealthClgSetPt | X | HealthHtgSetPt |  |  | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | 2174.0356 | MidFloor | 5 | 5 | 10.8702 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 40 | 0.15 | 30 | 434.807 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | 2174.0356 | MidFloor | 5 | 5 | 10.8702 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 40 | 0.15 | 30 | 434.807 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
Core_hi | Office (Greater than 250 square feet in floor area) | X | 27257.6 | X | 5 | X | 136.3 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.16197 | X | 4415 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 27257.6387 | HiFloor | 5 | 5 | 136.288 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.16197 | 32.3946 | 0.15 | 30 | 4415 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 27257.6387 | HiFloor | 5 | 5 | 136.288 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.16197 | 32.3946 | 0.15 | 30 | 4415 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - |  |  | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | HiFloor | 5 | -99996 | 0 |  | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | HiFloor | 5 | -99996 | 0 |  | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) | X | 3373.6 | X | 5 | X | 16.9 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 506 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.6125 | HiFloor | 5 | 5 | 16.8681 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 30 | 0.15 | 30 | 506.042 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.6125 | HiFloor | 5 | 5 | 16.8681 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 30 | 0.15 | 30 | 506.042 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | X | 2174.1 | X | 5 | X | 10.9 | X | OfficeOccupancy | X | 250 | X | 250 | X | 0.6 | X | OfficeLights | X | 0.2 | X | OfficeReceptacle | X | 0 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0 | X | 0 | X | NONE | X | NONE |  |  | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.0508 | HiFloor | 5 | 5 | 10.8703 | OfficeOccupancy | 250 | 250 | 0 | OfficeServiceHotWater | 0 | 0 | 0.15 | 30 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.0508 | HiFloor | 5 | 5 | 10.8703 | OfficeOccupancy | 250 | 250 | 0 | OfficeServiceHotWater | 0 | 0 | 0.15 | 30 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) | X | 3373.6 | X | 5 | X | 16.9 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 506 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.6348 | HiFloor | 5 | 5 | 16.8682 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 30 | 0.15 | 30 | 506.045 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.6348 | HiFloor | 5 | 5 | 16.8682 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 30 | 0.15 | 30 | 506.045 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) | X | 2174 | X | 5 | X | 10.9 | X | OfficeOccupancy | X | 250 | X | 200 | X | 0.75 | X | OfficeLights | X | 1.5 | X | OfficeReceptacle | X | 0.18 | X | OfficeServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 326 | X | OfficeClgSetPt | X | OfficeHtgSetPt |  |  | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 2174.0356 | HiFloor | 5 | 5 | 10.8702 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 30 | 0.15 | 30 | 326.105 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 2174.0356 | HiFloor | 5 | 5 | 10.8702 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 30 | 0.15 | 30 | 326.105 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
Core_top | Convention, Conference, Multipurpose and Meeting Center Areas | X | 27257.6 | X | 33.335 | X | 908.6 | X | AssemblyOccupancy | X | 245 | X | 155 | X | 1.2 | X | AssemblyLights | X | 1 | X | AssemblyReceptacle | X | 0.09 | X | AssemblyServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 13629 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6387 | TopFloor | 1 | 33.335 | 908.633 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 4088.65 | 13629.5 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6387 | TopFloor | 1 | 33.335 | 908.633 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 4088.65 | 13629.5 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas | X | 3373.6 | X | 33.335 | X | 112.5 | X | AssemblyOccupancy | X | 245 | X | 155 | X | 1.2 | X | AssemblyLights | X | 1 | X | AssemblyReceptacle | X | 0.09 | X | AssemblyServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 1688 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.6125 | TopFloor | 1 | 33.335 | 112.459 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 506.042 | 1686.89 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.6125 | TopFloor | 1 | 33.335 | 112.459 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 506.042 | 1686.89 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | X | 2174.1 | X | 5 | X | 10.9 | X | AssemblyOccupancy | X | 250 | X | 250 | X | 0.6 | X | AssemblyLights | X | 0.2 | X | AssemblyReceptacle | X | 0 | X | AssemblyServiceHotWater | X | Maximum | X | 0 | X | 0.15 | X | 326 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.0508 | TopFloor | 1 | 5 | 10.8703 | AssemblyOccupancy | 250 | 250 | 0 | AssemblyServiceHotWater | 0.15 | 30 | 0.15 | 30 | 326.108 | 0 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.0508 | TopFloor | 1 | 5 | 10.8703 | AssemblyOccupancy | 250 | 250 | 0 | AssemblyServiceHotWater | 0.15 | 30 | 0.15 | 30 | 326.108 | 0 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas | X | 3373.6 | X | 33.335 | X | 112.5 | X | AssemblyOccupancy | X | 245 | X | 155 | X | 1.2 | X | AssemblyLights | X | 1 | X | AssemblyReceptacle | X | 0.09 | X | AssemblyServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 1688 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.6348 | TopFloor | 1 | 33.335 | 112.46 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 506.045 | 1686.9 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.6348 | TopFloor | 1 | 33.335 | 112.46 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 506.045 | 1686.9 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas | X | 2174 | X | 33.335 | X | 72.5 | X | AssemblyOccupancy | X | 245 | X | 155 | X | 1.2 | X | AssemblyLights | X | 1 | X | AssemblyReceptacle | X | 0.09 | X | AssemblyServiceHotWater | X | Maximum | X | 15 | X | 0.15 | X | 1088 | X | AssemblyClgSetPt | X | AssemblyHtgSetPt |  |  | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.0356 | TopFloor | 1 | 33.335 | 72.4715 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 326.105 | 1087.07 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.0356 | TopFloor | 1 | 33.335 | 72.4715 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.50003 | 15 | 0.50003 | 15 | 326.105 | 1087.07 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - |  |  | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | TopFloor | 1 | -99996 | 0 |  | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | TopFloor | 1 | -99996 | 0 |  | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Ventilation
Building Story | [37 empty] | Space Interior Lighting Report | [33 empty] | Space Interior Lighting Report
Name | Floor Multiplier |  | Floor Area (ft2) |  | Ventilation (cfm) | [32 empty] | Space |  |  |  |  | Regulated | [7 empty] | Non-Regulated | [20 empty] | Space |  |  |  |  | Regulated | [10 empty] | Non-Regulated
[38 empty] | Name | Conditioning Type | Space Function | Lighting Status | Floor Area | Lighting Specification Method | Installed Power | Schedule Name | Schedule | Lighting System Count | Lighting Control Credit | Simulated Power | Simulated LPD | Power | Schedule Name | Schedule | LPD | [17 empty] | Name | Conditioning Type | Space Function | Lighting Status | Floor Area | Lighting Specification Method | Installed Power | Schedule Name | Schedule | Lighting System Count | Lighting Control Credit | General Lighting Power | Area Category Allowances | Tailored Allowances | Simulated Power | Simulated LPD | Power | Schedule Name | Schedule | LPD
Basement | 1 |  | 38353 | X | 5753 | [36 empty] | (ft2) |  | (Watts) |  | (FLH) |  | (Watts) | (Watts) | (Watts/ft2) | (Watts) |  | (FLH) | (Watts/ft2) | [21 empty] | (ft2) |  | (Watts) |  | (FLH) |  | (Watts) | (Watts) | (Watts) | (Watts) | (Watts) | (Watts/ft2) | (Watts) |  | (FLH) | (Watts/ft2)
GroundFloor | 1 |  | 38353 | X | 10214 | [32 empty] | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 38353 | AreaCategoryMethod | 28764.7 | OfficeLights | 2253.1 | -99996 | 0 | 28764.7 | 0.75 | [21 empty] | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 38353 | AreaCategoryMethod | 0 | OfficeLights | 2253.1 | -99996 | 0 | 28764.7 | 0 | 0 | 28764.7 | 0.75
MidFloor | 5 |  | 191764.9 | X | 7562 | [32 empty] | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 27257.6 | AreaCategoryMethod | 27257.6 | RetailLights | 3459.4 | -99996 | 0 | 27257.6 | 1 | [21 empty] | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 27257.6 | AreaCategoryMethod | 0 | RetailLights | 3459.4 | -99996 | 0 | 32709.2 | 0 | 0 | 32709.2 | 1.2
HiFloor | 5 |  | 191764.9 | X | 5753 | [32 empty] | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0 | [29 empty] | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
TopFloor | 1 |  | 38353 | X | 18416 | [32 empty] | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | New | 3373.61 | AreaCategoryMethod | 3204.93 | RetailLights | 3459.4 | -99996 | 0 | 3204.93 | 0.95 | [21 empty] | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | New | 3373.61 | AreaCategoryMethod | 0 | RetailLights | 3459.4 | -99996 | 0 | 3204.93 | 0 | 0 | 3204.93 | 0.95
[38 empty] | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | AreaCategoryMethod | 1087.03 | RetailLights | 3459.4 | -99996 | 0 | 1087.03 | 0.5 | [21 empty] | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | AreaCategoryMethod | 0 | RetailLights | 3459.4 | -99996 | 0 | 1304.43 | 0 | 0 | 1304.43 | 0.6
[38 empty] | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 3373.63 | AreaCategoryMethod | 3373.63 | RetailLights | 3459.4 | -99996 | 0 | 3373.63 | 1 | [21 empty] | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 3373.63 | AreaCategoryMethod | 0 | RetailLights | 3459.4 | -99996 | 0 | 4048.36 | 0 | 0 | 4048.36 | 1.2
[38 empty] | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 2174.04 | AreaCategoryMethod | 2174.04 | RetailLights | 3459.4 | -99996 | 0 | 2174.04 | 1 | [21 empty] | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 2174.04 | AreaCategoryMethod | 0 | RetailLights | 3459.4 | -99996 | 0 | 2608.84 | 0 | 0 | 2608.84 | 1.2
[38 empty] | Core_mid | DirectlyConditioned | Medical and Clinical Care | New | 27257.6 | AreaCategoryMethod | 27257.6 | HealthLights | 2806.45 | -99996 | 0 | 27257.6 | 1 | [21 empty] | Core_mid | DirectlyConditioned | Medical and Clinical Care | New | 27257.6 | AreaCategoryMethod | 0 | HealthLights | 2806.45 | -99996 | 0 | 32709.2 | 0 | 0 | 32709.2 | 1.2
[38 empty] | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0 | [29 empty] | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
[38 empty] | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | New | 3373.61 | AreaCategoryMethod | 3373.61 | HealthLights | 2806.45 | -99996 | 0 | 3373.61 | 1 | [21 empty] | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | New | 3373.61 | AreaCategoryMethod | 0 | HealthLights | 2806.45 | -99996 | 0 | 4048.34 | 0 | 0 | 4048.34 | 1.2
[38 empty] | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | AreaCategoryMethod | 1087.03 | HealthLights | 2806.45 | -99996 | 0 | 1087.03 | 0.5 | [21 empty] | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | AreaCategoryMethod | 0 | HealthLights | 2806.45 | -99996 | 0 | 1304.43 | 0 | 0 | 1304.43 | 0.6
[38 empty] | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | New | 3373.63 | AreaCategoryMethod | 3373.63 | HealthLights | 2806.45 | -99996 | 0 | 3373.63 | 1 | [21 empty] | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | New | 3373.63 | AreaCategoryMethod | 0 | HealthLights | 2806.45 | -99996 | 0 | 4048.36 | 0 | 0 | 4048.36 | 1.2
[38 empty] | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | New | 2174.04 | AreaCategoryMethod | 2174.04 | HealthLights | 2806.45 | -99996 | 0 | 2174.04 | 1 | [21 empty] | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | New | 2174.04 | AreaCategoryMethod | 0 | HealthLights | 2806.45 | -99996 | 0 | 2608.84 | 0 | 0 | 2608.84 | 1.2
[38 empty] | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 27257.6 | AreaCategoryMethod | 20443.2 | OfficeLights | 2253.1 | -99996 | 0 | 20443.2 | 0.75 | [21 empty] | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 27257.6 | AreaCategoryMethod | 0 | OfficeLights | 2253.1 | -99996 | 0 | 20443.2 | 0 | 0 | 20443.2 | 0.75
[38 empty] | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0 | [29 empty] | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
[38 empty] | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 3373.61 | AreaCategoryMethod | 2530.21 | OfficeLights | 2253.1 | -99996 | 0 | 2530.21 | 0.75 | [21 empty] | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 3373.61 | AreaCategoryMethod | 0 | OfficeLights | 2253.1 | -99996 | 0 | 2530.21 | 0 | 0 | 2530.21 | 0.75
[38 empty] | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | AreaCategoryMethod | 1087.03 | OfficeLights | 2253.1 | -99996 | 0 | 1087.03 | 0.5 | [21 empty] | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | AreaCategoryMethod | 0 | OfficeLights | 2253.1 | -99996 | 0 | 1304.43 | 0 | 0 | 1304.43 | 0.6
[38 empty] | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 3373.63 | AreaCategoryMethod | 2530.23 | OfficeLights | 2253.1 | -99996 | 0 | 2530.23 | 0.75 | [21 empty] | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 3373.63 | AreaCategoryMethod | 0 | OfficeLights | 2253.1 | -99996 | 0 | 2530.23 | 0 | 0 | 2530.23 | 0.75
[38 empty] | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 2174.04 | AreaCategoryMethod | 1630.53 | OfficeLights | 2253.1 | -99996 | 0 | 1630.53 | 0.75 | [21 empty] | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 2174.04 | AreaCategoryMethod | 0 | OfficeLights | 2253.1 | -99996 | 0 | 1630.53 | 0 | 0 | 1630.53 | 0.75
[38 empty] | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 27257.6 | AreaCategoryMethod | 32709.2 | AssemblyLights | 3340.2 | -99996 | 0 | 32709.2 | 1.2 | [21 empty] | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 27257.6 | AreaCategoryMethod | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 32709.2 | 0 | 0 | 32709.2 | 1.2
[38 empty] | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 3373.61 | AreaCategoryMethod | 4048.34 | AssemblyLights | 3340.2 | -99996 | 0 | 4048.34 | 1.2 | [21 empty] | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 3373.61 | AreaCategoryMethod | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 4048.34 | 0 | 0 | 4048.34 | 1.2
[38 empty] | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | AreaCategoryMethod | 1087.03 | AssemblyLights | 3340.2 | -99996 | 0 | 1087.03 | 0.5 | [21 empty] | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | AreaCategoryMethod | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 1304.43 | 0 | 0 | 1304.43 | 0.6
[38 empty] | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 3373.63 | AreaCategoryMethod | 4048.36 | AssemblyLights | 3340.2 | -99996 | 0 | 4048.36 | 1.2 | [21 empty] | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 3373.63 | AreaCategoryMethod | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 4048.36 | 0 | 0 | 4048.36 | 1.2
[38 empty] | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 2174.04 | AreaCategoryMethod | 2608.84 | AssemblyLights | 3340.2 | -99996 | 0 | 2608.84 | 1.2 | [21 empty] | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 2174.04 | AreaCategoryMethod | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 2608.84 | 0 | 0 | 2608.84 | 1.2
[38 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0 | [29 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
[38 empty] | Space Daylighting | [33 empty] | Space Daylighting
[38 empty] | Name | SpcFunc | FlrArea | DayltgCtrlType | MandMinDaylitArea | MinDimLtgFrac | MinDimPwrFrac | NumOfCtrlSteps | SkylitDaylitArea | SkylitDayltgCtrlLtgPwr | SkylitDayltgCtrlLtgFrac | SkylitDayltgIllumSetpt | SkylitDayltgIllumSetptAdjFac | SkylitDayltgAdjIllumSetpt |  | PriSideDayltgRefPtCoord[1] | PriSideDayltgRefPtCoord[2] | PriSideDayltgRefPtCoord[3] | PriSideDaylitArea | PriSideDayltgCtrlLtgPwr | PriSideDayltgCtrlLtgFrac | PriSideDayltgIllumSetpt | PriSideDayltgIllumSetptAdjFac | PriSideDayltgAdjIllumSetpt |  | SecSideDayltgRefPtCoord[1] | SecSideDayltgRefPtCoord[2] | SecSideDayltgRefPtCoord[3] | SecSideDaylitArea | SecSideDayltgCtrlLtgPwr | SecSideDayltgCtrlLtgFrac | SecSideDayltgIllumSetpt | SecSideDayltgIllumSetptAdjFac | SecSideDayltgAdjIllumSetpt | Name | SpcFunc | FlrArea | DayltgCtrlType | MandMinDaylitArea | MinDimLtgFrac | MinDimPwrFrac | NumOfCtrlSteps | SkylitDaylitArea | SkylitDayltgCtrlLtgPwr | SkylitDayltgCtrlLtgFrac | SkylitDayltgIllumSetpt | SkylitDayltgIllumSetptAdjFac | SkylitDayltgAdjIllumSetpt |  | PriSideDayltgRefPtCoord[1] | PriSideDayltgRefPtCoord[2] | PriSideDayltgRefPtCoord[3] | PriSideDaylitArea | PriSideDayltgCtrlLtgPwr | PriSideDayltgCtrlLtgFrac | PriSideDayltgIllumSetpt | PriSideDayltgIllumSetptAdjFac | PriSideDayltgAdjIllumSetpt |  | SecSideDayltgRefPtCoord[1] | SecSideDayltgRefPtCoord[2] | SecSideDayltgRefPtCoord[3] | SecSideDaylitArea | SecSideDayltgCtrlLtgPwr | SecSideDayltgCtrlLtgFrac | SecSideDayltgIllumSetpt | SecSideDayltgIllumSetptAdjFac | SecSideDayltgAdjIllumSetpt
[38 empty] | Space | [7 empty] | Skylit Zone | [6 empty] | Primary Sidelit Daylit Zone | [9 empty] | Secondary Sidelit Daylit Zone | [8 empty] | Space | [7 empty] | Skylit Zone | [6 empty] | Primary Sidelit Daylit Zone | [9 empty] | Secondary Sidelit Daylit Zone
[38 empty] | Name | Space Function | Floor Area | Control Type | MinDayltg per 140.3c | Min. Dim. Ltg. Frac. | Min Dim. Pwr. Frac. | Switched # Ctrl. Steps | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point | Name | Space Function | Floor Area | Control Type | MinDayltg per 140.3c | Min. Dim. Ltg. Frac. | Min Dim. Pwr. Frac. | Switched # Ctrl. Steps | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point
[40 empty] | (ft2) |  | (ft2) |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  | (ft2) |  | (ft2) |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux)
[38 empty] | Basement Spc | Office (Greater than 250 square feet in floor area) | 38353 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 1150 | Basement Spc | Office (Greater than 250 square feet in floor area) | 38353 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 1150
[38 empty] | Core_bottom | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 825 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 1100 | Core_bottom | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 825 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 1100
[38 empty] | GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 | GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0
[38 empty] | Perimeter_bot_ZN_1 | Lobby, Main Entry | 3373.61 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 125 | -99996 | 125 |  | 119.926 | 8.2021 | 2.5 | 1901.26 | 1806.19 | 0.56357 | 125 | -99996 | 187.5 |  | 119.93 | 14.75 | 2.5 | 1471.24 | 0 | 0 | 125 | -99996 | 250 | Perimeter_bot_ZN_1 | Lobby, Main Entry | 3373.61 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 125 | -99996 | 125 |  | 119.926 | 8.2021 | 2.5 | 1901.26 | 1806.19 | 0.56357 | 125 | -99996 | 187.5 |  | 119.93 | 14.75 | 2.5 | 1471.24 | 1397.68 | 0.4361 | 125 | -99996 | 250
[38 empty] | Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.651 | 79.951 | 2.5 | 1239.29 | 619.646 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 2.5 | 934.458 | 0 | 0 | 75 | -99996 | 150 | Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.651 | 79.951 | 2.5 | 1239.29 | 743.575 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 2.5 | 934.458 | 560.675 | 0.42982 | 75 | -99996 | 150
[38 empty] | Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | 119.926 | 151.7 | 2.5 | 1901.26 | 1901.26 | 0.56356 | 550 | -99996 | 825 |  | 119.93 | 145.167 | 2.5 | 1471.24 | 0 | 0 | 550 | -99996 | 1100 | Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | 119.926 | 151.7 | 2.5 | 1901.26 | 2281.51 | 0.56356 | 550 | -99996 | 825 |  | 119.93 | 145.167 | 2.5 | 1471.24 | 1765.49 | 0.4361 | 550 | -99996 | 1100
[38 empty] | Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | 8.2021 | 79.951 | 2.5 | 1245.27 | 1245.27 | 0.57279 | 550 | -99996 | 825 |  | 14.75 | 79.9535 | 2.5 | 928.477 | 0 | 0 | 550 | -99996 | 1100 | Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | 8.2021 | 79.951 | 2.5 | 1245.27 | 1494.33 | 0.57279 | 550 | -99996 | 825 |  | 14.75 | 79.9535 | 2.5 | 928.477 | 1114.17 | 0.42708 | 550 | -99996 | 1100
[38 empty] | Core_mid | Medical and Clinical Care | 27257.6 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 2475 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 3300 | Core_mid | Medical and Clinical Care | 27257.6 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 2475 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 3300
[38 empty] | MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 | MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0
[38 empty] | Perimeter_mid_ZN_1 | Medical and Clinical Care | 3373.61 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 119.926 | 8.2014 | 67.5 | 1901.26 | 1901.26 | 0.56357 | 1650 | -99996 | 2475 |  | 119.93 | 14.75 | 67.5 | 1471.24 | 0 | 0 | 1650 | -99996 | 3300 | Perimeter_mid_ZN_1 | Medical and Clinical Care | 3373.61 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 119.926 | 8.2014 | 67.5 | 1901.26 | 2281.51 | 0.56357 | 1650 | -99996 | 2475 |  | 119.93 | 14.75 | 67.5 | 1471.24 | 1765.49 | 0.4361 | 1650 | -99996 | 3300
[38 empty] | Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.652 | 79.951 | 67.5 | 1239.29 | 619.646 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 67.5 | 934.458 | 0 | 0 | 75 | -99996 | 150 | Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.652 | 79.951 | 67.5 | 1239.29 | 743.575 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 67.5 | 934.458 | 560.675 | 0.42982 | 75 | -99996 | 150
[38 empty] | Perimeter_mid_ZN_3 | Medical and Clinical Care | 3373.63 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 119.926 | 151.701 | 67.5 | 1901.26 | 1901.26 | 0.56356 | 1650 | -99996 | 2475 |  | 119.93 | 145.167 | 67.5 | 1471.24 | 0 | 0 | 1650 | -99996 | 3300 | Perimeter_mid_ZN_3 | Medical and Clinical Care | 3373.63 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 119.926 | 151.701 | 67.5 | 1901.26 | 2281.51 | 0.56356 | 1650 | -99996 | 2475 |  | 119.93 | 145.167 | 67.5 | 1471.24 | 1765.49 | 0.4361 | 1650 | -99996 | 3300
[38 empty] | Perimeter_mid_ZN_4 | Medical and Clinical Care | 2174.04 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 8.2014 | 79.951 | 67.5 | 1245.27 | 1245.27 | 0.57279 | 1650 | -99996 | 2475 |  | 14.75 | 79.9535 | 67.5 | 928.477 | 0 | 0 | 1650 | -99996 | 3300 | Perimeter_mid_ZN_4 | Medical and Clinical Care | 2174.04 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 8.2014 | 79.951 | 67.5 | 1245.27 | 1494.33 | 0.57279 | 1650 | -99996 | 2475 |  | 14.75 | 79.9535 | 67.5 | 928.477 | 1114.17 | 0.42708 | 1650 | -99996 | 3300
[38 empty] | Core_hi | Office (Greater than 250 square feet in floor area) | 27257.6 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 1150 | Core_hi | Office (Greater than 250 square feet in floor area) | 27257.6 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 1150
[38 empty] | HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 | HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0
[38 empty] | Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) | 3373.61 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 119.926 | 8.202 | 132.5 | 1901.26 | 1425.94 | 0.56357 | 287.5 | -99996 | 287.5 |  | 119.93 | 14.75 | 132.5 | 1471.24 | 0 | 0 | 287.5 | -99996 | 1150 | Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) | 3373.61 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 119.926 | 8.202 | 132.5 | 1901.26 | 1425.94 | 0.56357 | 287.5 | -99996 | 287.5 |  | 119.93 | 14.75 | 132.5 | 1471.24 | 1103.43 | 0.4361 | 287.5 | -99996 | 1150
[38 empty] | Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.651 | 79.951 | 132.5 | 1239.29 | 619.646 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 132.5 | 934.458 | 0 | 0 | 75 | -99996 | 150 | Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.651 | 79.951 | 132.5 | 1239.29 | 743.575 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 132.5 | 934.458 | 560.675 | 0.42982 | 75 | -99996 | 150
[38 empty] | Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) | 3373.63 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 119.926 | 151.7 | 132.5 | 1901.26 | 1425.94 | 0.56356 | 287.5 | -99996 | 287.5 |  | 119.93 | 145.167 | 132.5 | 1471.24 | 0 | 0 | 287.5 | -99996 | 1150 | Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) | 3373.63 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 119.926 | 151.7 | 132.5 | 1901.26 | 1425.94 | 0.56356 | 287.5 | -99996 | 287.5 |  | 119.93 | 145.167 | 132.5 | 1471.24 | 1103.43 | 0.4361 | 287.5 | -99996 | 1150
[38 empty] | Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) | 2174.04 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 8.202 | 79.951 | 132.5 | 1245.27 | 933.954 | 0.57279 | 287.5 | -99996 | 287.5 |  | 14.75 | 79.9535 | 132.5 | 928.477 | 0 | 0 | 287.5 | -99996 | 1150 | Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) | 2174.04 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 8.202 | 79.951 | 132.5 | 1245.27 | 933.954 | 0.57279 | 287.5 | -99996 | 287.5 |  | 14.75 | 79.9535 | 132.5 | 928.477 | 696.358 | 0.42708 | 287.5 | -99996 | 1150
[38 empty] | Core_top | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 247.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 330 | Core_top | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 247.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 330
[38 empty] | Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 119.926 | 8.201 | 145.5 | 1901.26 | 2281.51 | 0.56357 | 165 | -99996 | 247.5 |  | 119.93 | 14.75 | 145.5 | 1471.24 | 0 | 0 | 165 | -99996 | 330 | Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 119.926 | 8.201 | 145.5 | 1901.26 | 2281.51 | 0.56357 | 165 | -99996 | 247.5 |  | 119.93 | 14.75 | 145.5 | 1471.24 | 1765.49 | 0.4361 | 165 | -99996 | 330
[38 empty] | Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.652 | 79.951 | 145.5 | 1239.29 | 619.646 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 145.5 | 934.458 | 0 | 0 | 75 | -99996 | 150 | Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.652 | 79.951 | 145.5 | 1239.29 | 743.575 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 145.5 | 934.458 | 560.675 | 0.42982 | 75 | -99996 | 150
[38 empty] | Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 119.926 | 151.701 | 145.5 | 1901.26 | 2281.51 | 0.56356 | 165 | -99996 | 247.5 |  | 119.93 | 145.167 | 145.5 | 1471.24 | 0 | 0 | 165 | -99996 | 330 | Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 119.926 | 151.701 | 145.5 | 1901.26 | 2281.51 | 0.56356 | 165 | -99996 | 247.5 |  | 119.93 | 145.167 | 145.5 | 1471.24 | 1765.49 | 0.4361 | 165 | -99996 | 330
[38 empty] | Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 8.201 | 79.951 | 145.5 | 1245.27 | 1494.33 | 0.57279 | 165 | -99996 | 247.5 |  | 14.75 | 79.9535 | 145.5 | 928.477 | 0 | 0 | 165 | -99996 | 330 | Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 8.201 | 79.951 | 145.5 | 1245.27 | 1494.33 | 0.57279 | 165 | -99996 | 247.5 |  | 14.75 | 79.9535 | 145.5 | 928.477 | 1114.17 | 0.42708 | 165 | -99996 | 330
[38 empty] | TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 | TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0
[38 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[38 empty] | BuildingStory | [33 empty] | BuildingStory
[40 empty] | Floor Area (including multipliers) |  |  |  |  | Ventilation (Design) |  |  | Ventilation (For Balance) | [5 empty] | General |  | Comm. Kitchen |  | Parking Garage |  | Laboratory | [13 empty] | Floor Area (including multipliers) |  |  |  |  | Ventilation (Design) |  |  | Ventilation (For Balance) | [5 empty] | General |  | Comm. Kitchen |  | Parking Garage |  | Laboratory
[38 empty] | Name | Multiplier | Total | Cond. NRes | Cond. Res | Total Cond. | Number | Total | Code Min. | Exhaust | Total | Code Min. | Tot:Min Ratio | Exhaust | Vent:Exh Ratio | Vent Mult. | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | [10 empty] | Name | Multiplier | Total | Cond. NRes | Cond. Res | Total Cond. | Number | Total | Code Min. | Exhaust | Total | Code Min. | Tot:Min Ratio | Exhaust | Vent:Exh Ratio | Vent Mult. | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust
[40 empty] | (ft2) | (ft2) | (ft2) | (ft2) | (people) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) |  | (cfm) |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | [12 empty] | (ft2) | (ft2) | (ft2) | (ft2) | (people) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) |  | (cfm) |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
[38 empty] | Basement | 1 | 38353 | 38353 | 0 | 38353 | 191.8 | 5753 | 5753 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Basement | 1 | 38353 | 38353 | 0 | 38353 | 191.8 | 5753 | 5753 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | GroundFloor | 1 | 38353 | 38353 | 0 | 38353 | 670 | 10214 | 10214 | 0 | 10214 | 10214 | 1 | 0 | 1 | 1 | 10214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | GroundFloor | 1 | 38353 | 38353 | 0 | 38353 | 670 | 7393 | 10214 | 0 | 10214 | 10214 | 1 | 0 | 1 | 1 | 7393 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | MidFloor | 5 | 191764.9 | 191764.9 | 0 | 191764.9 | 958.8 | 7562 | 5753 | 0 | 7562 | 5753 | 0.761 | 0 | 1 | 1 | 7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | MidFloor | 5 | 191764.9 | 191764.9 | 0 | 191764.9 | 958.8 | 7562 | 5753 | 0 | 7562 | 5753 | 0.761 | 0 | 1 | 1 | 7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | HiFloor | 5 | 191764.9 | 191764.9 | 0 | 191764.9 | 958.8 | 5753 | 5753 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | HiFloor | 5 | 191764.9 | 191764.9 | 0 | 191764.9 | 958.8 | 5753 | 5753 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | TopFloor | 1 | 38353 | 38353 | 0 | 38353 | 1216.9 | 18416 | 18416 | 0 | 18416 | 18416 | 1 | 0 | 1 | 1 | 18416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | TopFloor | 1 | 38353 | 38353 | 0 | 38353 | 1216.9 | 5753 | 18416 | 0 | 18416 | 18416 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[38 empty] | Space | [33 empty] | Space
[45 empty] | Occupancy |  |  | Ventilation |  | Design Input (By Component) |  |  |  |  | Minimum Req. (By Component) |  |  |  | Simulated |  | Exhaust |  |  | ForBalance | [14 empty] | Occupancy |  |  | Ventilation |  | Design Input (By Component) |  |  |  |  | Minimum Req. (By Component) |  |  |  | Simulated |  | Exhaust |  |  | ForBalance
[38 empty] | Name | Story Name | Condg Type | Space Function | Thermal Zone | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Per Space | Calculated Flow | Per Occupant | Per Area | Per Volume | Calculated Flow |  |  | Calculated Flow | Lab Exh Type | Max Kitchen | Ventilation | Exhaust | [6 empty] | Name | Story Name | Condg Type | Space Function | Thermal Zone | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Per Space | Calculated Flow | Per Occupant | Per Area | Per Volume | Calculated Flow |  |  | Calculated Flow | Lab Exh Type | Max Kitchen | Ventilation | Exhaust
[43 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm) | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) |  | (cfm) | (cfm) | (cfm) | [11 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm) | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) |  | (cfm) | (cfm) | (cfm)
[38 empty] | Basement Spc | Basement | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Basement Thermal Zone | 38353 | 1 | 10 | 10 | 191.8 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 5753 | 15 | 0.15 | 0 | 5753 | 0 | 0.15 | 0 | UNDEFINED | 0 | 5753 | 0 | [6 empty] | Basement Spc | Basement | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Basement Thermal Zone | 38353 | 1 | 10 | 10 | 191.8 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 5753 | 15 | 0.15 | 0 | 5753 | 0 | 0.15 | 0 | UNDEFINED | 0 | 5753 | 0
[38 empty] | Core_bottom | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Core_bottom Thermal Zone | 27257.6 | 1 | 33.3 | 33.3 | 454.2 | Maximum | CO2Sensors | 15 | 0.2 | 0 | 0 | 6814 | 15 | 0.2 | 0 | 6814 | 15 | 0.2 | 0 | UNDEFINED | 0 | 6814 | 0 | [6 empty] | Core_bottom | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Core_bottom Thermal Zone | 27257.6 | 1 | 33.3 | 33.3 | 454.2 | Maximum | CO2Sensors | 15 | 0.2 | 0 | 0 | 5452 | 15 | 0.2 | 0 | 6814 | 15 | 0.2 | 0 | UNDEFINED | 0 | 6814 | 0
[38 empty] | GroundFloor_Plenum | GroundFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | GroundFloor_Plenum Thermal Zone | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | GroundFloor_Plenum | GroundFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | GroundFloor_Plenum Thermal Zone | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[38 empty] | Perimeter_bot_ZN_1 | GroundFloor | DirectlyConditioned | Lobby, Main Entry | Perimeter_bot_ZN_1 Thermal Zone | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 1687 | 15 | 0.15 | 0 | 1687 | 15 | 0.15 | 0 | UNDEFINED | 0 | 1687 | 0 | [6 empty] | Perimeter_bot_ZN_1 | GroundFloor | DirectlyConditioned | Lobby, Main Entry | Perimeter_bot_ZN_1 Thermal Zone | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 506 | 15 | 0.15 | 0 | 1687 | 15 | 0.15 | 0 | UNDEFINED | 0 | 1687 | 0
[38 empty] | Perimeter_bot_ZN_2 | GroundFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_bot_ZN_2 Thermal Zone | 2174.1 | 1 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_bot_ZN_2 | GroundFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_bot_ZN_2 Thermal Zone | 2174.1 | 1 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0
[38 empty] | Perimeter_bot_ZN_3 | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Perimeter_bot_ZN_3 Thermal Zone | 3373.6 | 1 | 33.3 | 33.3 | 56.2 | Maximum | CO2Sensors | 15 | 0.2 | 0 | 0 | 843 | 15 | 0.2 | 0 | 843 | 15 | 0.2 | 0 | UNDEFINED | 0 | 843 | 0 | [6 empty] | Perimeter_bot_ZN_3 | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Perimeter_bot_ZN_3 Thermal Zone | 3373.6 | 1 | 33.3 | 33.3 | 56.2 | Maximum | CO2Sensors | 15 | 0.2 | 0 | 0 | 675 | 15 | 0.2 | 0 | 843 | 15 | 0.2 | 0 | UNDEFINED | 0 | 843 | 0
[38 empty] | Perimeter_bot_ZN_4 | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Perimeter_bot_ZN_4 Thermal Zone | 2174 | 1 | 33.3 | 33.3 | 36.2 | Maximum | CO2Sensors | 15 | 0.2 | 0 | 0 | 543 | 15 | 0.2 | 0 | 543 | 15 | 0.2 | 0 | UNDEFINED | 0 | 543 | 0 | [6 empty] | Perimeter_bot_ZN_4 | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Perimeter_bot_ZN_4 Thermal Zone | 2174 | 1 | 33.3 | 33.3 | 36.2 | Maximum | CO2Sensors | 15 | 0.2 | 0 | 0 | 435 | 15 | 0.2 | 0 | 543 | 15 | 0.2 | 0 | UNDEFINED | 0 | 543 | 0
[38 empty] | Core_mid | MidFloor | DirectlyConditioned | Medical and Clinical Care | Core_mid Thermal Zone | 27257.6 | 5 | 10 | 10 | 136.3 | Maximum | Fixed | 15 | 0.2 | 0 | 0 | 5452 | 15 | 0.15 | 0 | 4089 | 0 | 0.2 | 0 | UNDEFINED | 0 | 5452 | 0 | [6 empty] | Core_mid | MidFloor | DirectlyConditioned | Medical and Clinical Care | Core_mid Thermal Zone | 27257.6 | 5 | 10 | 10 | 136.3 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 5452 | 15 | 0.15 | 0 | 4089 | 0 | 0.15216 | 0 | UNDEFINED | 0 | 5452 | 0
[38 empty] | MidFloor_Plenum | MidFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | MidFloor_Plenum Thermal Zone | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | MidFloor_Plenum | MidFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | MidFloor_Plenum Thermal Zone | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[38 empty] | Perimeter_mid_ZN_1 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_1 Thermal Zone | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 15 | 0.2 | 0 | 0 | 675 | 15 | 0.15 | 0 | 506 | 0 | 0.2 | 0 | UNDEFINED | 0 | 675 | 0 | [6 empty] | Perimeter_mid_ZN_1 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_1 Thermal Zone | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 675 | 15 | 0.15 | 0 | 506 | 0 | 0.15216 | 0 | UNDEFINED | 0 | 675 | 0
[38 empty] | Perimeter_mid_ZN_2 | MidFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_mid_ZN_2 Thermal Zone | 2174.1 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_mid_ZN_2 | MidFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_mid_ZN_2 Thermal Zone | 2174.1 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 326 | 0 | 0.11412 | 0 | UNDEFINED | 0 | 326 | 0
[38 empty] | Perimeter_mid_ZN_3 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_3 Thermal Zone | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 15 | 0.2 | 0 | 0 | 675 | 15 | 0.15 | 0 | 506 | 0 | 0.2 | 0 | UNDEFINED | 0 | 675 | 0 | [6 empty] | Perimeter_mid_ZN_3 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_3 Thermal Zone | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 675 | 15 | 0.15 | 0 | 506 | 0 | 0.15216 | 0 | UNDEFINED | 0 | 675 | 0
[38 empty] | Perimeter_mid_ZN_4 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_4 Thermal Zone | 2174 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.2 | 0 | 0 | 435 | 15 | 0.15 | 0 | 326 | 0 | 0.2 | 0 | UNDEFINED | 0 | 435 | 0 | [6 empty] | Perimeter_mid_ZN_4 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_4 Thermal Zone | 2174 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 435 | 15 | 0.15 | 0 | 326 | 0 | 0.15216 | 0 | UNDEFINED | 0 | 435 | 0
[38 empty] | Core_hi | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Core_hi Thermal Zone | 27257.6 | 5 | 10 | 10 | 136.3 | Sum | Fixed | 0 | 0 | 0 | 4415 | 4415 | 15 | 0.15 | 0 | 4089 | 0 | 0.16197 | 0 | UNDEFINED | 0 | 4415 | 0 | [6 empty] | Core_hi | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Core_hi Thermal Zone | 27257.6 | 5 | 10 | 10 | 136.3 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 4415 | 15 | 0.15 | 0 | 4089 | 0 | 0.16197 | 0 | UNDEFINED | 0 | 4415 | 0
[38 empty] | HiFloor_Plenum | HiFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | HiFloor_Plenum Thermal Zone | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | HiFloor_Plenum | HiFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | HiFloor_Plenum Thermal Zone | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[38 empty] | Perimeter_hi_ZN_1 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_1 Thermal Zone | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 506 | 15 | 0.15 | 0 | 506 | 0 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0 | [6 empty] | Perimeter_hi_ZN_1 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_1 Thermal Zone | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 506 | 15 | 0.15 | 0 | 506 | 0 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0
[38 empty] | Perimeter_hi_ZN_2 | HiFloor | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_hi_ZN_2 Thermal Zone | 2174.1 | 5 | 10 | 10 | 10.9 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 15 | 0.15 | 0 | 326 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | Perimeter_hi_ZN_2 | HiFloor | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_hi_ZN_2 Thermal Zone | 2174.1 | 5 | 10 | 10 | 10.9 | Maximum | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 15 | 0.15 | 0 | 326 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[38 empty] | Perimeter_hi_ZN_3 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_3 Thermal Zone | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 506 | 15 | 0.15 | 0 | 506 | 0 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0 | [6 empty] | Perimeter_hi_ZN_3 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_3 Thermal Zone | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 506 | 15 | 0.15 | 0 | 506 | 0 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0
[38 empty] | Perimeter_hi_ZN_4 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_4 Thermal Zone | 2174 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_hi_ZN_4 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_4 Thermal Zone | 2174 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0
[38 empty] | Core_top | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Core_top Thermal Zone | 27257.6 | 1 | 66.7 | 66.7 | 908.6 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 13630 | 15 | 0.15 | 0 | 13630 | 15 | 0.15 | 0 | UNDEFINED | 0 | 13630 | 0 | [6 empty] | Core_top | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Core_top Thermal Zone | 27257.6 | 1 | 66.7 | 66.7 | 908.6 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 4089 | 15 | 0.15 | 0 | 13630 | 15 | 0.15 | 0 | UNDEFINED | 0 | 13630 | 0
[38 empty] | Perimeter_top_ZN_1 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_1 Thermal Zone | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 1687 | 15 | 0.15 | 0 | 1687 | 15 | 0.15 | 0 | UNDEFINED | 0 | 1687 | 0 | [6 empty] | Perimeter_top_ZN_1 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_1 Thermal Zone | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 506 | 15 | 0.15 | 0 | 1687 | 15 | 0.15 | 0 | UNDEFINED | 0 | 1687 | 0
[38 empty] | Perimeter_top_ZN_2 | TopFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_top_ZN_2 Thermal Zone | 2174.1 | 1 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_top_ZN_2 | TopFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_top_ZN_2 Thermal Zone | 2174.1 | 1 | 10 | 10 | 10.9 | Maximum | Fixed | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0
[38 empty] | Perimeter_top_ZN_3 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_3 Thermal Zone | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 1687 | 15 | 0.15 | 0 | 1687 | 15 | 0.15 | 0 | UNDEFINED | 0 | 1687 | 0 | [6 empty] | Perimeter_top_ZN_3 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_3 Thermal Zone | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 506 | 15 | 0.15 | 0 | 1687 | 15 | 0.15 | 0 | UNDEFINED | 0 | 1687 | 0
[38 empty] | Perimeter_top_ZN_4 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_4 Thermal Zone | 2174 | 1 | 66.7 | 66.7 | 72.5 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 1087 | 15 | 0.15 | 0 | 1087 | 15 | 0.15 | 0 | UNDEFINED | 0 | 1087 | 0 | [6 empty] | Perimeter_top_ZN_4 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_4 Thermal Zone | 2174 | 1 | 66.7 | 66.7 | 72.5 | Maximum | CO2Sensors | 15 | 0.15 | 0 | 0 | 326 | 15 | 0.15 | 0 | 1087 | 15 | 0.15 | 0 | UNDEFINED | 0 | 1087 | 0
[38 empty] | TopFloor_Plenum | TopFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | TopFloor_Plenum Thermal Zone | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | TopFloor_Plenum | TopFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | TopFloor_Plenum Thermal Zone | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[38 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[38 empty] | ThermalZone | [33 empty] | ThermalZone
[45 empty] | Occupancy |  |  |  | Ventilation |  | Design Value (Total) |  |  |  |  | Minimum Req. (Total) |  |  |  | Simulated |  |  | Exhaust | [15 empty] | Occupancy |  |  |  | Ventilation |  | Design Value (Total) |  |  |  |  | Minimum Req. (Total) |  |  |  | Simulated |  |  | Exhaust
[38 empty] | Name | Story Name | Type | Ventilation Source | Pri. HVAC System | Ventilation System | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Calculated Flow |  | Per Occupant | Per Area | Per Volume | Calculated Flow | Per Occupant | Per Area | Calculated Flow | Calculated Flow | ExhSysRef | ExhOperMode | ExhCtrlMthd | ExhBalancedSchRef |  |  |  |  | Name | Story Name | Type | Ventilation Source | Pri. HVAC System | Ventilation System | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Calculated Flow |  | Per Occupant | Per Area | Per Volume | Calculated Flow | Per Occupant | Per Area | Calculated Flow | Calculated Flow | ExhSysRef | ExhOperMode | ExhCtrlMthd | ExhBalancedSchRef
[43 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) | (cfm) | [13 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) | (cfm)
[38 empty] | Basement Thermal Zone | Basement | Conditioned | Forced | BaseAirSys6-Basement | BaseAirSys6-Basement | 38353 | 1 | 10 | 10 | 191.8 | Maximum | Fixed | 30 | 0.15 | 1.1247 | 5753 |  | 30 | 0.15 | 1.1247 | 5753 | 0 | 0.15 | 5753 | [9 empty] | Basement Thermal Zone | Basement | Conditioned | Forced | BaseAirSys6 | BaseAirSys6 | 38353 | 1 | 10 | 10 | 191.8 | Maximum | Fixed | 30 | 0.15 | 1.1247 | 5753 |  | 30 | 0.15 | 1.1247 | 5753 | 0 | 0.15 | 5753
[38 empty] | Core_bottom Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-Bot | BaseAirSys6-Bot | 27257.6 | 1 | 33.3 | 33.3 | 454.2 | Maximum | CO2Sensors | 15 | 0.24998 | 1.666 | 6814 |  | 15 | 0.24998 | 1.666 | 6814 | 15 | 0.2 | 6814 | [9 empty] | Core_bottom Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-2 | BaseAirSys6-2 | 27257.6 | 1 | 33.3 | 33.3 | 454.2 | Maximum | CO2Sensors | 15 | 0.24998 | 1.666 | 6814 |  | 15 | 0.24998 | 1.666 | 6814 | 15 | 0.2 | 6814
[38 empty] | GroundFloor_Plenum Thermal Zone | GroundFloor | Plenum | None | NONE | NONE | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | GroundFloor_Plenum Thermal Zone | GroundFloor | Plenum | None | NONE | NONE | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | Perimeter_bot_ZN_1 Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-Bot | BaseAirSys6-Bot | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3325 | 1687 |  | 15 | 0.50003 | 3.3325 | 1687 | 15 | 0.15 | 1687 | [9 empty] | Perimeter_bot_ZN_1 Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-2 | BaseAirSys6-2 | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3325 | 1687 |  | 15 | 0.50003 | 3.3325 | 1687 | 15 | 0.15 | 1687
[38 empty] | Perimeter_bot_ZN_2 Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-Bot | BaseAirSys6-Bot | 2174.1 | 1 | 10 | 10 | 10.9 | Maximum | Fixed | 30 | 0.15 | 0.99971 | 326 |  | 30 | 0.15 | 0.99971 | 326 | 0 | 0.15 | 326 | [9 empty] | Perimeter_bot_ZN_2 Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-2 | BaseAirSys6-2 | 2174.1 | 1 | 10 | 10 | 10.9 | Maximum | Fixed | 30 | 0.15 | 0.99971 | 326 |  | 30 | 0.15 | 0.99971 | 326 | 0 | 0.15 | 326
[38 empty] | Perimeter_bot_ZN_3 Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-Bot | BaseAirSys6-Bot | 3373.6 | 1 | 33.3 | 33.3 | 56.2 | Maximum | CO2Sensors | 15 | 0.24998 | 1.6661 | 843 |  | 15 | 0.24998 | 1.6661 | 843 | 15 | 0.2 | 843 | [9 empty] | Perimeter_bot_ZN_3 Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-2 | BaseAirSys6-2 | 3373.6 | 1 | 33.3 | 33.3 | 56.2 | Maximum | CO2Sensors | 15 | 0.24998 | 1.6661 | 843 |  | 15 | 0.24998 | 1.6661 | 843 | 15 | 0.2 | 843
[38 empty] | Perimeter_bot_ZN_4 Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-Bot | BaseAirSys6-Bot | 2174 | 1 | 33.3 | 33.3 | 36.2 | Maximum | CO2Sensors | 15 | 0.24998 | 1.666 | 543 |  | 15 | 0.24998 | 1.666 | 543 | 15 | 0.2 | 543 | [9 empty] | Perimeter_bot_ZN_4 Thermal Zone | GroundFloor | Conditioned | Forced | BaseAirSys6-2 | BaseAirSys6-2 | 2174 | 1 | 33.3 | 33.3 | 36.2 | Maximum | CO2Sensors | 15 | 0.24998 | 1.666 | 543 |  | 15 | 0.24998 | 1.666 | 543 | 15 | 0.2 | 543
[38 empty] | Core_mid Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-Mid | BaseAirSys6-Mid | 27257.6 | 5 | 10 | 10 | 136.3 | Maximum | Fixed | 40 | 0.2 | 1.3329 | 5452 |  | 30 | 0.15 | 0.99971 | 4089 | 0 | 0.2 | 5452 | [9 empty] | Core_mid Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-3 | BaseAirSys6-3 | 27257.6 | 5 | 10 | 10 | 136.3 | Maximum | Fixed | 30.4313 | 0.15216 | 1.0141 | 4147 |  | 30 | 0.15 | 0.99971 | 4089 | 0 | 0.15216 | 4147
[38 empty] | MidFloor_Plenum Thermal Zone | MidFloor | Plenum | None | NONE | NONE | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | MidFloor_Plenum Thermal Zone | MidFloor | Plenum | None | NONE | NONE | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | Perimeter_mid_ZN_1 Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-Mid | BaseAirSys6-Mid | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 40 | 0.2 | 1.3329 | 675 |  | 30 | 0.15 | 0.99971 | 506 | 0 | 0.2 | 675 | [9 empty] | Perimeter_mid_ZN_1 Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-3 | BaseAirSys6-3 | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 30.4313 | 0.15216 | 1.0141 | 513 |  | 30 | 0.15 | 0.99971 | 506 | 0 | 0.15216 | 513
[38 empty] | Perimeter_mid_ZN_2 Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-Mid | BaseAirSys6-Mid | 2174.1 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 30 | 0.15 | 0.99971 | 326 |  | 30 | 0.15 | 0.99971 | 326 | 0 | 0.15 | 326 | [9 empty] | Perimeter_mid_ZN_2 Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-3 | BaseAirSys6-3 | 2174.1 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 22.8234 | 0.11412 | 0.76056 | 248 |  | 30 | 0.15 | 0.99971 | 326 | 0 | 0.11412 | 326
[38 empty] | Perimeter_mid_ZN_3 Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-Mid | BaseAirSys6-Mid | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 40 | 0.2 | 1.333 | 675 |  | 30 | 0.15 | 0.99973 | 506 | 0 | 0.2 | 675 | [9 empty] | Perimeter_mid_ZN_3 Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-3 | BaseAirSys6-3 | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 30.4313 | 0.15216 | 1.0141 | 513 |  | 30 | 0.15 | 0.99973 | 506 | 0 | 0.15216 | 513
[38 empty] | Perimeter_mid_ZN_4 Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-Mid | BaseAirSys6-Mid | 2174 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 40 | 0.2 | 1.3329 | 435 |  | 30 | 0.15 | 0.9997 | 326 | 0 | 0.2 | 435 | [9 empty] | Perimeter_mid_ZN_4 Thermal Zone | MidFloor | Conditioned | Forced | BaseAirSys6-3 | BaseAirSys6-3 | 2174 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 30.4313 | 0.15216 | 1.0141 | 331 |  | 30 | 0.15 | 0.9997 | 326 | 0 | 0.15216 | 331
[38 empty] | Core_hi Thermal Zone | HiFloor | Conditioned | Forced | BaseAirSys6-Hi | BaseAirSys6-Hi | 27257.6 | 5 | 10 | 10 | 136.3 | Sum | Fixed | 32.3946 | 0.16197 | 1.0795 | 4415 |  | 30 | 0.15 | 0.99971 | 4089 | 0 | 0.16197 | 4415 | [9 empty] | Core_hi Thermal Zone | HiFloor | Conditioned | Forced | BaseAirSys6-4 | BaseAirSys6-4 | 27257.6 | 5 | 10 | 10 | 136.3 | Maximum | Fixed | 32.3946 | 0.16197 | 1.0795 | 4415 |  | 30 | 0.15 | 0.99971 | 4089 | 0 | 0.16197 | 4415
[38 empty] | HiFloor_Plenum Thermal Zone | HiFloor | Plenum | None | NONE | NONE | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | HiFloor_Plenum Thermal Zone | HiFloor | Plenum | None | NONE | NONE | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[38 empty] | Perimeter_hi_ZN_1 Thermal Zone | HiFloor | Conditioned | Forced | BaseAirSys6-Hi | BaseAirSys6-Hi | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 30 | 0.15 | 0.99971 | 506 |  | 30 | 0.15 | 0.99971 | 506 | 0 | 0.15 | 506 | [9 empty] | Perimeter_hi_ZN_1 Thermal Zone | HiFloor | Conditioned | Forced | BaseAirSys6-4 | BaseAirSys6-4 | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 30 | 0.15 | 0.99971 | 506 |  | 30 | 0.15 | 0.99971 | 506 | 0 | 0.15 | 506
[38 empty] | Perimeter_hi_ZN_2 Thermal Zone | HiFloor | Unconditioned | None | NONE | NONE | 2174.1 | 5 | 10 | 10 | 10.9 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 30 | 0.15 | 0.99971 | 326 | 0 | 0 | 326 | [9 empty] | Perimeter_hi_ZN_2 Thermal Zone | HiFloor | Unconditioned | None | NONE | NONE | 2174.1 | 5 | 10 | 10 | 10.9 | Maximum | UNDEFINED | 0 | 0 | 0 | 0 |  | 30 | 0.15 | 0.99971 | 326 | 0 | 0 | 326
[38 empty] | Perimeter_hi_ZN_3 Thermal Zone | HiFloor | Conditioned | Forced | BaseAirSys6-Hi | BaseAirSys6-Hi | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 30 | 0.15 | 0.99973 | 506 |  | 30 | 0.15 | 0.99973 | 506 | 0 | 0.15 | 506 | [9 empty] | Perimeter_hi_ZN_3 Thermal Zone | HiFloor | Conditioned | Forced | BaseAirSys6-4 | BaseAirSys6-4 | 3373.6 | 5 | 10 | 10 | 16.9 | Maximum | Fixed | 30 | 0.15 | 0.99973 | 506 |  | 30 | 0.15 | 0.99973 | 506 | 0 | 0.15 | 506
[38 empty] | Perimeter_hi_ZN_4 Thermal Zone | HiFloor | Conditioned | Forced | BaseAirSys6-Hi | BaseAirSys6-Hi | 2174 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 30 | 0.15 | 0.9997 | 326 |  | 30 | 0.15 | 0.9997 | 326 | 0 | 0.15 | 326 | [9 empty] | Perimeter_hi_ZN_4 Thermal Zone | HiFloor | Conditioned | Forced | BaseAirSys6-4 | BaseAirSys6-4 | 2174 | 5 | 10 | 10 | 10.9 | Maximum | Fixed | 30 | 0.15 | 0.9997 | 326 |  | 30 | 0.15 | 0.9997 | 326 | 0 | 0.15 | 326
[38 empty] | Core_top Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-Top | BaseAirSys6-Top | 27257.6 | 1 | 66.7 | 66.7 | 908.6 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3325 | 13630 |  | 15 | 0.50003 | 3.3325 | 13630 | 15 | 0.15 | 13630 | [9 empty] | Core_top Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-5 | BaseAirSys6-5 | 27257.6 | 1 | 66.7 | 66.7 | 908.6 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3325 | 13630 |  | 15 | 0.50003 | 3.3325 | 13630 | 15 | 0.15 | 13630
[38 empty] | Perimeter_top_ZN_1 Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-Top | BaseAirSys6-Top | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3325 | 1687 |  | 15 | 0.50003 | 3.3325 | 1687 | 15 | 0.15 | 1687 | [9 empty] | Perimeter_top_ZN_1 Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-5 | BaseAirSys6-5 | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3325 | 1687 |  | 15 | 0.50003 | 3.3325 | 1687 | 15 | 0.15 | 1687
[38 empty] | Perimeter_top_ZN_2 Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-Top | BaseAirSys6-Top | 2174.1 | 1 | 10 | 10 | 10.9 | Maximum | Fixed | 30 | 0.15 | 0.99971 | 326 |  | 30 | 0.15 | 0.99971 | 326 | 0 | 0.15 | 326 | [9 empty] | Perimeter_top_ZN_2 Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-5 | BaseAirSys6-5 | 2174.1 | 1 | 10 | 10 | 10.9 | Maximum | Fixed | 30 | 0.15 | 0.99971 | 326 |  | 30 | 0.15 | 0.99971 | 326 | 0 | 0.15 | 326
[38 empty] | Perimeter_top_ZN_3 Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-Top | BaseAirSys6-Top | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3326 | 1687 |  | 15 | 0.50003 | 3.3326 | 1687 | 15 | 0.15 | 1687 | [9 empty] | Perimeter_top_ZN_3 Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-5 | BaseAirSys6-5 | 3373.6 | 1 | 66.7 | 66.7 | 112.5 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3326 | 1687 |  | 15 | 0.50003 | 3.3326 | 1687 | 15 | 0.15 | 1687
[38 empty] | Perimeter_top_ZN_4 Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-Top | BaseAirSys6-Top | 2174 | 1 | 66.7 | 66.7 | 72.5 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3325 | 1087 |  | 15 | 0.50003 | 3.3325 | 1087 | 15 | 0.15 | 1087 | [9 empty] | Perimeter_top_ZN_4 Thermal Zone | TopFloor | Conditioned | Forced | BaseAirSys6-5 | BaseAirSys6-5 | 2174 | 1 | 66.7 | 66.7 | 72.5 | Maximum | CO2Sensors | 15 | 0.50003 | 3.3325 | 1087 |  | 15 | 0.50003 | 3.3325 | 1087 | 15 | 0.15 | 1087
[38 empty] | TopFloor_Plenum Thermal Zone | TopFloor | Plenum | None | NONE | NONE | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | TopFloor_Plenum Thermal Zone | TopFloor | Plenum | None | NONE | NONE | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 030006-OffMed-Run12 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run12 |  | Model Revision no. |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run12.cibd16 |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Simulated Lighting Power Density (LPD) (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | Spc:IntLtgSpecMthd
Core_bottom | Waiting Area |  | 0.75 |  | 0.2 |  | 0.95 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_2 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_3 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | AreaCategoryMethod
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area |  | 0.75 |  | 0.2 |  | 0.95 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_2 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_3 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | AreaCategoryMethod
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area |  | 0.75 |  | 0.2 |  | 0.95 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_2 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_3 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | AreaCategoryMethod
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Simulated Lighting Power Density (LPD) (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | Spc:IntLtgSpecMthd
Core_bottom | Waiting Area |  | 0.64 |  | 0.2 |  | 0.84 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_2 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_3 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.64 | - | - |  | 0.75 |  | OfficeLights |  | AreaCategoryMethod
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area |  | 0.64 |  | 0.2 |  | 0.84 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_2 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_3 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.64 | - | - |  | 0.75 |  | OfficeLights |  | AreaCategoryMethod
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area |  | 0.64 |  | 0.2 |  | 0.84 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_2 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_3 | Lobby, Main Entry |  | 0.64 | - | - |  | 0.64 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.64 | - | - |  | 0.75 |  | OfficeLights |  | AreaCategoryMethod
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Note on C19: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M19: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on C25: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M25: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on C31: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M31: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on G40: Sandeep: Standards_Section 140.6: TAilored Method- The additional allowed power for ornamental/special effects lighting for each applicable area shall be the smaller of: a. The product of the allowed ornamental/special effects lighting power determined in accordance with Section 140.6(c)3Kiii, times floor square footage determined in accordance with Section 140.6(c)3Kiv; {or (0.5*10586.7) = 5293.35 W} b. The actual power of allowed ornamental/special effects lighting. {Installed power - 2112 W} Hence modeled 2112W or 2112/10586.7 = 0.2 W/ft2
Note on C44: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on I44: Sandeep: 160624_SDS: Space function updated which changes the baseline LPD
Note on M44: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on G46: Sandeep: Standards_Section 140.6: TAilored Method- The additional allowed power for ornamental/special effects lighting for each applicable area shall be the smaller of: a. The product of the allowed ornamental/special effects lighting power determined in accordance with Section 140.6(c)3Kiii, times floor square footage determined in accordance with Section 140.6(c)3Kiv; {or (0.5*10586.7) = 5293.35 W} b. The actual power of allowed ornamental/special effects lighting. {Installed power - 2112 W} Hence modeled 2112W or 2112/10586.7 = 0.2 W/ft2
Note on C50: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on I50: Sandeep: 160624_SDS: Space function updated which changes the baseline LPD
Note on M50: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on G52: Sandeep: Standards_Section 140.6: TAilored Method- The additional allowed power for ornamental/special effects lighting for each applicable area shall be the smaller of: a. The product of the allowed ornamental/special effects lighting power determined in accordance with Section 140.6(c)3Kiii, times floor square footage determined in accordance with Section 140.6(c)3Kiv; {or (0.5*10586.7) = 5293.35 W} b. The actual power of allowed ornamental/special effects lighting. {Installed power - 2112 W} Hence modeled 2112W or 2112/10586.7 = 0.2 W/ft2
Note on C56: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on I56: Sandeep: 160624_SDS: Space function updated which changes the baseline LPD
Note on M56: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'

## 030006-OffMed-Run13 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run13 |  | Model Revision no. |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run13.cibd16 |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name
Core_bottom | Waiting Area |  | 0.6 | - | - |  | 1.2 |  | 0.1 |  | 1.9 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_2 | Lobby, Main Entry |  | 0.816 |  | 0.09 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.8 | - | - | - | - | - | - |  | 0.8 |  | OfficeLights |  | AreaCategoryMethod
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area |  | 0.6 | - | - |  | 1.2 |  | 0.1 |  | 1.9 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_2 | Lobby, Main Entry |  | 0.816 |  | 0.09 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.8 | - | - | - | - | - | - |  | 0.8 |  | OfficeLights |  | AreaCategoryMethod
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area |  | 0.6 | - | - |  | 1.2 |  | 0.1 |  | 1.9 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_2 | Lobby, Main Entry |  | 0.816 |  | 0.09 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.8 | - | - | - | - | - | - |  | 0.8 |  | OfficeLights |  | AreaCategoryMethod
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name
Core_bottom | Waiting Area |  | 0.64 | - | - |  | 0.5 |  | 0.1 |  | 1.24 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 0.64 |  | 0.1 | - | - | - | - |  | 0.74 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_2 | Lobby, Main Entry |  | 0.64 |  | 0.09 | - | - | - | - |  | 0.73 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_3 | Lobby, Main Entry |  | 0.64 |  | 0.1 | - | - | - | - |  | 0.74 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.75 | - | - | - | - | - | - |  | 0.75 |  | OfficeLights |  | AreaCategoryMethod
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area |  | 0.64 | - | - |  | 0.5 |  | 0.1 |  | 1.24 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry |  | 0.64 |  | 0.1 | - | - | - | - |  | 0.74 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_2 | Lobby, Main Entry |  | 0.64 |  | 0.09 | - | - | - | - |  | 0.73 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_3 | Lobby, Main Entry |  | 0.64 |  | 0.1 | - | - | - | - |  | 0.74 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.75 | - | - | - | - | - | - |  | 0.75 |  | OfficeLights |  | AreaCategoryMethod
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area |  | 0.64 | - | - |  | 0.5 |  | 0.1 |  | 1.24 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry |  | 0.64 |  | 0.1 | - | - | - | - |  | 0.74 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_2 | Lobby, Main Entry |  | 0.64 |  | 0.09 | - | - | - | - |  | 0.73 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_3 | Lobby, Main Entry |  | 0.64 |  | 0.1 | - | - | - | - |  | 0.74 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 0.75 | - | - | - | - | - | - |  | 0.75 |  | OfficeLights |  | AreaCategoryMethod
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Note on C19: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M19: Sandeep: 160624_SDS: Space function updated along with the LPD
Note on Q19: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on C25: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M25: Sandeep: 160624_SDS: Space function updated along with the LPD
Note on Q25: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on C31: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M31: Sandeep: 160624_SDS: Space function updated along with the LPD
Note on Q31: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on C44: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M44: Sandeep: 160624_SDS: Space function updated which changes the baseline LPD
Note on Q44: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on C50: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M50: Sandeep: 160624_SDS: Space function updated which changes the baseline LPD
Note on Q50: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'
Note on C56: Sandeep: 160624_SDS: Space function updated to ensure atleast one of the zones in the multi-zone system is not controlled by DDC (SpaceFunction is responsible for the OccDens which triggers requirement for CO2 sensors aka DDC)
Note on M56: Sandeep: 160624_SDS: Space function updated which changes the baseline LPD
Note on Q56: Sandeep: 160624_SDS: SpaceFunction type - 'Office (greater than 250 square feet in floor area) is not compatible with the interior lighting specification method "Tailored Method', hence updated to 'AreaCategory Method'

## 020006-OffSml-Run14 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020006-OffSml-Run14 |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 020006-OffSml-Run14.cibd16 |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function |  | Installed Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor | Lighting Power Density (Simulated) (W/ft2) | Lighting Schedule
Spc | SpcFunc |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF | Spc:IntLPDReg | IntLtgRegSchRef
Perimeter_ZN_1 | Office (Greater than 250 square feet in floor area) |  | 1152 |  | 1094.4 |  | DemandResponsiveControl |  | 0.05 | 0.9 | OfficeLights
Perimeter_ZN_2 | Office (Greater than 250 square feet in floor area) |  | 640 |  | 608 |  | DemandResponsiveControl |  | 0.05 | 0.84 | OfficeLights
Perimeter_ZN_3 | Office (Greater than 250 square feet in floor area) |  | 1152 |  | 1094.4 |  | DemandResponsiveControl |  | 0.05 | 0.9 | OfficeLights
Perimeter_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 640 |  | 608 |  | DemandResponsiveControl |  | 0.05 | 0.84 | OfficeLights
Core_bottom | Office (Greater than 250 square feet in floor area) |  | 1408 |  | 1337.6 |  | DemandResponsiveControl |  | 0.05 | 0.83 | OfficeLights
Baseline
Internal Load Components
Space
Space Name | Space Function |  | Installed Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor | Lighting Power Density (Simulated) (W/ft2) | Lighting Schedule
Spc | SpcFunc |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF | Spc:IntLPDReg | IntLtgRegSchRef
Perimeter_ZN_1 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Perimeter_ZN_2 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Perimeter_ZN_3 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Perimeter_ZN_4 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Core_bottom | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Note on K13: Sandeep: The Proposed Transform does not utilize the PAF, the evaluation for the same has already been made and only the final LPD is relevant

## 080006-Whse-Run15 (hidden)
Note: Reference positions of the daylight control sensors are not being checked.
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 080006-Whse-Run15 |  | Model Revision no. |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006-Whse-Run15.cibd16 |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting Control |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Daylighting
Space
Space Name | Space Function |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | Continuous | - | - | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 10730.4 |  | 5000 |  | 250 |  | 250
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 34302 |  | 15000 |  | 250 |  | 250
Space Name | Space Function |  | Primary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint
Spc |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 538.667 |  | 150 |  | 400 |  | 400
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Space Name | Space Function |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 421.33 | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Baseline
Daylighting
Space
Space Name | Space Function |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | Continuous | - | - | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 10730.4 |  | 6438.25 |  | 250 |  | 250
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 34387.5 |  | 20632.5 |  | 250 |  | 250
Space Name | Space Function |  | Primary Sidelit Daylit Area |  | Controlled General Lighting Power |  | Illuminance Setpoint |  | Adjusted Illuminance Setpoint
|  |  | (ft2) |  | (W) |  | (lux) |  | (lux)
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 538.667 |  | 404 |  | 400 |  | 400
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Space Name | Space Function |  | Secondary Sidelit Daylit Area |  | Controlled General Lighting Power |  | Illuminance Setpoint |  | Adjusted Illuminance Setpoint
|  |  | (ft2) |  | (W) |  | (lux) |  | (lux)
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 421.33 |  | 316 |  | 287.5 |  | 1150
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -

## 050006-RetlMed-Run16 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 050006-RetlMed-Run16 |  |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 050006-RetlMed-Run16.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Retail |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting Control |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function | Space Floor Area (ft2) |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | Allowance Area (ft2)
Spc |  |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 |  | 0.6 | - | - |  | 0.6 | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 |  | 1.2 | - | - |  | 1.2 | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 0.95 | - | - |  | 0.95 | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 1.6 |  | 0.75 |  | 2.35 |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 1.2 | - | - |  | 1.2 | - | -
Daylighting
Space
Space Name | Space Function | Space Floor Area (ft2) |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 |  | Continuous |  | 16742.6 |  | 20091.1 |  | 950 |  | 950
Front_Entry | Lobby, Main Entry | 129.167 |  | ContinuousPlusOff | - | - | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | Continuous | - | - | - | - | - | - | - | -
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | Continuous | - | - | - | - | - | - | - | -
Space Name | Space Function | Space Floor Area (ft2) |  | Primary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint
Spc |  |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | - | - | - | - | - | - | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 114.3 |  | 108.58 |  | 200 |  | 300
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 718.1 |  | 1216 |  | 950 |  | 1425
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 718.1 |  | 861.69 |  | 950 |  | 1425
Space Name | Space Function | Space Floor Area (ft2) |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | - | - | - | - | - | - | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 14.8 | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 721.5 |  | 2592 |  | 950 |  | 1900
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 721.5 |  | 865.813 |  | 950 |  | 1900
Baseline
Internal Load Components
Space
Space Name | Space Function | Space Floor Area (ft2) |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | Allowance Area (ft2)
Spc |  |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 |  | 0.6 | - | - |  | 0.6 | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 |  | 1.2 | - | - |  | 1.2 | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 0.95 | - | - |  | 0.95 | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 1.34 |  | 0.38422 |  | 1.7242 |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 1.2 | - | - |  | 1.2 | - | -
Daylighting
Space
Spc
Space Name | Space Function | Space Floor Area (ft2) |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 |  | Continuous |  | 16742.6 |  | 20091.1 |  | 950 |  | 950
Front_Entry | Lobby, Main Entry | 129.167 | - | - | - | - | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | Continuous | - | - | - | - | - | - | - | -
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | Continuous | - | - | - | - | - | - | - | -
Space Name | Space Function | Space Floor Area (ft2) |  | Primary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint
Spc |  |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | - | - | - | - | - | - | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 114.297 | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 718.075 |  | 1238.1174 |  | 950 |  | 1425
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 718.075 |  | 861.69 |  | 950 |  | 1425
Space Name | Space Function | Space Floor Area (ft2) |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | - | - | - | - | - | - | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 14.7656 | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 721.51 |  | 1244.04 |  | 950 |  | 1900
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 721.51 |  | 865.812 |  | 950 |  | 1900
Note on H37: Sandeep: 151130: Exterior Lighting system - 'Front_Retail_Task&FloorDisplayLtgSys' with 1,216 W is assigned to Dalit zone - "PrimarySidelit'

## 020006-OffSml-Run18 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020006-OffSml-Run18 |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 020006-OffSml-Run18.cibd16 |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name | Status | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Perimeter_ZN_1 Thermal Zone | Perim1ZnSPVHP AirSys | New | SPVHP |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnSPVAC AirSys | New | SPVAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | New | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | New | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Thermal Zone - Floor/Zone | Zone System - Name | Status | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef |  |  | ZnSys:Type |  | ZnSys:AvailSchRef |  | ZnSys:ClgDsgnSupAirTemp |  | ZnSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl
Core_ZN Thermal Zone | CoreZNSPVAC ZnSys | New | PTAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
CoreZNSPVAC ZnSys | CoreZnCoolingCoil |  | DirectExpansion |  | 12 | - | - |  | CoilClgPTACEIRRatio_fTwbToadbSI |  | CoilClgPTACEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim1ZnSPVHP AirSys | Perim1ZnCoolingCoil |  | DirectExpansion |  | 12 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnSPVAC AirSys | Perim2ZnCoolingCoil |  | DirectExpansion |  | 12 | - | - |  | CoilClgPTACEIRRatio_fTwbToadbSI |  | CoilClgPTACEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil |  | DirectExpansion |  | 13 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil |  | DirectExpansion |  | 13 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name |  | Type |  | Coefficient of Performance (COP) |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Heat Pump Part-Load Efficiency Adjustment Curve |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  | CoilHtg:Type |  |  |  | CoilHtg:FurnThrmlEff |  |  |  | (HtPumpEIR_fPLFCrvRef) |  | (FurnHIR_fPLRCrvRef)
CoreZNSPVAC ZnSys | CoreZnHeatingCoil |  | Furnace (Natural Gas) | - | - |  | 0.80003 | - | - | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim1ZnSPVHP AirSys | Perim1ZnHeatingCoil |  | HeatPump |  | 3.5 | - | - | - | - |  | CoilHtgHPEIRRatio_fQFrac | - | -
Perim2ZnSPVAC AirSys | Perim2ZnHeatingCoil |  | Furnace (Natural Gas) | - | - |  | 0.80003 | - | - | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil |  | Furnace (Natural Gas) | - | - |  | 0.80003 | - | - | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil |  | Furnace (Natural Gas) | - | - |  | 0.80003 | - | - | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name |  | Control Method |  | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
CoreZNSPVAC ZnSys | CoreZnSupplyFan |  | Constant Volume |  | BrakeHorsePower |  | 1.6 | - | - | - | - |  | 2 |  | 0.865
Perim1ZnSPVHP AirSys | Perim1ZnSupplyFan |  | Constant Volume |  | BrakeHorsePower |  | 1.12 | - | - | - | - |  | 1.5 |  | 0.855
Perim2ZnSPVAC AirSys | Perim2ZnSupplyFan |  | Constant Volume |  | BrakeHorsePower |  | 0.8 | - | - | - | - |  | 1 |  | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan |  | Constant Volume |  | BrakeHorsePower |  | 1.2 | - | - | - | - |  | 1.5 |  | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan |  | Constant Volume |  | BrakeHorsePower |  | 0.8 | - | - | - | - |  | 1 |  | 0.855
Thermal Zone - Name | Conditioning Type |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_4 Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
AirSystem - Name | OA - Control Name | Status | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
AirSys |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
Perim1ZnSPVHP AirSys | Perim1OAControl | New | FixedDryBulb |  | NonIntegrated |  | 70 | - | -
Perim2ZnSPVAC AirSys | Perim2OAControl | New | NoEconomizer | - | - | - | - | - | -
Perim3ZnPSZ AirSys | Perim3 OAControl | New | NoEconomizer | - | - | - | - | - | -
Perim4ZnPSZ AirSys | Perim4 OAControl | New | NoEconomizer | - | - | - | - | - | -
Baseline
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Core_ZN Thermal Zone | BaseAirSys3 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | BaseAirSys3-2 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | BaseAirSys3-3 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | BaseAirSys3-4 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | BaseAirSys3-5 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilHtg:SysServed | CoilClg |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-2 | BaseSys3 CoilClg-2 |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-3 | BaseSys3 CoilClg-3 |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-4 | BaseSys3 CoilClg-4 |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-5 | BaseSys3 CoilClg-5 |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name |  | Type |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg |  | Furnace (Natural Gas) |  | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-2 | BaseSys3 CoilHtg-2 |  | Furnace (Natural Gas) |  | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-3 | BaseSys3 CoilHtg-3 |  | Furnace (Natural Gas) |  | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-4 | BaseSys3 CoilHtg-4 |  | Furnace (Natural Gas) |  | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-5 | BaseSys3 CoilHtg-5 |  | Furnace (Natural Gas) |  | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan |  | Constant Volume |  | StaticPressure |  | 1134.98 |  | 0.89431 |  | 0.5 |  | 2.5 |  | 1 | 0.855
BaseAirSys3-2 | BaseSys3 Fan-2 |  | Constant Volume |  | StaticPressure |  | 1136.94 |  | 0.89586 |  | 0.5 |  | 2.5 |  | 1 | 0.855
BaseAirSys3-3 | BaseSys3 Fan-3 |  | Constant Volume |  | StaticPressure |  | 594.292 |  | 0.46828 |  | 0.5 |  | 2.5 |  | 0.5 | 0.855
BaseAirSys3-4 | BaseSys3 Fan-4 |  | Constant Volume |  | StaticPressure |  | 881.199 |  | 0.69435 |  | 0.5 |  | 2.5 |  | 0.75 | 0.855
BaseAirSys3-5 | BaseSys3 Fan-5 |  | Constant Volume |  | StaticPressure |  | 642.385 |  | 0.50617 |  | 0.5 |  | 2.5 |  | 0.75 | 0.855
Thermal Zone - Name | Conditioning Type |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_4 Thermal Zone | Conditioned |  | OfficeClgSetPt |  | OfficeHtgSetPt
AirSystem - Name | OA - Control Name | Status | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
AirSys |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BaseAirSys3 | BaseSys3 OACtrl | New | NoEconomizer | - | - | - | - | - | -
BaseAirSys3-2 | BaseSys3 OACtrl-2 | New | NoEconomizer | - | - | - | - | - | -
BaseAirSys3-3 | BaseSys3 OACtrl-3 | New | NoEconomizer | - | - | - | - | - | -
BaseAirSys3-4 | BaseSys3 OACtrl-4 | New | NoEconomizer | - | - | - | - | - | -
BaseAirSys3-5 | BaseSys3 OACtrl-5 | New | NoEconomizer | - | - | - | - | - | -
Note on F22: Sandeep: 160706_SDS: System type switched from SPVAC to PTAC to enable correct translation by OS
Note on H80: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H98: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N98: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P98: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on R98: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T98: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.

## 030006-OffMed-Run19
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run19 |  |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 030006-OffMed-Run19.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Complete |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space Name | Space Function | Space Floor Area (ft2) |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name
Spc |  |  |  | RecptPwrDens |  | RecptSchRef:Name
Core_bottom | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_mid | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_top | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor | BottomVAV | New |  | Bottom Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | Mid VAV | New |  | Mid Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | Top VAV | New |  | Top Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Core_bottom Thermal Zone | Core_bottomZnPSZ AirSys | New |  | Bottom Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Core_mid Thermal Zone | Core_midZnPSZ AirSys | New |  | Mid Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Core_top Thermal Zone | Core_topZnPSZ AirSys | New |  | Top Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | New |  | DirectExpansion |  | 12.96 |  | 15.12 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | New |  | DirectExpansion |  | 12.96 |  | 15.12 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | New |  | DirectExpansion |  | 12.96 |  | 15.12 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_bottomZnPSZ AirSys | Core_bottomZnCoolingCoil | New |  | DirectExpansion |  | 13.65 |  | 15.7 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_midZnPSZ AirSys | Core_midZnCoolingCoil | New |  | DirectExpansion |  | 13.65 |  | 15.7 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_topZnPSZ AirSys | Core_topZnCoolingCoil | New |  | DirectExpansion |  | 13.65 |  | 15.7 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating | New |  | HotWater
Mid VAV | Mid VAV CoilHeating | New |  | HotWater
Top VAV | Top VAV CoilHeating | New |  | HotWater
BottomVAV | (All ReheatCoils) | New |  | HotWater
Mid VAV | (All ReheatCoils) | New |  | HotWater
Top VAV | (All ReheatCoils) | New |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Power adjustment curve
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
Bottom Floor | BottomVAV SupplyFan | New |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 6.21 | - | - | - | - |  | 7.5 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Mid Floor | MidVAV SupplyFan | New |  | VariableSpeedDrive |  | Static Pressure |  | 10850 |  | 7.8917 |  | 0.65 |  | 3 |  | 10 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Top Floor | TopVAV SupplyFan | New |  | VariableSpeedDrive |  | Static Pressure |  | 10200 |  | 9.3767 |  | 0.6 |  | 3.5 |  | 10 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Core_bottom Thermal Zone | Core_bottomZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
Core_mid Thermal Zone | Core_midZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
Core_top Thermal Zone | Core_topZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV |  | New |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV |  | New |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV |  | New |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Core_bottomZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Core_midZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Core_topZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Perimeter Zones) | Conditioned | New |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Core Zones) | Conditioned | New |  | DataClgSetpt |  | DataHtgSetpt
(All Plenum) | Plenum | New | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 |  | New |  | 1700000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Baseline
Internal Load Components
Space Name | Space Function | Space Floor Area (ft2) |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name
Spc |  |  |  | RecptPwrDens |  | RecptSchRef:Name
Core_bottom | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_mid | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_top | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Core_bottom Thermal Zone | BaseAirSys11 | New |  | Bottom Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
Core_mid Thermal Zone | BaseAirSys11-2 | New |  | Mid Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
Core_top Thermal Zone | BaseAirSys11-3 | New |  | Top Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 10.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11 | BaseSys11 CoilClg | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11-2 | BaseSys11 CoilClg-2 | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11-3 | BaseSys11 CoilClg-3 | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index | Pump Power Part-load Curve
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx | (Pwr_fPLRCrvRef)
Bottom Floor (Peripheral Zones) | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 7151.02 |  | 6.5738 |  | 0.6 |  | 3.5 |  | 7.5 |  | 0.917 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Mid Floor (Peripheral Zones) | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 8324.53 |  | 7.6526 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Top Floor (Peripheral Zones) | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 8663.41 |  | 7.9641 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Core_bottom Thermal Zone | BaseSys11 Fan | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 38118.4 |  | 23.2974 |  | 0.62 |  | 2.4045 |  | 20 |  | 0.93 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Core_mid Thermal Zone | BaseSys11 Fan-2 | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 37976.2 |  | 23.2105 |  | 0.62 |  | 2.4045 |  | 20 |  | 0.93 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Core_top Thermal Zone | BaseSys11 Fan-3 | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 38336.7 |  | 23.582 |  | 0.62 |  | 2.4201 |  | 25 |  | 0.936 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Bottom Floor (Peripheral Zones) | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 6786.56 |  | 2.0053 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
Mid Floor (Peripheral Zones) | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 7960.07 |  | 2.3521 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
Top Floor (Peripheral Zones) | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 8298.95 |  | 2.4522 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Peripheral Zones) | Conditioned | New |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Core Zones) | Conditioned | New |  | DataClgSetpt |  | DataHtgSetpt
(All Plenum) | Plenum | New | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 126995 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Note on H131: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on R149: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T149: Sandeep:
Note on H151: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on P151: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on H152: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on P152: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on H153: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on P153: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on H157: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on P157: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on H158: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on P158: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on H159: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on P159: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on H180: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.

## 040006-OffLrg-Run20
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 040006-OffLrg-Run20 |  |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 040006-OffLrg-Run20.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Complete |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | New Complete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Basement Floor | BsmntZnPSZ AirSys | New |  | Basement Floor/Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Bottom Floor | BaseAirSys6-Bot | New |  | Bottom Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys6-Mid | New |  | Mid Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Hi Floor | BaseAirSys6-Hi | New |  | Hi Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys6-Top | New |  | Top Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BsmntZnPSZ AirSys | BsmntZnCoolingCoil | New |  | DirectExpansion |  | 11.4 |  | 13.16 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys6-Bot | BaseSys6 CoilClg-Bot | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Mid | BaseSys6 CoilClg-Mid | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Hi | BaseSys6 CoilClg-Hi | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Top | BaseSys6 CoilClg-Top | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating |  |  | HotWater
Mid VAV | Mid VAV CoilHeating |  |  | HotWater
Hi VAV | Hi VAV CoilHeating |  |  | HotWater
Top VAV | Top VAV CoilHeating |  |  | HotWater
BottomVAV | (All ReheatCoils) |  |  | HotWater
Mid VAV | (All ReheatCoils) |  |  | HotWater
Hid VAV | (All ReheatCoils) |  |  | HotWater
Top VAV | (All ReheatCoils) |  |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Basement Floor | BsmntZnSupplyFan | New |  | ConstantVolume |  | StaticPressure |  | 190000 |  | 169.0293 |  | 0.62 |  | 3.5 |  | 200 |  | 0.962
Bottom Floor | BaseSys6 Fan-Bot | New |  | VariableSpeedDrive |  | StaticPressure |  | 38624.3 |  | 44.1787 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Mid Floor | BaseSys6 Fan-Mid | New |  | VariableSpeedDrive |  | StaticPressure |  | 40232.3 |  | 46.018 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Hi Floor | BaseSys6 Fan-Hi | New |  | VariableSpeedDrive |  | StaticPressure |  | 40232.3 |  | 46.018 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Top Floor | BaseSys6 Fan-Top | New |  | VariableSpeedDrive |  | StaticPressure |  | 42188.3 |  | 48.2553 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BsmntZnPSZ AirSys |  |  |  | NoEconomizer |  | UNDEFINED
BaseAirSys6-Bot |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Mid |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Hi |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Top |  |  |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Basement Floor | Conditioned |  |  | DataClgSetpt |  | DataHtgSetpt
Bottom, Mid, Hi and Top Floors | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 2887230 |  | 0.82 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Centrifugal |  | Electric |  | Fluid |  | 5268800 |  | 6.01 (0.585 kW/ton) |  | 0.38 |  | 0.1
Base Chlr-2 | BaseChWSystem | New |  | Centrifugal |  | Electric |  | Fluid |  | 5268800 |  | 6.01 (0.585 kW/ton) |  | 0.38 |  | 0.1
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Base Chlr-2 | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment |  |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 144.31 |  | 2.74 (19 W/gpm) |  | 5 |  | 63.2 |  | 0.895 | - | -
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 144.31 |  | 2.74 (19 W/gpm) |  | 5 |  | 63.2 |  | 0.895 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 1229.88 |  | 16.01 (13 W/gpm) |  | 20 |  | 45 |  | 0.93 | - | -
Base CW Pump-2 | Base Tower-2 | New |  | OnDemand |  | ConstantSpeed |  | 1229.88 |  | 16.01 (13 W/gpm) |  | 20 |  | 45 |  | 0.93 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 526.68 |  | 8.15 (15.5 W/gpm) |  | 15 |  | 53.172 |  | 0.924 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
Base ChW Pump-2 | Base Chlr-2 | New |  | OnDemand |  | VariableSpeed |  | 526.68 |  | 8.15 (15.5 W/gpm) |  | 15 |  | 53.172 |  | 0.924 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
0
480.183
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 6151760 |  | 1229.88 |  | 20.5 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Base Tower-2 | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 6151760 |  | 1229.88 |  | 20.5 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Baseline
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys6 | New |  | Bottom Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys6-2 | New |  | Mid Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Hi Floor | BaseAirSys6-3 | New |  | Hi Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys6-4 | New |  | Top Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Basement Floor | BaseAirSys10 | New |  | Basement Floor/Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys6 | BaseSys6 CoilClg | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-2 | BaseSys6 CoilClg-2 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-3 | BaseSys6 CoilClg-3 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-4 | BaseSys6 CoilClg-4 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys10 | BaseSys10 CoilClg | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys6 | BaseSys6 CoilHtg |  |  | HotWater
BaseAirSys6-2 | BaseSys6 CoilHtg-2 |  |  | HotWater
BaseAirSys6-3 | BaseSys6 CoilHtg-3 |  |  | HotWater
BaseAirSys6-4 | BaseSys6 CoilHtg-4 |  |  | HotWater
BaseAirSys6/6-2/6-3/6-4 | (All BaseVAVReheatCoils) |  |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx
Bottom Floor | BaseSys6 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 38154 |  | 43.6408 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945 | - | -
Mid Floor | BaseSys6 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 32101.5 |  | 36.7179 |  | 0.62 |  | 4.5 |  | 40 |  | 0.941 | - | -
Hi Floor | BaseSys6 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 32083.9 |  | 36.6978 |  | 0.62 |  | 4.5 |  | 40 |  | 0.941 | - | -
Top Floor | BaseSys6 Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 30387.5 |  | 34.7574 |  | 0.62 |  | 4.5 |  | 40 |  | 0.941 | - | -
Basement Floor | BaseSys10 Fan | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 142675 |  | 89.4513 |  | 0.62 |  | 2.4666 |  | 75 |  | 0.954 |  | 0.49
Bottom Floor | BaseRelief Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 36236.3 |  | 11.421 |  | 0.5 |  | 1 |  | 15 |  | 0.924 | - | -
Mid Floor | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 22513.3 |  | 7.0958 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917 | - | -
Hi Floor | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 22495.7 |  | 7.0902 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917 | - | -
Top Floor | BaseRelief Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 28469.9 |  | 8.9732 |  | 0.5 |  | 1 |  | 10 |  | 0.917 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseSys6 OACtrl |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-2 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-3 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-4 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys10 OACtrl |  | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Basement Floor | Conditioned |  |  | DataClgSetpt |  | DataHtgSetpt
Bottom, Mid, Hi and Top Floors | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 1999770 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Centrifugal |  | Electric |  | Fluid |  | 6644380 |  | 6.01 (0.585 kW/ton) | - | - |  | 0.1
Base Chlr-2 | BaseChWSystem | New |  | Centrifugal |  | Electric |  | Fluid |  | 6644380 |  | 6.01 (0.585 kW/ton) | - | - |  | 0.1
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Base Chlr-2 | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment |  |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 99.95 |  | 1.9 (19 W/gpm) |  | 3 |  | 63.2 |  | 0.895 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 1549.34 |  | 20.04 (12.9 W/gpm) |  | 30 |  | 45 |  | 0.936 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 664.19 |  | 10.95 (16.5 W/gpm) |  | 15 |  | 56.611 |  | 0.924 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 99.95 |  | 1.9 (19 W/gpm) |  | 3 |  | 63.2 |  | 0.895 | - | -
Base ChW Pump-2 | Base Chlr-2 | New |  | OnDemand |  | VariableSpeed |  | 664.19 |  | 10.95 (16.5 W/gpm) |  | 15 |  | 56.611 |  | 0.924 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base CW Pump-2 | Base Tower-2 | New |  | OnDemand |  | ConstantSpeed |  | 1549.34 |  | 20.04 (12.9 W/gpm) |  | 30 |  | 45 |  | 0.936 | - | -
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 7749660 |  | 1549.34 |  | 25.82 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Base Tower-2 | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 7749660 |  | 1549.34 |  | 25.82 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Note on P73: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on N75: Sandeep: Chiller Type: Centrifugal, Path B Efficiency Cap <150 Tons = 0.695 kW/Ton Cap <300 Tons = 0.635 kW/Ton Cap <400 Tons = 0.595 kW/Ton Cap <600 Tons = 0.585 kW/Ton Cap >=600 Tons = 0.585 kW/Ton EER = 12 / (kW/ton) COP = EER / 3.412
Note on N76: Sandeep: Cap <75 Tons = 0.78 kW/Ton Cap <150 Tons = 0.75 kW/Ton Cap <300 Tons = 0.68 kW/Ton Cap >=300 Tons = 0.625 kW/Ton EER = 12 / (kW/ton) COP = EER / 3.412
Note on J79: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on L87: Sandeep: Pump Motor Power-Per-Unit-Flow: 19 W/gpm for heating hot water and service hot water pumps
Note on L88: Sandeep: Pump Motor Power-Per-Unit-Flow: 19 W/gpm for heating hot water and service hot water pumps
Note on L89: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P89 for the calculation method Impeller Efficiency: 0.7
Note on L90: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P90 for the calculation method Impeller Efficiency: 0.7
Note on L91: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P91, for the calculation method Impeller Efficiency: 0.7.
Note on L92: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P92, for the calculation method Impeller Efficiency: 0.7.
Note on R130: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T130: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on H132: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N132: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P132: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on H133: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N133: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P133: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on H134: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N134: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P134: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on H135: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N135: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P135: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N136: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on H137: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on H138: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on H139: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on H140: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on H160: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.
Note on P165: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on R165: Sandeep: The standard design 'Chiller Min Unloading Ratio' is determined based on the 'Chiller Type'. Centrifugal = 10% See ACM ' Default Minimum Unloading Ratios Table-48 for further details
Note on F167: Sandeep: 'The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller, equally sized >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons.
Note on H167: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on J167: Sandeep: Standard Design The baseline chiller is always assumed to have a water-cooled condenser, although the chiller type will change depending on the design capacity.
Note on L167: Sandeep: 151106: Auto-sized. The full load output of the chiller operating at rating temperatures and flows including adjustment for pump heat and the project sizing ratio.
Note on N167: Sandeep: Chiller Type: Centrifugal, Path B Efficiency Cap <150 Tons = 0.695 kW/Ton Cap <300 Tons = 0.635 kW/Ton Cap <400 Tons = 0.595 kW/Ton Cap <600 Tons = 0.585 kW/Ton Cap >=600 Tons = 0.585 kW/Ton EER = 12 / (kW/ton) COP = EER / 3.412 Use the minimum efficiency requirements from Tables 110.2-D Path B. If Chiller Type is Screw, use the efficiency for Positive Displacement chillers from Table 110.2-D.
Note on F168: Sandeep: 'The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller, equally sized >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons.
Note on H168: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on J168: Sandeep: Standard Design The baseline chiller is always assumed to have a water-cooled condenser, although the chiller type will change depending on the design capacity.
Note on L168: Sandeep: 151106: Auto-sized. The full load output of the chiller operating at rating temperatures and flows including adjustment for pump heat and the project sizing ratio.
Note on N168: Sandeep: Chiller Type: Centrifugal, Path B Efficiency Cap <150 Tons = 0.695 kW/Ton Cap <300 Tons = 0.635 kW/Ton Cap <400 Tons = 0.595 kW/Ton Cap <600 Tons = 0.585 kW/Ton Cap >=600 Tons = 0.585 kW/Ton EER = 12 / (kW/ton) COP = EER / 3.412 Use the minimum efficiency requirements from Tables 110.2-D Path B. If Chiller Type is Screw, use the efficiency for Positive Displacement chillers from Table 110.2-D.
Note on R177: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on F179: Sandeep: The baseline system pumps are assumed to operate in On-Demand mode. The heating hot water pumps are tied to the boiler operation.
Note on H179: Sandeep: The hot water pumps shall be modeled as fixed-speed, variable flow, riding the curve.
Note on J179: Sandeep: Please refer to the reporting file - '040006-OffLrg-Run20 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formula below Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on L179: Sandeep: Pump Motor Power-Per-Unit-Flow: 19 W/gpm for heating hot water and service hot water pumps
Note on N179: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on P179: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L179) Impeller Efficiency: 0.7
Note on R179: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on J180: Sandeep: 'Please refer to the reporting file - '040006-OffLrg-Run20 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formula below Cooling Tower Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 10 degF
Note on L180: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow capacity: Autosized Total Head: Refer to P182), for the calculation method Impeller Efficiency:0.7
Note on N180: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on P180: Sandeep: For condenser water pumps, Head: 45 ft
Note on R180: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on J181: Sandeep: 'Please refer to the reporting file - '040006-OffLrg-Run20 - ap - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formula below Chiller Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 20 degF
Note on L181: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P185, for the calculation method Impeller Efficiency: 0.7.
Note on N181: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on P181: Sandeep: For chilled water pumps, 40 ft plus an additional allowance of 0.03 ft/ton, but not to exceed 100 ft. (See formula in the cell above)
Note on R181: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on F182: Sandeep: The baseline system pumps are assumed to operate in On-Demand mode. The heating hot water pumps are tied to the boiler operation.
Note on H182: Sandeep: The hot water pumps shall be modeled as fixed-speed, variable flow, riding the curve.
Note on J182: Sandeep: Please refer to the reporting file - '040006-OffLrg-Run20 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formula below Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on L182: Sandeep: Pump Motor Power-Per-Unit-Flow: 19 W/gpm for heating hot water and service hot water pumps
Note on N182: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on P182: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L180) Impeller Efficiency: 0.7
Note on R182: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on J183: Sandeep: 'Please refer to the reporting file - '040006-OffLrg-Run20 - ap - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formula below Chiller Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 20 degF
Note on L183: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P186, for the calculation method Impeller Efficiency: 0.7.
Note on N183: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on P183: Sandeep: For chilled water pumps, 40 ft plus an additional allowance of 0.03 ft/ton, but not to exceed 100 ft. (See formula in the cell above)
Note on R183: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on J184: Sandeep: 'Please refer to the reporting file - '040006-OffLrg-Run20 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formula below Cooling Tower Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 10 degF
Note on L184: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow capacity: Autosized Total Head: Refer to P183), for the calculation method Impeller Efficiency:0.7
Note on N184: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on P184: Sandeep: For condenser water pumps, Head: 45 ft
Note on R184: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on N189: Sandeep: The cooling tower fan horsepower is 60 gpm/hp.
Note on N190: Sandeep: The cooling tower fan horsepower is 60 gpm/hp.

## 080006-Whse-Run21 (hidden)
General Details |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 080006-Whse-Run21 |  | Model Revision no. | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006-Whse-Run21.cibd16 |  | Version of Ruleset (Trunk rev. No.) | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse |  | Date Tested | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC |  | Testing Performed by | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [5 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name |  | Type | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  | AirSys:Type | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Zone1 Office Thermal Zone | OfficeZnPSZAirSys |  | SZAC | WarehouseHVACAvail |  | 55 |  | 95 |  | NoSATControl
Zone2 Fine Storage Thermal Zone | FineSto_ZnPSZAirSys |  | SZAC | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
Zone3 Bulk Storage Thermal Zone | BulkSto_ZnPSZAirSys |  | SZAC | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name |  | Type | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  | CoilClg:Type | CoilClg:DXEER |  | CoilClg:DXIEER |  |  |  | (DXEIR_fTempCrvRef) | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
OfficeZnPSZAirSys | OfficeZnCoolingCoil |  | DirectExpansion | 11.2 |  | 12.9 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXEIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name |  | Type | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
OfficeZnPSZAirSys | OfficeZnHeatingCoil |  | Furnace (Natural Gas) | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
FineSto_ZnPSZAirSys | FineSto_ZnHeatingCoil |  | Furnace (Natural Gas) | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
BulkSto_ZnPSZAirSys | BulkSto_ZnHeatingCoil |  | Furnace (Natural Gas) | 0.81 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name |  | Control Method | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  | Fan:CtrlMthd | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
OfficeZnPSZAirSys | OfficeZnSupplyFan |  | Constant Volume | BreakHorsePower |  | 2 | - | - | - | - | 5 | 0.89
FineSto_ZnPSZAirSys | FineSto_ZnSupplyFan |  | Constant Volume | BreakHorsePower |  | 5.5 | - | - | - | - | 10 | 0.92
BulkSto_ZnPSZAirSys | BulkSto_ZnSupplyFan |  | Constant Volume | BreakHorsePower |  | 20 | - | - | - | - | 30 | 0.92
Thermal Zone - Name | Conditioning Type |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Zone1 Office Thermal Zone | Conditioned |  | WarehouseClgSetPt | WarehouseHtgSetPt
Zone2 Fine Storage Thermal Zone | Conditioned | - | - | WarehouseHtgSetPt
Zone3 Bulk Storage Thermal Zone | Conditioned | - | - | WarehouseHtgSetPt
Baseline
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name |  | Type | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  | AirSys:Type | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Zone1 Office Thermal Zone | BaseAirSys3 |  | SZAC | WarehouseHVACAvail |  | 55 |  | 95 |  | NoSATControl
Zone2 Fine Storage Thermal Zone | BaseAirSys9 |  | HV | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
Zone3 Bulk Storage Thermal Zone | BaseAirSys9-2 |  | HV | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name |  | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  | CoilClg:Type | CoilClg:DXEER |  |  |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg |  | DirectExpansion | 11 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name |  | Type | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys9 | BaseSys9 CoilHtg |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys9-2 | BaseSys9 CoilHtg-2 |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name |  | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan |  | Constant Volume | StaticPressure |  | 3300.8 |  | 2.6009 |  | 0.6 | 3 | 3 | 0.895
BaseAirSys9 | BaseSys9 Fan |  | Constant Volume | StaticPressure |  | 6165.05 |  | 4.8578 |  | 0.6 | 3 | 5 | 0.895
BaseAirSys9-2 | BaseSys9 Fan-2 |  | Constant Volume | StaticPressure |  | 29459.6 |  | 26.2081 |  | 0.62 | 3.5 | 30 | 0.936
BaseAirSys3 | BaseRelief Fan |  | VariableSpeedDrive | StaticPressure |  | 3173.31 |  | 0.93766 |  | 0.4 | 0.75 | 1 | 0.855
Thermal Zone - Name | Conditioning Type |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Zone1 Office Thermal Zone | Conditioned |  | WarehouseClgSetPt | WarehouseHtgSetPt
Zone2 Fine Storage Thermal Zone | Conditioned | - | - | WarehouseHtgSetPt
Zone3 Bulk Storage Thermal Zone | Conditioned | - | - | WarehouseHtgSetPt
Note on G54: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on G66: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on Q66: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on S66: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on M68: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on O68: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on M69: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on O69: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on M70: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on O70: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification

## 070015-HotSml-Run22
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 070015-HotSml-Run22 |  |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 070015-HotSml-Run22.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Common Areas: Floor 1 | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 2 | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 3 | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 4 | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Zone: KitchenFlr1 | KitchenMUA | New |  | Zone: KitchenFlr1 |  | SZAC |  | RestaurantHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl
GuestRoom101 Thermal Zone | GuestRoom101_Pkdg1Ph-SZAC | New |  | Residential Units: Floor 1 |  | PTAC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
GuestRoom102 Thermal Zone | GuestRoom102_Split1Ph-SZAC | New |  | Residential Units: Floor 2 |  | PTAC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
GuestRoom103 Thermal Zone | GuestRoom103_Pkgd1Ph-SZHP | New |  | Residential Units: Floor 3 |  | PTHP |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
GuestRoom104 Thermal Zone | GuestRoom104_Split1Ph-SZHP | New |  | Residential Units: Floor 4 |  | PTHP |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
Residential Units: All Floors (other than zones above) | Residential Units: FPFC (All) (other than zones above) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
Zone: KitchenFlr1 | KitchenExhaust | New |  | Zone: KitchenFlr1 |  | Exhaust |  | RestaurantHVACAvail | - | - | - | - |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 11 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
GuestRoom101_Pkdg1Ph-SZAC | GuestRoom101_Dx CoilClg | New |  | DirectExpansion |  | 10.8 |  |  |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
GuestRoom102_Split1Ph-SZAC | GuestRoom102_Dx CoilClg | New |  | DirectExpansion |  | 12.2 |  |  |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
GuestRoom103_Pkgd1Ph-SZHP | GuestRoom103_Dx CoilClg | New |  | DirectExpansion |  | 11.4072 |  |  |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
GuestRoom104_Split1Ph-SZHP | GuestRoom104_Dx CoilClg | New |  | DirectExpansion |  | 11.4072 |  |  |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Residential Units: FPFC (All) | Residential Units: FPFC CoilClg (All) | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | -
KitchenMUA | Kitchen CoilClg | New |  | DirectExpansion |  | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
GuestRoom101_Pkdg1Ph-SZAC | GuestRoom101_Furnace Htg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
GuestRoom102_Split1Ph-SZAC | GuestRoom102_Furnace Htg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
GuestRoom103_Pkgd1Ph-SZHP | GuestRoom103_HP CoilHtg | New |  | Electric | - | - | - | - | - | -
GuestRoom104_Split1Ph-SZHP | GuestRoom104_HP CoilHtg | New |  | Electric | - | - | - | - | - | -
Residential Units: FPFC (All) | Residential Units: FPFC CoilHtg (All) | New |  | HotWater | - | - | - | - | - | -
KitchenMUA | KitchenCoilHtg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 12396.3 |  | 12.6035 |  | 0.62 |  | 4 |  | 15 |  | 0.924
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1646.78 |  | 1.5571 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1674.51 |  | 1.5833 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1721.44 |  | 1.6277 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Residential Units: Floor1 | GuestRoom101_Supply Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom102_Supply Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom103_Supply Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom104_Supply Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom105_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom201_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom202_205_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom206_208_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom209_212_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom213_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom214_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom215_218_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom219_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom220_223_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom224_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom301_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom302_305_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom306_308_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom309_312_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom313_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom314_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom315_318_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom319_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom320_323_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom324_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom401_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom402_405_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom406_408_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom409_412_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom413_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom414_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom415_418_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom419_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom420_423_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom424_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Zone: KitchenFlr1 | Kitchen Fan | New |  | ConstantVolume |  | StaticPressure |  | 864.069 |  | 0.68085 |  | 0.5 |  | 2.5 |  | 0.75 |  | 0.855
Zone: KitchenFlr1 | KitchExh Fan | New |  | ConstantVolume |  | StaticPressure |  | 1050 |  | 0.49641 |  | 0.5 |  | 1.5 |  | 0.5 |  | 0.855
AirSystem - Name | OA - Control Name | Status |  | Economizer Control |  | Economizer Integration
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
KitchenMUA | Kitchen OAControl | New |  | DifferentialDryBulb |  | Integrated
Ventilation and Thermostat Schedules
Thermal Zone - Name | Conditioning Type | Status |  | Space Floor Area (ft2) |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Exhaust Flow (cfm) | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  |  |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZn:VentPerAreaSim | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
CorridorFlr1 Thermal Zone | Conditioned | New |  | 1620 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 8.1 |  | 0 |  | 0.15 |  | 243 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr2 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr3 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr4 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
EmployeeLoungeFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
ExerciseCenterFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontLoungeFlr1 Thermal Zone | Conditioned | New |  | 1755.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 125.4 |  | 15 |  | 0.15 |  | 1881 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontOfficeFlr1 Thermal Zone | Conditioned | New |  | 1404 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 7 |  | 0 |  | 0.15 |  | 211 | - | - | OfficeClgSetpt | OfficeHtgSetpt
LaundryRoomFlr1 Thermal Zone | Conditioned | New |  | 1053 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 5.3 |  | 0 |  | 0.15 |  | 158 | - | - | OfficeClgSetpt | OfficeHtgSetpt
MechanicalRoomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 3 |  | 0.5 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
KitchenFlr1 Thermal Zone | Conditioned | New |  | 864.1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.2 |  | 0 |  | 0.15 |  | 130 |  | 1050 | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr1 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr2 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr3 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr4 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr1 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr2 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr3 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr4 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RestroomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
Space Name | Conditioning Type | Status |  | Thermal Zone - Name |  | Space Function |  | Space Floor Area (ft2) |  | Number of Residential Living or Hotel/Motel units in a modeled space |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerArea (cfm/ft2) | Calculated Ventilation (cfm) | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
Spc:Name | ThrmlZn:Type |  |  | ThrmlZn:Name |  | SpcFunc |  |  |  | Spc:ResLivingUnitCnt |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerAreaSim |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
GuestRoom101 | Conditioned | New |  | GuestRoom101 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom102 | Conditioned | New |  | GuestRoom102 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom103 | Conditioned | New |  | GuestRoom103 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom104 | Conditioned | New |  | GuestRoom104 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom105 | Conditioned | New |  | GuestRoom105 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom201 | Conditioned | New |  | GuestRoom201 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom202_205 | Conditioned | New |  | GuestRoom202_205 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 | 120 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom206_208 | Conditioned | New |  | GuestRoom206_208 Thermal Zone |  | Hotel/Motel Guest Room |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | 0.079358 | 90 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom209_212 | Conditioned | New |  | GuestRoom209_212 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 | 120 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom213 | Conditioned | New |  | GuestRoom213 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom214 | Conditioned | New |  | GuestRoom214 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom215_218 | Conditioned | New |  | GuestRoom215_218 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 | 120 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom219 | Conditioned | New |  | GuestRoom219 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom220_223 | Conditioned | New |  | GuestRoom220_223 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 | 120 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom224 | Conditioned | New |  | GuestRoom224 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom301 | Conditioned | New |  | GuestRoom301 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom302_305 | Conditioned | New |  | GuestRoom302_305 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 | 120 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom306_308 | Conditioned | New |  | GuestRoom306_308 Thermal Zone |  | Hotel/Motel Guest Room |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | 0.079358 | 90 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom309_312 | Conditioned | New |  | GuestRoom309_312 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 | 120 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom313 | Conditioned | New |  | GuestRoom313 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom314 | Conditioned | New |  | GuestRoom314 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom315_318 | Conditioned | New |  | GuestRoom315_318 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 | 120 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom319 | Conditioned | New |  | GuestRoom319 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom320_323 | Conditioned | New |  | GuestRoom320_323 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 | 120 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom324 | Conditioned | New |  | GuestRoom324 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom401 | Conditioned | New |  | GuestRoom401 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed |  | - |  | 3 |  | 0.10274 | 36.06 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom402_405 | Conditioned | New |  | GuestRoom402_405 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404.1 |  | 4 |  | Forced |  | Sum |  | Fixed |  | - |  | 12 |  | 0.10273 | 144.25 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom406_408 | Conditioned | New |  | GuestRoom406_408 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1134.1 |  | 3 |  | Forced |  | Sum |  | Fixed |  | - |  | 9 |  | 0.099679 | 113.05 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom409_412 | Conditioned | New |  | GuestRoom409_412 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404.1 |  | 4 |  | Forced |  | Sum |  | Fixed |  | - |  | 12 |  | 0.10273 | 144.25 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom413 | Conditioned | New |  | GuestRoom413 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed |  | - |  | 3 |  | 0.10274 | 36.06 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom414 | Conditioned | New |  | GuestRoom414 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed |  | - |  | 3 |  | 0.10274 | 36.06 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom415_418 | Conditioned | New |  | GuestRoom415_418 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404 |  | 4 |  | Forced |  | Sum |  | Fixed |  | - |  | 12 |  | 0.10274 | 144.24 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom419 | Conditioned | New |  | GuestRoom419 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed |  | - |  | 3 |  | 0.10274 | 36.06 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom420_423 | Conditioned | New |  | GuestRoom420_423 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404 |  | 4 |  | Forced |  | Sum |  | Fixed |  | - |  | 12 |  | 0.10274 | 144.24 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom424 | Conditioned | New |  | GuestRoom424 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed |  | - |  | 3 |  | 0.10274 | 36.06 | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 363000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Electric |  | Fluid |  | 348000 |  | 4.51 (0.78 kW/ton) 15.4 EER |  | 0.5 |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Water-Side Economizer Name |  | Status |  | Type |  | Economizer Integration
(HX:Type) |  |  |  | (HX:Type) |  | (HX:EconoIntegration)
WS-Economizer |  | New |  | CounterFlow |  | Integrated
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 18.14 |  | 0.34 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 18.14 |  | 0.34 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 85 |  | 1.19 (14 W/gpm) |  | 1.5 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 34.79 |  | 0.45 (12.9 W/gpm) |  | 0.75 |  | 40.87 |  | 0.855 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 425184 |  | 85 |  | 1.42 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Baseline
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Common Areas: Floor 1 | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 2 | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 3 | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 4 | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Zone: KitchenFlr1 | BaseAirSys13 | New |  | Zone: KitchenFlr1 |  | SZAC |  | RestaurantHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Residential Units: All Floors | Residential Units: FPFC (All) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 11 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys13 | BaseSys13 CoilClg | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys2 | Residential Units: BaseSys2 CoilClg (All) | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys13 | BaseSys13 CoilHtg | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys2 | Residential Units: BaseSys2 CoilHtg (All) | New |  | HotWater | - | - |  | 1.25 | - | -
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 8247.55 |  | 7.5818 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | -
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1469.61 |  | 1.3896 |  | 0.5 |  | 3 |  | 1.5 |  | 0.865 | - | -
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1477.91 |  | 1.3974 |  | 0.5 |  | 3 |  | 1.5 |  | 0.865 | - | -
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1746.84 |  | 1.6517 |  | 0.5 |  | 3 |  | 2 |  | 0.865 | - | -
Zone: KitchenFlr1 | BaseSys13 Fan | New |  | ConstantVolume |  | Static Pressure |  | 798.755 |  | 0.62938 |  | 0.5 |  | 2.5 |  | 0.75 |  | 0.855 | - | -
Residential Units: All Floors | BaseSys2 Fan | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 167.38 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-2 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 169.73 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-3 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 164.89 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-4 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 161.52 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-5 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 161.99 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-6 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 182.63 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-7 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 152.34 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-8 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 150.837 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-9 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 139.335 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-10 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 140.6 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-11 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 137.48 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-12 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 135.227 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-13 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 137.32 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-14 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 134.697 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-15 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 136.36 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-16 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 171.79 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-17 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 143.188 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-18 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 152.62 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-19 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 141.12 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-20 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 141.69 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-21 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 138.77 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-22 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 138.07 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-23 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 136.98 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-24 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 136.773 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-25 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 135.62 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-26 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 233.14 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-27 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 199.148 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-28 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 215.667 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-29 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 198.405 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-30 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 199.21 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-31 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 195.4 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-32 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 193.982 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-33 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 193.55 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-34 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 192.025 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-35 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 191.57 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Common Areas: Floor 1 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 7846.58 |  | 2.3185 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | -
Common Areas: Floor 2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1362.95 |  | 0.40273 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
Common Areas: Floor 3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1371.25 |  | 0.40518 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
Common Areas: Floor 4 | BaseRelief Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1640.18 |  | 0.48465 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys13 | BaseSys13 OACtrl | New | - | - | - | -
BaseAirSys2 | - | New | - | - | - | -
Ventilation and Thermostat Schedules
Thermal Zone - Name | Conditioning Type | Status |  | Space Floor Area (ft2) |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Exhaust Flow (cfm) | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  |  |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZn:VentPerAreaSim | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
CorridorFlr1 Thermal Zone | Conditioned | New |  | 1620 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 8.1 |  | 0 |  | 0.15 |  | 243 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr2 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr3 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr4 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
EmployeeLoungeFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
ExerciseCenterFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontLoungeFlr1 Thermal Zone | Conditioned | New |  | 1755.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 125.4 |  | 15 |  | 0.15 |  | 1881 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontOfficeFlr1 Thermal Zone | Conditioned | New |  | 1404 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 7 |  | 0 |  | 0.15 |  | 211 | - | - | OfficeClgSetpt | OfficeHtgSetpt
LaundryRoomFlr1 Thermal Zone | Conditioned | New |  | 1053 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 5.3 |  | 0 |  | 0.15 |  | 158 | - | - | OfficeClgSetpt | OfficeHtgSetpt
MechanicalRoomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 3 |  | 0.5 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
KitchenFlr1 Thermal Zone | Conditioned | New |  | 864.1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.2 |  | 0 |  | 0.15 |  | 130 |  | 1050 | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr1 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr2 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr3 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr4 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr1 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr2 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr3 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr4 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RestroomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
Space Name | Conditioning Type | Status |  | Thermal Zone - Name |  | Space Function |  | Space Floor Area (ft2) |  | Number of Residential Living or Hotel/Motel units in a modeled space |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Infiltration Method | Required Ventilation - Simulated as Infiltration (cfm) | Infiltration Schedule |  | Exhaust Flow (cfm) | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
Spc:Name | ThrmlZn:Type |  |  | ThrmlZn:Name |  | SpcFunc |  |  |  | Spc:ResLivingUnitCnt |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | (InfMthd index="1") | (DsgnInfRt index="1") | (InfSchRef index="1") |  | ThrmlZn:ExhFlowSim | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
GuestRoom101 | Conditioned | New |  | GuestRoom101 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom102 | Conditioned | New |  | GuestRoom102 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom103 | Conditioned | New |  | GuestRoom103 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom104 | Conditioned | New |  | GuestRoom104 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom105 | Conditioned | New |  | GuestRoom105 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom201 | Conditioned | New |  | GuestRoom201 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom202_205 | Conditioned | New |  | GuestRoom202_205 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom206_208 | Conditioned | New |  | GuestRoom206_208 Thermal Zone |  | Hotel/Motel Guest Room |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | FlowSpace | 90 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom209_212 | Conditioned | New |  | GuestRoom209_212 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom213 | Conditioned | New |  | GuestRoom213 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom214 | Conditioned | New |  | GuestRoom214 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom215_218 | Conditioned | New |  | GuestRoom215_218 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom219 | Conditioned | New |  | GuestRoom219 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom220_223 | Conditioned | New |  | GuestRoom220_223 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom224 | Conditioned | New |  | GuestRoom224 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom301 | Conditioned | New |  | GuestRoom301 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom302_305 | Conditioned | New |  | GuestRoom302_305 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom306_308 | Conditioned | New |  | GuestRoom306_308 Thermal Zone |  | Hotel/Motel Guest Room |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | FlowSpace | 90 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom309_312 | Conditioned | New |  | GuestRoom309_312 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom313 | Conditioned | New |  | GuestRoom313 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom314 | Conditioned | New |  | GuestRoom314 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom315_318 | Conditioned | New |  | GuestRoom315_318 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom319 | Conditioned | New |  | GuestRoom319 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom320_323 | Conditioned | New |  | GuestRoom320_323 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom324 | Conditioned | New |  | GuestRoom324 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom401 | Conditioned | New |  | GuestRoom401 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 1 |  | FlowSpace | 26.06 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom402_405 | Conditioned | New |  | GuestRoom402_405 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed | - | - |  | 12 |  | FlowSpace | 144.246 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom406_408 | Conditioned | New |  | GuestRoom406_408 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed | - | - |  | 9 |  | FlowSpace | 113.046 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom409_412 | Conditioned | New |  | GuestRoom409_412 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed | - | - |  | 12 |  | FlowSpace | 144.246 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom413 | Conditioned | New |  | GuestRoom413 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 3 |  | FlowSpace | 36.06 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom414 | Conditioned | New |  | GuestRoom414 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 3 |  | FlowSpace | 36.06 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom415_418 | Conditioned | New |  | GuestRoom415_418 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed | - | - |  | 12 |  | FlowSpace | 144.24 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom419 | Conditioned | New |  | GuestRoom419 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 3 |  | FlowSpace | 36.06 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom420_423 | Conditioned | New |  | GuestRoom420_423 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed | - | - |  | 12 |  | FlowSpace | 144.24 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom424 | Conditioned | New |  | GuestRoom424 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 3 |  | FlowSpace | 36.06 | On | - | - | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 241918 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Electric |  | Fluid |  | 330372 |  | 4.51 (0.78 kW/ton) 15 EER | - | - |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 12.09 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 80.699 |  | 1.13 (14 W/gpm) |  | 1.5 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 33.025 |  | 0.42 (12.8 W/gpm) |  | 0.5 |  | 40.8259 |  | 0.855 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 12.09 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 403646 |  | 80.69 |  | 1.34 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Note on B23: Sandeep: 150630_SDS: Added in cycle v3c.
Note on H23: Sandeep: 160707_SDS: System type switched from SZAC to PTAC to enable correct translation by OS
Note on H24: Sandeep: 160707_SDS: System type switched from SZAC to PTAC to enable correct translation by OS
Note on H25: Sandeep: 160707_SDS: System type switched from SZHP to PTHPto enable correct translation by OS
Note on H26: Sandeep: 160707_SDS: System type switched from SZHP to PTHPto enable correct translation by OS
Note on P118: Sandeep: Multiplier of 0.5 has been added.
Note on V150: Sandeep: Multiplier of 0.5 has been added.
Note on P195: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on N197: Sandeep: Chiller Type: Screw, Path B Efficiency Cap <75 Tons = 0.78 kW/Ton Cap <150 Tons = 0.75 kW/Ton Cap <300 Tons = 0.68 kW/Ton Cap >=300 Tons = 0.625 kW/Ton
Note on J200: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on H239: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H263: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on R263: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T263: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on P265: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on P266: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on P267: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on P268: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on P269: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N305: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P305: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on N306: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P306: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on N307: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P307: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on N308: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P308: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on P322: Sandeep: Multiplier of 0.5 has been added.
Note on V354: Sandeep: Multiplier of 0.5 has been added.
Note on H394: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.
Note on P399: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on R399: Sandeep: The standard design 'Chiller Min Unloading Ratio' is determined based on the 'Chiller Type'. Screw = 15% See ACM ' Default Minimum Unloading Ratios Table-48 for further details
Note on F401: Sandeep: 'The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller, equally sized >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons.
Note on H401: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on N401: Sandeep: Chiller Type: Screw, Path B Efficiency Cap <75 Tons = 0.78 kW/Ton Cap <150 Tons = 0.75 kW/Ton Cap <300 Tons = 0.68 kW/Ton Cap >=300 Tons = 0.625 kW/Ton
Note on R409: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on P411: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L179) Impeller Efficiency: 0.7
Note on R411: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on P412: Sandeep: For condenser water pumps, Head: 45 ft
Note on R412: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on P413: Sandeep: For chilled water pumps, 40 ft plus an additional allowance of 0.03 ft/ton, but not to exceed 100 ft. (See formula in the cell above)
Note on R413: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on P414: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L180) Impeller Efficiency: 0.7
Note on R414: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower

## 030006-OffMed-Run23
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run23 |  |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 030006-OffMed-Run23.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope, Fenestration and HVAC |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Alteration | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.065 |  | 0.8 |  | 0.8 |  | 0.1 |  | 0.9
Exterior Wall | NACM_Metal Framed Wall_New | Altered | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | Exisiting | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New |  | Top Floor-South Window |  | FixedWindow |  | 0.4 |  | 0.33 |  | 0.5
Window | FixedWindow_Unaltered | Exisiting |  | All Other |  | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3081 |  | 0.33 |  | 0.33 |  | 0.33 |  | 0.22
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Metal Framed Wall | Exisiting/New |  | Stucco - 7/8 in. |  | Building Paper - 1/16 in. |  | Expanded Polystyrene - EPS - 3 in. R13 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Roof | NACM_Roof | Altered |  | Metal Standing Seam - 1/16 in. |  | Expanded Polystyrene - EPS - 3 1/2 in. R15 | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Flr / All Zone | BottomVAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Flr / All Zone | Mid VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / All Zone (Except Zone 4) | Top VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / Zone 4 | Perimeter_top_ZN_4 New AirSys | New |  | Top Floor - Zone 4 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 |  | 11.4 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 |  | 11.4 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 |  | 11.4 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perimeter_top_ZN_4 New AirSys | Perim_top_4Zn CoolingCoil | New |  | DirectExpansion |  | 13 | - | - | - | - |  | CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BottomVAV | Bottom VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | CoreBottomReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom4ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | Mid VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | CoreMidReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid4ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | Top VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | CoreTopReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Perimeter_top_ZN_4 New AirSys | Perim_top_4Zn HeatingCoil | New |  | Furnace (Natural Gas) |  | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Power adjustment curve
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
BottomVAV | BottomVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 20.45 | - | - | - | - |  | 25 |  | 0.936 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Mid VAV | MidVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 20.8 | - | - | - | - |  | 25 |  | 0.936 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Top VAV | TopVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 18.76 | - | - | - | - |  | 20 |  | 0.93 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Perimeter_top_ZN_4 New AirSys | Perim_top_4ZnSupplyFan | New |  | Constant Volume |  | BrakeHorsePower | - | - |  | 1.23 | - | - | - | - |  | 1.5 |  | 0.865 | - | -
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV | BottomVAV Economizer | Exisiting |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV | MidVAV OACtrl | Exisiting |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV | Top VAV OACtrl | Exisiting |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Perimeter_top_ZN_4 New AirSys | Perime1OAControl | New | - | - | - | - | - | - | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 |  | Exisiting |  | 600000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 29.99 |  | 0.59 (19.68 W/gpm) |  | 0.8 |  | 65.857 |  | 0.9 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresWoodFramingAndOtherRoofU049 | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.049 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU069 | Altered | - | - |  | MetalFrameWall |  | 0.069 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | Exisiting | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting |  | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3081 |  | 0.33 |  | 0.33 |  | 0.33 |  | 0.22
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU069 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R10.06 |  | Compliance Insulation R2.00 |  | Compliance Insulation R0.20 |  | Compliance Insulation R0.10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
Exterior Wall | NACM_Metal Framed Wall | Exisiting |  | Stucco - 7/8 in. |  | Building Paper - 1/16 in. |  | Expanded Polystyrene - EPS - 3 in. R13 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofU049 | Altered |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R19.63 | - | - | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  | AirSys:Type |  | AirSys:AvailSchRef |  |  |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Flr / All Zone | BottomVAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Flr / All Zone | Mid VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / All Zone (Except Zone 4) | Top VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / Zone 4 | BaseAirSys3 | New |  | Top Floor - Zone 4 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BottomVAV | Bottom VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | CoreBottomReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom4ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | Mid VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | CoreMidReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid4ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | Top VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | CoreTopReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) |  | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Power adjustment curve
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
BottomVAV | BottomVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower |  | 20109.4 |  | 20.45 | - | - | - | - |  | 25 |  | 0.936 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Mid VAV | MidVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower |  | 20454.5 |  | 20.8 | - | - | - | - |  | 25 |  | 0.936 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Top VAV | TopVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower |  | 18454.5 |  | 18.76 | - | - | - | - |  | 20 |  | 0.93 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume |  | StaticPressure |  | 1161.95 |  | 0.91449 |  | 0.5 |  | 2.5 |  | 1 |  | 0.855 | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV | BottomVAV Economizer | Existing |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV | MidVAV OACtrl | Existing |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV | Top VAV OACtrl | Existing |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
BaseAirSys3 | BaseSys3 OACtrl | New | - | - | - | - | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 |  | Exisiting |  | 600000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 29.9886 |  | 0.59 (19.68 W/gpm) |  | 0.8 |  | 65.86 |  | 0.9 | - | -
Note on B17: Sandeep: 140811: underground wall not being tested, not documented
Note on H73: Sandeep: =0.0051427*(79)+0.3989
Note on L107: Sandeep: Pump Power is revised based on the recalculated pump head. Refer note in cell P107 for more information on the recalulated pump head values.
Note on P107: Sandeep: The MotorBHP calculated for pump 'HotWater Pump' is less than the ACM required value for the user-specified MotorHP. The Proposed TotHd will be revised to 65.9 ft for compliance analysis. Based on the calculation below MinMtrBHP / FlowCap * 3960 * ImpellerEff Where, MinMtrBHP = The minimum Proposed model MtrBHP is Max(User calc MtrBHP, 95% x MHPi-1) (The minimum allowed MtrBHP used in the Proposed model simulation based on user specified MtrHP.) Flow Cap = Based on Boiler Capacity Impeller Efficiency = 0.7
Note on H146: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H173: Sandeep: =0.0051427*(79)+0.3989
Note on H176: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N176: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P181: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on R181: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T181: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on H201: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.
Note on P207: Sandeep: The MotorBHP calculated for pump 'HotWater Pump' is less than the ACM required value for the user-specified MotorHP. The Proposed TotHd will be revised to 65.9 ft for compliance analysis. Based on the calculation below MinMtrBHP / FlowCap * 3960 * ImpellerEff Where, MinMtrBHP = The minimum Proposed model MtrBHP is Max(User calc MtrBHP, 95% x MHPi-1) (The minimum allowed MtrBHP used in the Proposed model simulation based on user specified MtrHP.) Flow Cap = Based on Boiler Capacity Impeller Efficiency = 0.7

## 020006-OffSml-Run24
General Details |  |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 020006-OffSml-Run24 |  |  | Model Revision no. | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 020006-OffSml-Run24.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration and HVAC |  |  | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Alteration | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered |  | Top Floor-South Window | FixedWindow |  | 0.4 |  | 0.33 |  | 0.5
Window | FixedWindow_Unaltered | Exisiting |  | All Other | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.21 | 0.2 |  | 0.2 |  | 0.24 |  | 0.2
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Core_ZN Thermal Zone | CoreZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | Perim1ZnPSZ AirSys_New | New |  | Bottom Floor - Zone 1 | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
CoreZnPSZ AirSys | CoreZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnPSZ AirSys | Perim2ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 |  |  |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim1ZnPSZ AirSys_New | Perim1ZnCoolingCoil | New |  | DirectExpansion | 13 | - | - |  | CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
CoreZnPSZ AirSys | CoreZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim2ZnPSZ AirSys | Perim2ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim1ZnPSZ AirSys_New | Perim1ZnHeatingCoil | New |  | Furnace (Natural Gas) | 0.80414 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
CoreZnPSZ AirSys | CoreZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower | - | - |  | 1.6 | - | - | - | - | 2 | 0.865
Perim2ZnPSZ AirSys | Perim2ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower | - | - |  | 0.8 | - | - | - | - | 1 | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower | - | - |  | 1.2 | - | - | - | - | 1.5 | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower | - | - |  | 0.8 |  |  |  |  | 1 | 0.855
Perim1ZnPSZ AirSys_New | Perim1ZnSupplyFan | New |  | Constant Volume | BrakeHorsePower | - | - |  | 1.12 | - | - | - | - | 1.5 | 0.855
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
Fan:ZnServed | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_4 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered |  | FixedWindow | 0.47 |  | 0.31 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting |  | FixedWindow | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.21 | 0.2 |  | 0.2 |  | 0.24 |  | 0.2
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Core_ZN Thermal Zone | CoreZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | Exisiting |  |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | BaseAirSys3 | New |  | Bottom Floor - Zone 1 | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
CoreZnPSZ AirSys | CoreZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnPSZ AirSys | Perim2ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
CoreZnPSZ AirSys | CoreZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim2ZnPSZ AirSys | Perim2ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
CoreZnPSZ AirSys | CoreZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower |  | 1610.9 |  | 1.6 | - | - | - | - | 2 | 0.865
Perim2ZnPSZ AirSys | Perim2ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower |  | 724.411 |  | 0.8 | - | - | - | - | 1 | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower |  | 1221.17 |  | 1.2 | - | - | - | - | 1.5 | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower |  | 724.411 |  | 0.8 | - | - | - | - | 1 | 0.855
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume | StaticPressure |  | 1449.12 |  | 1.1405 |  | 0.5 |  | 2.5 | 1.5 | 0.865
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_4 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Note on H92: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on N110: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on H116: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on P116: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on R116: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T116: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.

## 020006-OffSml-Run25 (hidden)
General Details |  |  | Model/Software Details |  |  |  | Key
Test Name | 020006-OffSml-Run25 |  | Model Revision no. | Rev4376 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006-OffSml-Run25.cibd16 |  | Version of Ruleset (Trunk rev. No.) | Rev4376 |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2016.2.1 |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested | Upated 09/18/2016 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration |  | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Alteration |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Relevant Position | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC | FenConsRef:VT
Window | FixedWindow_Altered | Altered | South Window | FixedWindow | 0.4 |  | 0.33 | 0.5
Window | FixedWindow_Unaltered | Exisiting | All Other | FixedWindow | 0.55 |  | 0.56 | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered | FixedWindow | 0.47 | 0.31 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting | FixedWindow | 0.55 | 0.56 |  | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2

## 020006-OffSml-Run26 (hidden)
General Details |  |  | Model/Software Details |  |  |  | Key
Test Name | 020006-OffSml-Run26 |  | Model Revision no. | Rev4376 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006-OffSml-Run26.cibd16 |  | Version of Ruleset (Trunk rev. No.) | Rev4376 |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2016.2.1 |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested | Upated 09/18/2016 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration |  | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Alteration |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Relevant Position | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC | FenConsRef:VT
Window | FixedWindow_Altered | New | South Window | FixedWindow | 0.35 |  | 0.32 | 0.53
Window | FixedWindow_Unaltered | Exisiting | All Other | FixedWindow | 0.55 |  | 0.56 | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New | FixedWindow | 0.36 | 0.25 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting | FixedWindow | 0.55 | 0.56 |  | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.4 | 0.2 | 0.2 |  | 0.87 | 0.2
Note on H33: Sandeep: 160706_SDS: Previous Value - 19% Previously the existing windows on North, East and West façade were also resized to reduce the overa;; WWR to 40%, when the south window was of status 'NEW'. In this current version only the south window with status 'NEW' is being altered to reduce the overall WWR to 40%.
Note on J33: Sandeep: 160706_SDS: Previous Value - 19% Previously the existing windows on North, East and West façade were also resized to reduce the overa;; WWR to 40%, when the south window was of status 'NEW'. In this current version only the south window with status 'NEW' is being altered to reduce the overall WWR to 40%.
Note on L33: Sandeep: 160706_SDS: Previous Value - 89% Previously the existing windows on North, East and West façade were also resized to reduce the overa;; WWR to 40%, when the south window was of status 'NEW'. In this current version only the south window with status 'NEW' is being altered to reduce the overall WWR to 40%.
Note on N33: Sandeep: 160706_SDS: Previous Value - 19% Previously the existing windows on North, East and West façade were also resized to reduce the overa;; WWR to 40%, when the south window was of status 'NEW'. In this current version only the south window with status 'NEW' is being altered to reduce the overall WWR to 40%.

## 050006-RetlMed-Run27 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 050006-RetlMed-Run27 |  |  | Model Revision no. |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 050006-RetlMed-Run27.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration and HVAC |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Addition | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 | New |  | South Windows (All Windows) |  | FixedWindow |  | 0.35 |  | 0.32 |  | 0.53
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3716 |  | 0 |  | 0 |  | 0.4603 |  | 0
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Front_Entry | Lobby, Main Entry | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.6 |  | 0.75 |  | 2.35 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.15 | - | - |  | 1.15 |  | RetailLights |  | Area Category Method | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Bottom Floor / All Zones | SouthAddtn AirSys | New |  | All additions |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
SouthAddtn AirSys | SouthAddtn CoolingCoil | New |  | DirectExpansion |  | 11 |  | 12.7 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
SouthAddtn AirSys | SouthAddtn HeatingCoil | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
SouthAddtn AirSys | SouthAddtn SupplyFan | New |  | Constant Volume |  | BrakeHorsePower | - | - |  | 3.2 | - | - | - | - | 3 | 0.895
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
SouthAddtn AirSys | SouthAddtn OAControl | New |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 | New |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3716 |  | 0 |  | 0 |  | 0.4603 |  | 0
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Front_Entry | Lobby, Main Entry | New |  | 0.95 | - | - |  | 0.95 |  | RetailLights |  | Area Category Method | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.34 |  | 0.38422 |  | 1.72 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Bottom Floor / All Zones | BaseAirSys3 | New |  | All additions |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion |  | 10.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) |  | 0.8 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume |  | StaticPressure |  | 6028.04 |  | 4.7442 |  | 0.6 |  | 3 | 5 | 0.895
BaseAirSys3 | BaseRelief Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 5865.71 |  | 1.7312 |  | 0.4 |  | 0.75 | 2 | 0.865
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
SouthAddtn AirSys | BaseSys3 OACtrl | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Note on H89: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H99: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on R99: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T99: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on N101: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P101: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N102: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P102: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1

## 050006-RetlMed-Run28
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 050006-RetlMed-Run28 |  |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 050006-RetlMed-Run28.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope, Fenestration and HVAC |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Addition and Alteration | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | Altered metal bldg roof | Altered |  | Low |  | MetalBuildingRoof |  | 0.034 |  | 0.75 |  | 0.75 |  | 0.08 |  | 0.92
Roof | Other Altered Roof | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.021 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Low |  | WoodFramingAndOtherRoof |  | 1.282 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.039 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | Altered metal frame wall | Altered | - | - |  | MetalFrameWall |  | 0.053 | - | - | - | - | - | - | - | -
Exterior Wall | Altered metal building wall | Altered | - | - |  | MetalBuildingWall |  | 0.052 | - | - | - | - | - | - | - | -
Exterior Wall | New heavy mass wall | New | - | - |  | MassHeavyWall |  | 0.051 | - | - | - | - | - | - | - | -
Exterior Wall | Altered light mass wall | Altered | - | - |  | MassLightWall |  | 0.046 | - | - | - | - | - | - | - | -
Exterior Wall | Altered heavy mass wall | Altered | - | - |  | MassHeavyWall |  | 0.051 | - | - | - | - | - | - | - | -
Exterior Wall | Base_CZ12-NonresMetalFrameWallU062_New | New | - | - |  | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | -
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | Altered metal bldg roof | Altered |  | Metal standing seam roof, R-0 |  | Air - Cavity - Wall Roof Ceiling - 4 in. or more |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 | - | - | - | - | - | -
Roof | Other Altered Roof | Altered |  | Built-up roofing - 3/8 in. |  | Expanded Polystyrene - EPS - 6 1/10 in. R25 |  | Wood, Roof24in OC, 2x6, cav. R-19 |  | Air - Cavity - Wall Roof Ceiling - 4 in. or more |  | Acoustic Tile - 3/4 in. | - | -
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Metal Standing Seam - 1/16 in. | - | - | - | - | - | - | - | - | - | -
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039 | New |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R24.86 | - | - | - | - | - | - | - | -
Exterior Wall | Altered metal frame wall | Altered |  | Stucco - 7/8 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall | Altered metal building wall | Altered |  | Metal Siding - 1/16 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Plywood 3/4in | - | - | - | -
Exterior Wall | New heavy mass wall | New |  | Stucco - 7/8 in. |  | Concrete - 140 lb/ft3 - 6 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Exterior Wall | Altered light mass wall | Altered |  | Stucco - 7/8 in. |  | Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. |  | Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
Exterior Wall | Altered heavy mass wall | Altered |  | Stucco - 7/8 in. |  | Concrete - 140 lb/ft3 - 6 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Exterior Wall | Base_CZ12-NonresMetalFrameWallU062 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R13.99 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall (UnConditioned) | Base_CZ12-NonresMetalFrameWallU062 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R13.99 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Fenestrations
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.07 |  | 0 |  | 0 |  | 0.25 |  | 0
|  | Type |  | Skylight to Roof Ratio (Frac)
CondSRR
|  | Skylights |  | 0.02
Internal Load Components
Space
Space Name | Space Function |  |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Exisiting |  | 0.5 | - | - |  | 0.5 |  | RetailLights |  | Area Category Method | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | Exisiting |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
Front_Entry | Lobby, Main Entry | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.6 |  | 0.75 |  | 2.35 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.15 | - | - |  | 1.15 |  | RetailLights |  | Area Category Method | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor / Exisiting Zones | BaseAirSys5 | Exisiting |  | Exisiting Zones |  | PVAV |  | RetailHVACAvail |  | 60 |  | 60 |  | WarmestReset |  | 60 |  | 55
Bottom Floor / Addition Zones | SouthAddtn AirSys | Exisiting |  | All South Zones |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | Exisiting |  | DirectExpansion |  | 9.8 |  | 11.4 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
SouthAddtn AirSys | SouthAddtn CoolingCoil | Exisiting |  | DirectExpansion |  | 11 |  | 12.7 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | Exisiting |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil | Exisiting |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil-2 | Exisiting |  | HotWater | - | - | - | - | - | -
SouthAddtn AirSys | SouthAddtn HeatingCoil | Exisiting |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Bottom Floor / Exisiting Zones | BaseSys5 Fan | Exisiting |  | VariableSpeedDrive |  | Static Pressure | - | - |  | 21.67 |  | 0.62 |  | 4 |  | 25 |  | 0.936
Bottom Floor / Addition Zones | SouthAddtn SupplyFan | Exisiting |  | Constant Volume |  | BrakeHorsePower | - | - |  | 3.2 | - | - | - | - |  | 3.5 |  | 0.895
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | Exisiting |  | DifferentialDryBulb |  | Integrated
SouthAddtn AirSys |  | Exisiting |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Back_Space | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Core_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | Exisiting |  | 240681 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 12.03 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
HotWater Pump | Boiler 2 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 12.03 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresMetalBuildingRoofU041 | Altered |  | Low |  | MetalBuildingRoof |  | 0.041 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofU049 | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.049 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Low |  | WoodFramingAndOtherRoof |  | 1.282 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofU049 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.049 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU069 | Altered | - | - |  | MetalFrameWall |  | 0.069 | - | - | - | - | - | - | - | -
Exterior Wall | MetalBldgWallU113 | Altered | - | - |  | MetalBuildingWall |  | 0.113 | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU069 | New | - | - |  | MetalFrameWall |  | 0.069 | - | - | - | - | - | - | - | -
Exterior Wall | MassLightWallU440 | Altered | - | - |  | MassLightWall |  | 0.44 | - | - | - | - | - | - | - | -
Exterior Wall | MassHeavyWallU690 | Altered | - | - |  | MassHeavyWall |  | 0.69 | - | - | - | - | - | - | - | -
Exterior Wall (UnConditioned) | MetalFrameWallUnconditioned | New |  |  |  | MetalFrameWall |  | 0.971
Exterior Wall | MetalFrameWallU069 | New | - | - |  | MetalFrameWall |  | 0.069 | - | - | - | - | - | - | - | -
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | FlatNonresMetalBuildingRoofU041 | Altered |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R20.05 |  | Compliance Insulation R2.00 |  | Compliance Insulation R1.00 |  | Compliance Insulation R0.50 |  | Compliance Insulation R0.05 |  | Compliance Insulation R0.01
Roof | FlatNonresWoodFramingAndOtherRoofU049 | Altered |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R19.63 | - | - | - | - | - | - | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Metal Standing Seam - 1/16 in. | - | - | - | - | - | - | - | - | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofU049 | New |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R19.63 | - | - | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU069 | Altered |  | Stucco - 7/8 in. |  | Compliance Insulation R10.06 |  | Compliance Insulation R2.00 |  | Compliance Insulation R0.20 |  | Compliance Insulation R0.10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
Exterior Wall | MetalBldgWallU113 | Altered |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R8.00 | - | - | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU069 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R10.06 |  | Compliance Insulation R2.00 |  | Compliance Insulation R0.20 |  | Compliance Insulation R0.10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
Exterior Wall | MassLightWallU440 | Altered |  | Concrete - 140 lb/ft3 - 4 in. |  | Compliance Insulation R0.02 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Wall | MassHeavyWallU690 | Altered |  | Concrete - 140 lb/ft3 - 8 in. |  | Compliance Insulation R0.01 | - | - | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU069 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R10.06 |  | Compliance Insulation R2.00 |  | Compliance Insulation R0.20 |  | Compliance Insulation R0.10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
Exterior Wall (UnConditioned) | MetalFrameWallUnconditioned | New |  | Stucco - 7/8 in. | - | - | - | - | - | - | - | - | - | - | - | -
Fenestrations
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.07 |  | 0 |  | 0 |  | 0.25 |  | 0
|  | Type |  | Skylight to Roof Ratio (Frac)
CondSRR
|  | Skylights |  | 0.02
Internal Load Components
Space
Space Name | Space Function |  |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Exisiting |  | 0.5 | - | - |  | 0.5 |  | RetailLights |  | Area Category Method | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | Exisiting |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
Front_Entry | Lobby, Main Entry | New |  | 0.95 | - | - |  | 0.95 |  | RetailLights |  | Area Category Method | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.34 |  | 0.38422 |  | 1.7242 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor / Exisiting Zones | BaseAirSys5 | Exisiting |  | Exisiting Zones |  | PVAV |  | RetailHVACAvail |  | 60 |  | 60 |  | WarmestReset |  | 60 |  | 55
Bottom Floor / Addition Zones | SouthAddtn AirSys | Exisiting |  | All South Zones |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | Exisiting |  | DirectExpansion |  | 9.8 |  | 11.4 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
SouthAddtn AirSys | SouthAddtn CoolingCoil | Exisiting |  | DirectExpansion |  | 11 |  | 12.7 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | Existing |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil | Existing |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil-2 | Existing |  | HotWater | - | - | - | - | - | -
SouthAddtn AirSys | SouthAddtn HeatingCoil | Existing |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BaseAirSys5 | BaseSys5 Fan | Exisiting |  | VariableSpeedDrive |  | Static Pressure | - | - |  | 21.67 |  | 0.62 |  | 4 |  | 25 |  | 0.936
SouthAddtn AirSys | SouthAddtn SupplyFan | Exisiting |  | Constant Volume |  | BrakeHorsePower | - | - |  | 3.2 | - | - | - | - |  | 3.5 |  | 0.895
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | Exisiting |  | DifferentialDryBulb |  | Integrated
SouthAddtn AirSys |  | Exisiting |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Back_Space | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Core_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | Exisiting |  | 240681 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | Exisiting |  | OnDemand |  | ConstantSpeed |  | 12.03 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base HW Pump-2 | Base Blr-2 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 12.03 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Note on C126: Sandeep: 151125: 'Back_Space_Wall_West' which in the proposed design is a 'New' 'MassHeavyWall'
Note on C129: Sandeep: 151125: 'Front_Entry_Wall_South' in the proposed design is designated as 'New' MetalFrameWall' with construction similar other exterior walls ('Base_CZ12-NonresMetalFrameWallU062_New')
Note on C143: Sandeep: 151125: 'Back_Space_Wall_West' which in the proposed design is a 'New' 'MassHeavyWall'
Note on C147: Sandeep: 151125: 'Front_Entry_Wall_South' in the proposed design is designated as 'New' MetalFrameWall' with construction similar other exterior walls ('Base_CZ12-NonresMetalFrameWallU062_New')
Note on H211: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.

## 030006-OffMed-Run29 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run29 |  |  | Model Revision no. |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run29.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope and HVAC |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | New Envelope | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.065 |  | 0.78 |  | 0.78 |  | 0.75 |  | 0.25
Exterior Wall | NACM_Metal Framed Wall | New | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Exterior Floor | NACM_Conc Raised Flr | New | - | - |  | MassFloor |  | 0.039 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 |  |  | FixedWindow |  | 0.35 |  | 0.32 |  | 0.53
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | NACM_Roof | New |  | Metal Standing Seam - 1/16 in. |  | Expanded Polystyrene - EPS - 3 1/2 in. R15 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | New |  | Stucco - 7/8 in. |  | Building Paper - 1/16 in. |  | Expanded Polystyrene - EPS - 3 in. R13 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Exterior Floor | NACM_Conc Raised Flr | New |  | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 |  | Concrete - 80 lb/ft3 - 4 in. |  | Metal Deck - 1/16 in. |  | OSB - Oriented Strand Board - 5/8 in. |  | Carpet - 3/4 in. | - | -
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Spaces) | Office (Greater than 250 square feet in floor area) | Future |  | 0.75 |  | OfficeLights
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd |  | AirSys:ClRstSupHi | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power | Motor Efficiency |  | Power adjustment curve
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 14718.9 |  | 14.9649 |  | 0.62 |  | 4 |  | 15 | 0.924 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14222.9 |  | 14.4607 |  | 0.62 |  | 4 |  | 15 | 0.924 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14857 |  | 15.1054 |  | 0.62 |  | 4 |  | 20 | 0.93 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 13825.1 |  | 4.3574 |  | 0.5 |  | 1 |  | 5 | 0.895 |  | FanVSDPwrRatio_fCFMRatio
BaseAirSys5-2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13329.1 |  | 4.2011 |  | 0.5 |  | 1 |  | 5 | 0.895 |  | FanVSDPwrRatio_fCFMRatio
BaseAirSys5-3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13963.2 |  | 4.401 |  | 0.5 |  | 1 |  | 5 | 0.895 |  | FanVSDPwrRatio_fCFMRatio
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 311701 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 15.58 |  | 0.296 (19 W/gpm) |  | 0.5 |  | 60.4 | 0.855 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresWoodFramingAndOtherRoofU049 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.049 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU069 | New | - | - |  | MetalFrameWall |  | 0.069 | - | - | - | - | - | - | - | -
Exterior Floor | OtherFloorU071 | New | - | - |  | OtherFloor |  | 0.071 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 |  |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | FlatNonresWoodFramingAndOtherRoofU049 | New |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R19.63 | - | - | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU069 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R10.06 |  | Compliance Insulation R2.00 |  | Compliance Insulation R0.20 |  | Compliance Insulation R0.10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
Exterior Floor | OtherFloorU071 | New |  | Compliance Insulation R9.83 |  | Plywood - 5/8 in. |  | Carpet - 3/4 in. | - | - | - | - | - | - | - | -
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Spaces) | Office (Greater than 250 square feet in floor area) | Future |  | 0.75 |  | OfficeLights
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power | Motor Efficiency |  | Power adjustment curve
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 15267.4 |  | 15.5044 |  | 0.62 |  | 4 |  | 20 | 0.93 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14158.2 |  | 14.378 |  | 0.62 |  | 4 |  | 15 | 0.924 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14876.2 |  | 15.1071 |  | 0.62 |  | 4 |  | 20 | 0.93 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 14373.6 |  | 4.525 |  | 0.5 |  | 1 |  | 5 | 0.895 |  | FanVSDPwrRatio_fCFMRatio
BaseAirSys5-2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13264.4 |  | 4.1758 |  | 0.5 |  | 1 |  | 5 | 0.895 |  | FanVSDPwrRatio_fCFMRatio
BaseAirSys5-3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13982.4 |  | 4.4018 |  | 0.5 |  | 1 |  | 5 | 0.895 |  | FanVSDPwrRatio_fCFMRatio
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 323366 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 16.16 |  | 0.31 (19 W/gpm) |  | 0.5 |  | 60.4 | 0.855 | - | -
Note on H131: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H146: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on R146: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T146: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on N148: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P148: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N149: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P149: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N150: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on P150: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on N151: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P151: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on N152: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P152: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on N153: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P153: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on H170: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.
Note on T175: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower

## 030006-OffMed-Run30
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run30 |  |  | Model Revision no. |  | Rev4376 |  |  |  | Use cell to check if values are verified
Model File Name | 030006-OffMed-Run30.cibd16 |  |  | Version of Ruleset (Trunk rev. No.) |  | Rev4376 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2016.2.1 |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | Upated 09/18/2016 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC and Partial Lighting |  |  | Testing Performed by |  | 0 |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | New Mechanical and Partial Lighting | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function | Status |  | Installed Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor |  | Lighting Power Density (Simulated) (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF |  | Spc:IntLPDReg |  | IntLtgRegSchRef:Name
(All Levels - Core Zones) | Office (Greater than 250 square feet in floor area) | New |  | 8448 |  | 5068.8 |  | OccupantSensingControls-1to125SF |  | 0.4 |  | 0.48 |  | OfficeLights
(All Levels - South Zones - Zone 1) | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - |  | 0.8 |  | OfficeLights
(All Levels - All other Zones) | Office (Greater than 250 square feet in floor area) | Existing | - | - | - | - | - | - | - | - |  | 1.2 |  | OfficeLights
Daylighting
Space - Name | Space Function | Status |  | Primary Sidelit - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux) |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Core_bottom | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 952.362 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 952.362 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 952.362 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Bottom Floor | BottomVAV | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | Mid VAV | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | Top VAV | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | New |  | DirectExpansion |  | 13.1 |  | 15.24 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | New |  | DirectExpansion |  | 13.1 |  | 15.24 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | New |  | DirectExpansion |  | 13.1 |  | 15.24 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | 3.8394
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating | New |  | HotWater
Mid VAV | Mid VAV CoilHeating | New |  | HotWater
Top VAV | Top VAV CoilHeating | New |  | HotWater
BottomVAV | (All ReheatCoils) | New |  | HotWater
Mid VAV | (All ReheatCoils) | New |  | HotWater
Top VAV | (All ReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Power adjustment curve
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
BottomVAV | BottomVAV SupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 14.085 | - | - | - | - |  | 15 |  | 0.9 | - | -
Mid VAV | MidVAV SupplyFan | New |  | ConstantVolume |  | Static Pressure |  | 17875.9 |  | 12.9866 |  | 0.65 |  | 3 |  | 15 |  | 0.9 | - | -
Top VAV | TopVAV SupplyFan | New |  | ConstantVolume |  | Static Pressure |  | 17875.9 |  | 18.1534 |  | 0.62 |  | 4 |  | 20 |  | 0.9 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl: |  | OACtrl:
BottomVAV |  | New |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV |  | New |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV |  | New |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 | New |  |  | 700000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | New |  | 1 |  | OnDemand |  | ConstantSpeed |  | 34.9867 |  | 1.18 (33.74 W/gpm) |  | 2 |  | 112.9029 |  | 0.9 | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (Simulated) (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Levels - Core Zones) | Office (Greater than 250 square feet in floor area) | New |  | 0.75 |  | OfficeLights
(All Levels - South Zones - Zone 1) | Office (Greater than 250 square feet in floor area) | New |  | 0.75 |  | OfficeLights
(All Levels - All other Zones) | Office (Greater than 250 square feet in floor area) | Existing |  | 1.2 |  | OfficeLights
Daylighting
Space - Name | Space Function | Status |  | Primary Sidelit - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux) |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Core_bottom | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 892.84 |  | 287.5 |  | 287.5 |  | 1040.8 |  | 780.598 |  | 287.5 |  | 1150
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 892.84 |  | 287.5 |  | 287.5 |  | 1040.8 |  | 780.598 |  | 287.5 |  | 1150
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 892.84 |  | 287.5 |  | 287.5 |  | 1040.8 |  | 780.598 |  | 287.5 |  | 1150
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseSys5 CoilHtg | BaseSys5 CoilHtg | New |  | HotWater
BaseSys5 CoilHtg-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseSys5 CoilHtg-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Power adjustment curve
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 14319.8 |  | 14.5421 |  | 0.62 |  | 4 |  | 15 |  | 0.924 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14805.2 |  | 15.035 |  | 0.62 |  | 4 |  | 20 |  | 0.93 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 17504.7 |  | 17.7764 |  | 0.62 |  | 4 |  | 20 |  | 0.93 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
BaseAirSys5 | BaseRelief Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 13426 |  | 4.2267 |  | 0.5 |  | 1 |  | 5 |  | 0.895 |  | FanVSDPwrRatio_fCFMRatio
BaseAirSys5-2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13911.4 |  | 4.3795 |  | 0.5 |  | 1 |  | 5 |  | 0.895 |  | FanVSDPwrRatio_fCFMRatio
BaseAirSys5-3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 16610.9 |  | 5.2293 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917 |  | FanVSDPwrRatio_fCFMRatio
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 253774 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 12.6839 |  | 0.24 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Note on R93: Sandeep: The MotorBHP calculated for pump 'HotWater Pump' is less than the ACM required value for the user-specified MotorHP. The Proposed TotHd will be revised to112.9 ft for compliance analysis. Based on the calculation below MinMtrBHP / FlowCap * 3960 * ImpellerEff Where, MinMtrBHP = The minimum Proposed model MtrBHP is Max(User calc MtrBHP, 95% x MHPi-1) (The minimum allowed MtrBHP used in the Proposed model simulation based on user specified MtrHP.) Flow Cap = Based on Boiler Capacity Impeller Efficiency = 0.7
Note on H134: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H149: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on R149: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T149: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 29) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on N151: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on N152: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on N153: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,0000cfm = 62%
Note on N154: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P154: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on N155: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P155: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on N156: Sandeep: The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P156: Sandeep: The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on H173: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.
Note on T178: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table available in the NACM, for the next larger motor size than the calculated standard design brake horsepower