## Documentation Main Sheet (hidden)
General Details | Model/Software Details
Test Name | Model Revision no. | 4000
Model File Name | Version of Ruleset (Trunk rev. No.) | Rel (828)
Climate Zone | CBECC Software | CBECC-Com 2013-3d (828)
| Date Tested | 2016-04-14
| Testing Performed by | Sandeep Doddaballapur

## Test Status Summary
Ruleset Implementation Tests - Test Specification Status | [12 empty] | Detailed Geometry |  | Status of Example Test Files - Detailed Geometry |  | Status of Example Test Files - Simplified Geometry
Test No | Building Type | Test Name | Compliance Type | Category | Test Criteria | Notes | Streamlined Set v3 -> v3a |  | Streamlined Set v3a -> v3b |  | Streamlined Set v3b -> v3c |  | Streamlined Set v3c -> v3d |  | Example Test File Status | Example Test File Path | Example Test File Status | Example Test File Path
1 | Small Office | 020006-OffSml-Run01 | NewComplete | Exterior Envelope | Envelope and window assembly performance | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006-OffSml-Run01/020006-OffSml-Run01.cibd | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006S-OffSml-Run01/020006S-OffSml-Run01.cibd
2 | Small Office | 020006-OffSml-Run02 | NewComplete | Exterior Envelope | Envelope and window assembly performance | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020015-OffSml-Run02/020015-OffSml-Run02.cibd | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020015S-OffSml-Run02/020015S-OffSml-Run02.cibd
3 | Small Hotel | 070015-HotSml-Run03 | NewComplete | Exterior Envelope | Envelope and window assembly performance |  |  |  | X | Baseline fenestration properties changes, for 'Operable' windows. | X |  | X | Required Input: Residential Living Unit counts added at space. 'Updated model spaces with 'Occupancy Class- residential' to test different ventilation strategies - Level 1: OA via System - Level2: Four Pipe Fan Coil (FPFC) + Dedicated Outdoor Air System (DOAS) - Level 3: Natural Ventilation - Level 4: Four Pipe Fan Coil (FPFC) + Zone Exhaust system (exhaust driven ventilation) | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/070015-HotSml-Run03/070015-HotSml-Run03.cibd | Status: Test Not Performed Date: Version:
4 | Medium Office | 030006-OffMed-Run04 | NewComplete | Exterior Envelope | Envelope minimum requirements | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006-OffMed-Run04/030006-OffMed-Run04.cibd | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006S-OffMed-Run04/030006S-OffMed-Run04.cibd
5 | Large Office | 040006-OffLrg-Run05 | NewComplete | Fenestration | Window Wall Ratio (WWR) | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/040006-OffLrg-Run05/040006-OffLrg-Run05.cibd | Status: Test Not Performed Date: Version:
6 | Large Office | 040006-OffLrg-Run06 | NewComplete | Fenestration | Window Wall Ratio (WWR) | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/040006-OffLrg-Run06/040006-OffLrg-Run06.cibd | Status: Test Not Performed Date: Version:
7 | Warehouse | 080006-Whse-Run07 | NewComplete | Skylight | Skylight to Roof Ratio (SRR) and Skylight Performance | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/080006-Whse-Run07/080006-Whse-Run07.cibd | Status: Test Not Performed Date: Version:
8 | Warehouse | 080006-Whse-Run08 | NewComplete | Skylight | Skylight to Roof Ratio (SRR) and Daylit Area | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | [8 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/080006-Whse-Run08/080006-Whse-Run08.cibd | Status: Test Not Performed Date: Version:
9 | Warehouse |  |  | Skylight | SRR and Daylit Area | Adding/Enlarging Skylights to meet 140.3C daylit area requirements currently not supported | [8 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
10 | Medium Office |  |  | Space Function | Internal Loads- Complete Bldg method | Complete Building test method currently not supported | [8 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
11 | Large Office | 040006-OffLrg-Run11 | NewComplete | Space Function | Internal loads - Space-by-Space |  |  |  | X | - Occupancy density for 'Lobby, Main Entry' changed - Ventilation rates at the thermal zones have changed. Model Updates: - Core_hi: - VentPerPerson and VentPerArea set to '0' - VentPerSpc set tp 4415 - Perimeter_hi_ZN_2: - CondgType changed to 'IndirectlyConditioned' - Perimeter_hi_ZN_2 Thermal Zone: - Type changed to 'Unconditioned' - VentSrc set to 'None' - VentSpecMthd set to 'NoVentilation' - Core_hi Thermal Zone: - VentSpecMthd set to 'Sum' | X | - Change in the precision of the OccDens to help ensure the ventilation rate calculations done in CBECC, based on people/1000ft2, are consistent with those calculated using ft2/person. | X | Rules governing ccupancy density and ventilation calculations have been updated. | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/040006-OffLrg-Run11/040006-OffLrg-Run11.cibd | Status: Test Not Performed Date: Version:
12 | Medium Office | 030006-OffMed-Run12 | NewComplete | Lighting | Lighting - tailored lighting method | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006-OffMed-Run12/030006-OffMed-Run12.cibd | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006S-OffMed-Run12/030006S-OffMed-Run12.cibd
13 | Medium Office | 030006-OffMed-Run13 | NewComplete | Lighting | Lighting - tailored lighting method | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006-OffMed-Run13/030006-OffMed-Run13.cibd | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006S-OffMed-Run13/030006S-OffMed-Run13.cibd
14 | Small Office | 020006-OffSml-Run14 | NewComplete | Lighting | Lighting - Power Adjustment Factors (PAF) rules |  |  |  |  | Interior Lighting system: SchRef is no longer a required user input. Appendix 3c has been updated |  |  |  |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006-OffSml-Run14/020006-OffSml-Run14.cibd | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006S-OffSml-Run14/020006S-OffSml-Run14.cibd
15 | Warehouse | 080006-Whse-Run15 | NewComplete | Lighting Control | Daylighting | Exclude Test for Simplified Geometry: Only daylighting parameters are tested. | [8 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/080006-Whse-Run15/080006-Whse-Run15.cibd | Status: Date: Version: | Test Excluded for Simplified geometry
16 | Medium Retail | 050006-RetlMed-Run16 | NewComplete | Lighting Control | Lighting and daylighting | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters |  |  |  | Front_Retail Space 'Controlled General Lighting Power' is corrected to represent the installed watts and not the simulated Watts. |  |  |  |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/050006-RetlMed-Run16/050006-RetlMed-Run16.cibd | Status: Test Not Performed Date: Version:
17 | Large Office |  |  | Ext.Lighting/SHW | Ext. Lighting/SHW | Prescriptive Exterior Lighting Compliance not supported | [8 empty] | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
18 | Small Office | 020006-OffSml-Run18 | NewComplete | HVAC | HVAC - SZAC |  |  |  | X | - Core Zone: SZAC: Design supply air temperature changed. - Baseline fan capacities changed. | X |  | X |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006-OffSml-Run18/020006-OffSml-Run18.cibd | Status: Verified Date: Version: | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006S-OffSml-Run18/020006S-OffSml-Run18.cibd
19 | Medium Office | 030006-OffMed-Run19 | NewComplete | HVAC | HVAC - PVAV and CRAC |  | X | - Revised baseline IntWall/IntFlr construction - Revised baseline ThrmlZn: ClgDsgnSupAirTemp for interior 'Data' zones from 65 to 60 (Rules) | X | - All peripheral spaces 'SpaceType' changed from 'Lobby, Main Entry' to 'Office (250ft2 or greater) - Core Zone - Computer Rooms Heating Design Suppy Air Temperature: No Longer specified, SZAC system in the zone provides NO HEATING - User input EPD of 18W/ft2 for Core Space: Computer Room, less than the minimum for that space type, Proposed and Baselibe get updated to 20W/ft2 - Baseline DXEIR_fFlowCrvRef changed - Baseline fan capacities and other properties changed | X |  | X |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006-OffMed-Run19/030006-OffMed-Run19.cibd | Status: Test Not Performed Date: Version:
20 | Large Office | 040006-OffLrg-Run20 | NewComplete | HVAC | HVAC - VAV and CRAH |  | X | - Revised baseline IntWall/IntFlr construction - Revised baseline ThrmlZn: ClgDsgnSupAirTemp for interior 'Data' zones from 65 to 60 (Rules) | X | Basement Floor 'Design Suppy Air Temperature (Heating)' is not a valid input as the 'BsmntZnPSZ AirSys' is cooling only. | X |  | X |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/040006-OffLrg-Run20/040006-OffLrg-Run20.cibd | Status: Test Not Performed Date: Version:
21 | Warehouse | 080006-Whse-Run21 | NewComplete | HVAC | HVAC - SZAC and HV | [8 empty] | Warehouse spaces (Fine and Bulk Storage Spaces) the HVAC systems changed to a Heating/Ventilation (HV) system. | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/080006-Whse-Run21/080006-Whse-Run21.cibd | Status: Test Not Performed Date: Version:
22 | Hotel | 070015-HotSml-Run22 | NewComplete | HVAC | HVAC - PVAV, SZAC and FPFC |  | X | - Revised baseline IntWall/IntFlr construction - Baseline Kitchen Exhaust Fan: 'ExhOperMode' changed from 'CoupledTo System' to 'DecoupledFromSystem' - Baseline: Fan efficiencies and sizing changed | X | Design Suppy Air Temperature of he 'KitchenMUA' system has changed from 60 to 55. (proposed model) | X | - Additional HVAC system added to the proposed model to to evaluate the single-phase vs. three-phase rules. | X | - Level 4: All spaces with 'Occupancy Class- residential' changed from space function 'Hotel/Motel Guest Room' to 'High-Rise Residential Living Spaces'. Occupancy has been 'User Input' to 1 person per unit. - Required Input: High-rise residential living unit counts added at the duilding data. - Required Input: Residential living unit and counts added at space. Water-source economizers added in the 'User Model'. | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/070015-HotSml-Run22/070015-HotSml-Run22.cibd | Status: Test Not Performed Date: Version:
23 | Medium Office | 030006-OffMed-Run23 | ExistingAlteration | Existing Alteration | Window alteration and HVAC replacement |  | X | - Revised baseline IntWall/IntFlr construction - Design Suppy Air Temperature (Cooling) changed from 55 to 60 for office space with no vertical fenestration | X | - SZAC: Design supply air temperature changed. - Baseline fan capacities and other properties changed | X |  | X |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006-OffMed-Run23/030006-OffMed-Run23.cibd | Status: Test Not Performed Date: Version:
24 | Small Office | 020006-OffSml-Run24 | ExistingAlteration | Existing Alteration | Window alteration and HVAC replacement |  | X | - Revised baseline IntWall/IntFlr construction - Design Suppy Air Temperature (Cooling) changed from 55 to 60 for office spaces in the core zones. - Baseline: Fan BHP and capacities changed | X | - Core Zone: SZAC: Design supply air temperature changed. - Baseline fan capacities and other properties changed | X |  | X |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006-OffSml-Run24/020006-OffSml-Run24.cibd | Status: Test Not Performed Date: Version:
25 | Small Office | 020006-OffSml-Run25 | ExistingAlteration | Existing Alteration | Window alteration | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006-OffSml-Run25/020006-OffSml-Run25.cibd | Status: Test Not Performed Date: Version:
26 | Small Office | 020006-OffSml-Run26 | ExistingAlteration | Existing Alteration | Window alteration | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/020006-OffSml-Run26/020006-OffSml-Run26.cibd | Status: Test Not Performed Date: Version:
27 | Retail Medium | 050006-RetlMed-Run27 | ExistingAddition | Existing Addition | Addition modeled alone: Envelope performance, window assembly performance and HVAC - SZAC | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/050006-RetlMed-Run27/050006-RetlMed-Run27.cibd | Status: Test Not Performed Date: Version:
28 | Retail Medium | 050006-RetlMed-Run28 | ExistingAdditionAndAlteration | Existing Addition and Alteration | Addition modeled with an altered existing building: Envelope performance, Window Wall Ratio (WWR) and HVAC - SZAC |  | X | -Revised baseline IntWall/IntFlr construction - ClgDsgnSupAirTemp raised from 55-60degF for zones with no vertical fenestrations | X | Rule modification for Existing/Alterations for altered lighting. Altered LPD in Front_Entry is < 85% of Baseline Lighting Power Allowance. Baseline LPD is set equal to proposed. | X | - Test fails because the status of envelope components are being wrongly changed from 'New' to 'Altered' by the ruleset. - Demand Responsive controls in the Front_Retail space was removed. - The installed lighting power in the Front_Retail space was reduced to ensure the lighting power density in the space remains at 2.35 W/ft2. | X |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/050006-RetlMed-Run28/050006-RetlMed-Run28.cibd | Status: Test Not Performed Date: Version:
29 | Medium Office | 030006-OffMed-Run29 | NewEnvelope | New Envelope | Envelope and correct assignment of proposed HVAC systems. | [9 empty] | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006-OffMed-Run29/030006-OffMed-Run29.cibd | Status: Test Not Performed Date: Version:
30 | Medium Office | 030006-OffMed-Run30 | NewMechanicalAndPartialLighting | New Mechanical and Partial Lighting | New/exisiting lighting and HVAC - PVAV | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | X | - Revised baseline IntWall/IntFlr construction - Fan capacity, BHP, nameplate HP and efficiency changed. - Revised baseline roof construction | X | Economizer Lockout tempertaure setpoints are being evaluated. | X |  | X |  | Status: Verified Date: 04/14/2016 Version: Rel (828) | svn.code.sf.net/p/cbecc-com/code/trunk/CBECC-Com13/Projects/RulesetImplementationTests/030006-OffMed-Run30/030006-OffMed-Run30.cibd | Status: Test Not Performed Date: Version:

## 020006-OffSml-Run01 (hidden)
General Details |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 020006-OffSml-Run01 |  | Model Revision no. | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006-OffSml-Run01.cibd |  | Version of Ruleset (Trunk rev. No.) | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [5 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof |  | Steep | WoodFramingAndOtherRoof |  | 0.044 |  | 0.78 |  | 0.78 |  | 0.75 |  | 0.25
Exterior Wall | NACM_Wood Framed Wall | - | - | WoodFramingAndOtherWall |  | 0.091 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Conc Raised FLr | - | - | MassFloor |  | 0.039 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit | - | - | OtherFloor |  | 0.07 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow |  | FixedWindow | 0.25 |  | 0.2 |  | 0.45
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Wood Framed Wall |  | Stucco - 7/8 in. | Building Paper - 1/16 in. |  | Wood framed wall, 16in. OC, 4.0in., R-15 |  | Gypsum Board - 1/2 in. | - | - | - | -
Roof | NACM_Roof |  | Asphalt roll roofing - 1/4 in. | Hardboard - HDF - 50 lb/ft3 - 3/4 in. |  | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit |  | Plywood - 3/4 in. | Wood framed floor, 16in. OC, 4.0in., R-15 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Conc Raised FLr |  | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | Concrete - 80 lb/ft3 - 4 in. |  | Metal Deck - 1/16 in. |  | OSB - Oriented Strand Board - 5/8 in. |  | Carpet - 3/4 in. | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | SteepNonresWoodFramingAndOtherRoofU075 |  | Steep | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.2 |  | 0.8
Exterior Wall | MetalFrameWallU098 | - | - | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU071 | - | - | OtherFloor |  | 0.071 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow |  | FixedWindow | 0.36 |  | 0.25 |  | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  | CodeItem | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU098 |  | Stucco - 7/8 in. | Compliance Insulation R8.07 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Roof | SteepNonresWoodFramingAndOtherRoofU075 |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R12.55 | - | - | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU071 |  | Compliance Insulation R9.83 | Plywood - 5/8 in. |  | Carpet - 3/4 in. | - | - | - | - | - | - | - | -
Note on H40: Sandeep: Values currenlty not being reported at the construction

## 020015-OffSml-Run02 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020015-OffSml-Run02 |  | Model Revision no. |  | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020015-OffSml-Run02.cibd |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-15 |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.) |  | On/Below Grade Floor F-factor (Btu/h-°F-ft2) |  | Total Perimeter Area (ft2) |  | Total Perimeter exposed (ft)
| ConsAssmRef:Name |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs |  | ConsAssmRef:FFactor |  | UndgrFlr:Area |  | UndgrFlr:PerimExposed
Roof | NACM_Roof |  | Steep |  | WoodFramingAndOtherRoof |  | 0.053 |  | 0.7 |  | 0.7 |  | 0.6 |  | 0.4 | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | - | - |  | MetalFrameWall |  | 0.056 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit | - | - |  | OtherFloor |  | 0.07 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
On/Below Grade Floor | NACM_Slab Floor | - | - | - | NA (Slab -on grade) | - | - | - | - | - | - | - | - | - | - |  | 0.7 |  | 3891.16 |  | 302.82
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow |  | FixedWindow |  | 0.25 |  | 0.2 |  | 0.45
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Metal Framed Wall |  | Stucco - 7/8 in. |  | Building Paper - 1/16 in. |  | Expanded Polystyrene - EPS - 3 in. R13 |  | Metal framed wall, 16in. OC, 5.5in., R-19 |  | Gypsum Board - 1/2 in. | - | -
Roof | NACM_Roof |  | Asphalt roll roofing - 1/4 in. |  | Hardboard - HDF - 50 lb/ft3 - 3/4 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit |  | Plywood - 3/4 in. |  | Wood framed floor, 16in. OC, 4.0in., R-15 | - | - | - | - | - | - | - | -
Shading Objects
(ExtShdgObj)
Shading Objects on Windows
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.) |  | On/Below Grade Floor F-factor (Btu/h-°F-ft2) |  | Total Perimeter Area (ft2) |  | Total Perimeter exposed (ft)
| ConsAssmRef:Name |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs |  | ConsAssmRef:FFactor |  | UndgrFlr:Area |  | UndgrFlr:PerimExposed
Roof | SteepNonresWoodFramingAndOtherRoofU039 |  | Steep |  | WoodFramingAndOtherRoof |  | 0.039 |  | 0.85 |  | 0.85 |  | 0.2 |  | 0.8 | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU062 | - | - |  | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU039 | - | - |  | OtherFloor |  | 0.039 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
On/Below Grade Floor | SlabOnOrBelowGradeF073 | - | - | - | NA (Slab -on grade) | - | - | - | - | - | - | - | - | - | - |  | 0.73 |  | 3891.16 |  | 302.82
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU062 |  | Stucco 7/8 in. |  | Compliance Insulation R13.99 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Roof | SteepNonresWoodFramingAndOtherRoofU039 |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R24.86 | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU039 |  | Compliance Insulation R21.39 |  | Plywood - 5/8 in. |  | Carpet - 3/4 in. | - | - | - | - | - | -
Shading Objects
(ExtShdgObj)
NO - Shading Objects on Windows
Note on H43: Sandeep: Values currenlty not being reported at the construction

## 070015-HotSml-Run03
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 070015-HotSml-Run03 |  |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 070015-HotSml-Run03.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-15 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Hotel |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof |  |  | Low |  | WoodFramingAndOtherRoof |  | 0.055 |  | 0.7 |  | 0.7 |  | 0.6 |  | 0.4
Exterior Wall | NACM_Mtl Framed Wall |  | - | - |  | MetalFrameWall |  | 0.082 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Ext.Conc Raised FLr |  | - | - |  | MassFloor |  | 0.058 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
| Window Non-res Fixed |  |  | FixedWindow |  | 0.25 |  | 0.2 |  | 0.47
| Window Res Operable |  |  | OperableWindow |  | 0.42 |  | 0.18 |  | 0.35
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | NACM_Roof | New |  | Metal Standing Seam - 1/16 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Wall | NACM_Mtl Framed Wall | New |  | Stucco - 7/8 in. |  | Expanded Polystyrene - EPS - 2 7/16 in. R10 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 3/8 in. | - | - | - | -
Above-grade Floor | NACM_Ext.Conc Raised FLr | New |  | Metal Deck - 1/16 in. |  | Concrete - 80 lb/ft3 - 4 in. |  | Expanded Polystyrene - EPS - 1 7/8 in. R8.0 |  | Expanded Polyurethane - 3/4 in. R4.7 |  | Carpet - 3/4 in. | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low) |  | Fixed Temperature
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
None | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55 | - | -
None | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55 | - | -
None | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55 | - | -
None | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55 | - | -
GuestRoom202_205 Thermal Zone | 2nd Floor DOAS | New |  | Guest Rooms: Floor 2 |  | SZAC |  | ResidentialLivingHVACAvail |  | 72 |  | 62 |  | FixedDualSetpoint | - | - | - | - |  | 72
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl
Residential Units: Levels 1-3 | Residential Units: FPFC (All) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
Residential Units: Level 4 | Residential Units: Zonal Exhaust Systems | New |  | Residential Units: Floor 4 |  | Exhaust |  | ResidentialLivingHVACAvail | - | - | - | - |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | DirectExpansion |  | 9.8 |  | 9.9 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | DirectExpansion |  | 11 |  | 11.2 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Residential Units: FPFC (All) | Residential Units: FPFC CoilClg (All) | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
2nd Floor DOAS | DOAS CoilClg | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
Residential Units: FPFC (All) | Residential Units: FPFC CoilHtg (All) | New |  | HotWater | - | - | - | - | - | -
2nd Floor DOAS | DOAS CoilHtg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 14146.3 |  | 14.3828 |  | 0.62 |  | 4 |  | 15 |  | 0.924
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1646.78 |  | 1.5571 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1674.51 |  | 1.5833 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1721.44 |  | 1.6277 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Residential Units: Floor1 | GuestRoom101_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom102_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom103_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom104_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom105_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom201_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom202_205_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom206_208_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom209_212_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom213_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom214_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom215_218_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom219_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom220_223_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom224_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom301_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom302_305_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom306_308_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom309_312_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom313_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom314_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom315_318_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom319_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom320_323_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom324_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom401_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom402_405_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom406_408_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom409_412_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom413_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom414_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom415_418_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom419_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom420_423_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom424_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom401-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 50 |  | 0.033255 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom402_405-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom406_408-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom409_412-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom413-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom414-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom415_418-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom419-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom420_423-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor4 | GuestRoom424-Exh Fan | New |  | ConstantVolume |  | StaticPressure |  | 30 |  | 0.019953 |  | 0.5 |  | 2.1102 |  | 0.083 |  | 0.855
Residential Units: Floor2 | DOAS SupFan | New |  | ConstantVolume |  | StaticPressure |  | 720 |  | 0.56733 |  | 0.5 |  | 2.5 |  | 0.75 |  | 0.855
AirSystem - Name | OA - Control Name | Status |  | Economizer Control |  | Economizer Integration
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
2nd Floor DOAS | DOAS OACtrl | New |  | NoEconomizer |  | Undefined
Ventilation and Thermostat schedules
Thermal Zone - Name | Conditioning Type | Status |  | Space Floor Area (ft2) |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  |  |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
CorridorFlr1 Thermal Zone | Conditioned | New |  | 1620 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 8.1 |  | 0 |  | 0.15 |  | 243 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr2 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr3 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr4 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.75 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
EmployeeLoungeFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
ExerciseCenterFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontLoungeFlr1 Thermal Zone | Conditioned | New |  | 1755.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 125.4 |  | 15 |  | 0.15 |  | 1881 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontOfficeFlr1 Thermal Zone | Conditioned | New |  | 1404 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 7.02 |  | 0 |  | 0.15 |  | 211 |  | OfficeClgSetpt |  | OfficeHtgSetpt
LaundryRoomFlr1 Thermal Zone | Conditioned | New |  | 1053 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 5.27 |  | 0 |  | 0.15 |  | 158 |  | OfficeClgSetpt |  | OfficeHtgSetpt
MechanicalRoomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 3 |  | 0.53 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
MeetingRoomFlr1 Thermal Zone | Conditioned | New |  | 864.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 61.74 |  | 15 |  | 0.15 |  | 926 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr1 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr2 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr3 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr4 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr1 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr2 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr3 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr4 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.68 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.08 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RestroomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.76 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
Space Name | Conditioning Type | Status |  | Space Function |  | Thermal Zone - Name |  | Space Floor Area (ft2) |  | Number of Residential Living or Hotel/Motel units in a modeled space |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerArea (cfm/ft2) |  | Simulated VentPerArea (cfm/ft2) |  | Infiltration Method |  | Required Ventilation - Simulated as Infiltration (cfm) |  | Infiltration Schedule |  | Exhaust Flow (cfm) |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
Spc:Name | ThrmlZn:Type |  |  | SpcFunc |  | ThrmlZn:Name |  |  |  | Spc:ResLivingUnitCnt |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerAreaSim |  | ThrmlZn:VentPerAreaSim |  | (InfMthd index="1") |  | (DsgnInfRt index="1") |  | (InfSchRef index="1") |  | ThrmlZn:VentPerAreaSim |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
GuestRoom101 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom101 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom102 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom102 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom103 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom103 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom104 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom104 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom105 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom105 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom201 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom201 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom202_205 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom202_205 Thermal Zone | X | 1404.1 | X | 4 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 3.5 | X | 0.085464 | X | 120 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom206_208 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom206_208 Thermal Zone | X | 1134.1 | X | 3 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 2.8 | X | 0.079358 | X | 90 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom209_212 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom209_212 Thermal Zone | X | 1404.1 | X | 4 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 3.5 | X | 0.085464 | X | 120 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom213 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom213 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom214 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom214 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom215_218 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom215_218 Thermal Zone | X | 1404 | X | 4 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 3.5 | X | 0.08547 | X | 120 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom219 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom219 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom220_223 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom220_223 Thermal Zone | X | 1404 | X | 4 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 3.5 | X | 0.08547 | X | 120 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom224 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom224 Thermal Zone | X | 351 | X | 1 | X | Forced | X | Maximum | X | Fixed | X | 5 | X | 0.9 | X | 0.08547 | X | 30 | - | - | - | - | - | - | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom301 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom301 Thermal Zone | X | 351 | X | 1 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 0.9 | - | - | - | - | X | FlowSpace | X | 30 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom302_305 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom302_305 Thermal Zone | X | 1404.1 | X | 4 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 3.5 | - | - | - | - | X | FlowSpace | X | 120 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom306_308 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom306_308 Thermal Zone | X | 1134.1 | X | 3 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 2.8 | - | - | - | - | X | FlowSpace | X | 90 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom309_312 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom309_312 Thermal Zone | X | 1404.1 | X | 4 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 3.5 | - | - | - | - | X | FlowSpace | X | 120 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom313 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom313 Thermal Zone | X | 351 | X | 1 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 0.9 | - | - | - | - | X | FlowSpace | X | 30 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom314 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom314 Thermal Zone | X | 351 | X | 1 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 0.9 | - | - | - | - | X | FlowSpace | X | 30 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom315_318 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom315_318 Thermal Zone | X | 1404 | X | 4 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 3.5 | - | - | - | - | X | FlowSpace | X | 120 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom319 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom319 Thermal Zone | X | 351 | X | 1 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 0.9 | - | - | - | - | X | FlowSpace | X | 30 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom320_323 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom320_323 Thermal Zone | X | 1404 | X | 4 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 3.5 | - | - | - | - | X | FlowSpace | X | 120 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom324 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom324 Thermal Zone | X | 351 | X | 1 | X | Natural | X | Maximum | X | UNDEFINED | X | 5 | X | 0.9 | - | - | - | - | X | FlowSpace | X | 30 | X | On | - | - | X | ResidentialLivingClgSetpt | X | ResidentialLivingHtgSetpt
GuestRoom401 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom401 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 | - | - | - | - |  | FlowSpace |  | 50 |  | On |  | 50 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom402_405 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom402_405 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 | - | - | - | - |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom406_408 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom406_408 Thermal Zone |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.8 | - | - | - | - |  | FlowSpace |  | 90 |  | On |  | 90 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom409_412 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom409_412 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 | - | - | - | - |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom413 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom413 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 | - | - | - | - |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom414 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom414 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 | - | - | - | - |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom415_418 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom415_418 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 | - | - | - | - |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom419 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom419 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 | - | - | - | - |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom420_423 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom420_423 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 | - | - | - | - |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom424 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom424 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 | - | - | - | - |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 363000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Electric |  | Fluid |  | 348000 |  | 4.4 (0.8 kW/ton, 15 EER) |  | 0.6 |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 18.14 |  | 0.34 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 18.14 |  | 0.34 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 85.4 |  | 1.2 (14 W/gpm) |  | 1.5 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 34.79 |  | 0.45 (12.9 W/gpm) |  | 0.75 |  | 40.87 |  | 0.855 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 427163 |  | 85.4 |  | 1.42 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Non-Residential Roof | FlatNonresWoodFramingAndOtherRoofU039 |  |  | Low |  | WoodFramingAndOtherRoof |  | 0.039 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Residential Roof | FlatResWoodFramingAndOtherRoofU028 |  |  | Low |  | WoodFramingAndOtherRoof |  | 0.028 |  | 0.85 |  | 0.85 |  | 0.55 |  | 0.45
NonResidential - Exterior Wall | MetalFrameWallU062 |  | - | - |  | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | -
Residential - Exterior Wall | MetalFrameWallU105 |  | - | - |  | MetalFrameWall |  | 0.105 | - | - | - | - | - | - | - | -
Residential and NonResidential - Above-grade Floor | OtherFloorU039 |  | - | - |  | OtherFloor |  | 0.039 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
| Window Non-res Fixed/Window Res Operable |  |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
| Window Non-res Fixed/Window Res Operable |  |  | OperableWindow |  | 0.46 |  | 0.22 |  | 0.32
Constructions/Layers
Opaque
Type | Construction Assembly Name |  |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
NonResidential - Exterior Wall | MetalFrameWallU062 |  |  | Stucco 7/8 in. |  | Compliance Insulation R13.99 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Residential - Exterior Wall | MetalFrameWallU105 |  |  | Stucco 7/8 in. |  | Compliance Insulation R7.39 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
NonResidential - Roof | FlatNonresWoodFramingAndOtherRoofU039 |  |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R24.86 | - | - | - | - | - | - | - | - | - | -
Residential - Roof | FlatResWoodFramingAndOtherRoofU028 |  |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R34.93 | - | - | - | - | - | - | - | - | - | -
Residential and NonResidential - Above-grade Floor | OtherFloorU039 |  |  | Compliance Insulation R21.39 |  | Plywood - 5/8 in. |  | Carpet - 3/4 in. | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Common Areas: Floor 1 | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 2 | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 3 | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 4 | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl
Residential Units: All Floors | Residential Units: FPFC (All) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 11 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys2 | Residential Units: BaseSys2 CoilClg (All) | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys2 | Residential Units: BaseSys2 CoilHtg (All) | New |  | HotWater | - | - |  | 1.25 | - | -
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 9760.13 |  | 8.9723 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | -
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1491.64 |  | 1.4104 |  | 0.5 |  | 3 |  | 1.5 |  | 0.865 | - | -
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1493.53 |  | 1.4122 |  | 0.5 |  | 3 |  | 1.5 |  | 0.865 | - | -
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1740.02 |  | 1.6453 |  | 0.5 |  | 3 |  | 2 |  | 0.865 | - | -
Residential Units: All Floors | BaseSys2 Fan | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 183.22 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-2 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 185.8 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-3 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 179.55 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-4 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 171.72 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-5 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 172.3 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-6 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 223.56 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-7 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 163.563 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-8 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 164.59 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-9 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 151.438 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-10 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 152.12 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-11 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 145.41 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-12 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 142.48 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-13 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 144.93 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-14 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 141.747 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-15 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 143.78 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-16 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 212.53 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-17 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 153.59 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-18 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 163.76 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-19 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 151.432 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-20 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 152.19 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-21 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 145.91 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-22 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 144.952 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-23 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 144.19 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-24 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 143.55 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-25 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 142.68 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-26 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 245.6 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-27 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 180.42 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-28 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 197.393 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-29 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 179.443 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-30 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 179.65 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-31 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 170.81 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-32 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 169.31 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-33 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 169 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-34 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 167.445 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-35 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 166.99 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Common Areas: Floor 1 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 9315.96 |  | 2.7527 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | -
Common Areas: Floor 2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1384.99 |  | 0.40924 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
Common Areas: Floor 3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1386.87 |  | 0.4098 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
Common Areas: Floor 4 | BaseRelief Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1633.36 |  | 0.48263 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys2 | - | New | - | - | - | -
Ventilation and Thermostat Schedules
Thermal Zone - Name | Conditioning Type | Status |  | Space Floor Area (ft2) |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  |  |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
CorridorFlr1 Thermal Zone | Conditioned | New |  | 1620 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 8.1 |  | 0 |  | 0.15 |  | 243 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr2 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr3 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
CorridorFlr4 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 |  | OfficeClgSetpt |  | OfficeHtgSetpt
EmployeeLoungeFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
ExerciseCenterFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontLoungeFlr1 Thermal Zone | Conditioned | New |  | 1755.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 125.4 |  | 15 |  | 0.15 |  | 1881 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontOfficeFlr1 Thermal Zone | Conditioned | New |  | 1404 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 7 |  | 0 |  | 0.15 |  | 211 |  | OfficeClgSetpt |  | OfficeHtgSetpt
LaundryRoomFlr1 Thermal Zone | Conditioned | New |  | 1053 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 5.3 |  | 0 |  | 0.15 |  | 158 |  | OfficeClgSetpt |  | OfficeHtgSetpt
MechanicalRoomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 3 |  | 0.5 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
MeetingRoomFlr1 Thermal Zone | Conditioned | New |  | 864.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 61.7 |  | 15 |  | 0.15 |  | 926 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr1 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr2 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr3 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStairsFlr4 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr1 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr2 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr3 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
FrontStorageFlr4 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStairsFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RearStorageFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 |  | OfficeClgSetpt |  | OfficeHtgSetpt
RestroomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 |  | OfficeClgSetpt |  | OfficeHtgSetpt
Space Name | Conditioning Type | Status |  | Space Function |  | Thermal Zone - Name |  | Space Floor Area (ft2) |  | Number of Residential Living or Hotel/Motel units in a modeled space |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Infiltration Method |  | Required Ventilation - Simulated as Infiltration (cfm) |  | Infiltration Schedule |  | Exhaust Flow (cfm) |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
Spc:Name | ThrmlZn:Type |  |  | Spc:SpcFunc |  | ThrmlZn:Name |  |  |  | Spc:ResLivingUnitCnt |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | (InfMthd index="1") |  | (DsgnInfRt index="1") |  | (InfSchRef index="1") |  | ThrmlZn:VentPerAreaSim |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
GuestRoom101 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom101 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom102 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom102 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom103 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom103 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom104 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom104 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom105 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom105 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom201 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom201 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom202_205 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom202_205 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom206_208 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom206_208 Thermal Zone |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.8 |  | FlowSpace |  | 90 |  | On |  | 90 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom209_212 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom209_212 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom213 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom213 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom214 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom214 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom215_218 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom215_218 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom219 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom219 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom220_223 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom220_223 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom224 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom224 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom301 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom301 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom302_305 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom302_305 Thermal Zone |  | 1404.1 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom306_308 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom306_308 Thermal Zone |  | 1134.1 |  | 3 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 2.8 |  | FlowSpace |  | 90 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom309_312 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom309_312 Thermal Zone |  | 1404.1 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom313 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom313 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom314 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom314 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom315_318 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom315_318 Thermal Zone |  | 1404 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom319 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom319 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom320_323 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom320_323 Thermal Zone |  | 1404 |  | 4 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom324 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom324 Thermal Zone |  | 351 |  | 1 |  | Natural |  | Maximum |  | UNDEFINED |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On | - | - |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom401 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom401 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom402_405 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom402_405 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom406_408 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom406_408 Thermal Zone |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.8 |  | FlowSpace |  | 90 |  | On |  | 90 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom409_412 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom409_412 Thermal Zone |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom413 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom413 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom414 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom414 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom415_418 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom415_418 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom419 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom419 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom420_423 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom420_423 Thermal Zone |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.5 |  | FlowSpace |  | 120 |  | On |  | 120 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
GuestRoom424 | Conditioned | New |  | Hotel/Motel Guest Room |  | GuestRoom424 Thermal Zone |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.9 |  | FlowSpace |  | 30 |  | On |  | 30 |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 264496 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Electric |  | Fluid |  | 318840 |  | 4.4 (0.8 kW/ton, 15 EER) | - | - |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 13.22 |  | 0.25 (19 W/gpm) |  | 0.28803 |  | 60.4 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 78.24 |  | 1.09 (14 W/gpm) |  | 1.2702 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 31.87 |  | 0.41 (12.8 W/gpm) |  | 0.46908 |  | 40.7971 |  | 0.855 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 13.22 |  | 0.25 (19 W/gpm) |  | 0.28803 |  | 60.4 |  | 0.855 | - | -
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 391370 |  | 78.24 |  | 1.304 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Note on AB172: Sandeep: CHECK *.*ap.xml
Note on AD172: Sandeep: CHECK *.*ap.xml
Note on AF172: Sandeep: CHECK *.*ap.xml
Note on AD198: Sandeep: 151123: Exhaust flow rate increased to be more than the required ventilation rate.
Note on AH198: Sandeep: 151123: Exhaust flow rate increased to be more than the required ventilation rate.
Note on P217: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on N219: Sandeep: Chiller Type: Screw, Path B Efficiency Cap <75 Tons = 0.80 kW/Ton Cap <150 Tons = 0.79 kW/Ton Cap <300 Tons = 0.718 kW/Ton Cap >=300 Tons = 0.639 kW/Ton EER = 12 / (kW/ton) COP = EER / 3.412 EER = 12 / (kW/ton) COP = EER / 3.412
Note on H283: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H305: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N305: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P305: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R305: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T305: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.
Note on P362: Sandeep: Multiplier of 0.5 has been added.
Note on V394: Sandeep: Multiplier of 0.5 has been added.
Note on F434: Sandeep: The boiler is sized to be 25% larger than the peak loads of the baseline building. Baseline boilers shall be sized using weather files containing 99.6% heating design temperatures and 0.5% dry-bulb and 1% wet-bulb cooling design temperatures.
Note on F439: Sandeep: The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons.
Note on H439: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on J439: Sandeep: Standard Design The baseline chiller is always assumed to have a water-cooled condenser, although the chiller type will change depending on the design capacity.
Note on L439: Sandeep: Auto-sized. The full load output of the chiller operating at rating temperatures and flows including adjustment for pump heat and the project sizing ratio.
Note on P439: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on R439: Sandeep: The standard design 'Chiller Min Unloading Ratio' is determined based on the 'Chiller Type'. Screw = 15% See ACM ' Default Minimum Unloading Ratios Table-50 for further details
Note on H441: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on N441: Sandeep: Chiller Type: Screw, Path B Efficiency Cap <75 Tons = 0.80 kW/Ton Cap <150 Tons = 0.79 kW/Ton Cap <300 Tons = 0.718 kW/Ton Cap >=300 Tons = 0.639 kW/Ton EER = 12 / (kW/ton) COP = EER / 3.412 EER = 12 / (kW/ton) COP = EER / 3.412
Note on F449: Sandeep: The baseline system pumps are assumed to operate in On-Demand mode. The chilled water and condenser pumps are tied to the chiller operation, cycling on and off with the chiller, and the heating hot water pumps are tied to the boiler operation.
Note on H449: Sandeep: The chilled water pumps shall be modeled as variable-speed, variable flow, and the condenser water pumps shall be modeled as fixed speed. The hot water pumps shall be modeled as fixed-speed, variable flow, riding the curve.
Note on J449: Sandeep: Please refer to the reporting file - '070015-HotSml-Run03 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formulae commented in the cells below
Note on N449: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on R449: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table-31 available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on J451: Sandeep: Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on P451: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L451) Impeller Efficiency: 0.7
Note on J452: Sandeep: Cooling Tower Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 10 degF
Note on P452: Sandeep: For condenser water pumps, Head: 45 ft
Note on J453: Sandeep: Chiller Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 20 degF
Note on P453: Sandeep: For chilled water pumps, 40 ft plus an additional allowance of 0.03 ft/ton, but not to exceed 100 ft. (See formula in the cell)
Note on J454: Sandeep: Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on P454: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L454) Impeller Efficiency: 0.7
Note on N459: Sandeep: The cooling tower fan horsepower is 60 gpm/hp.

## 030006-OffMed-Run04 (hidden)
General Details |  |  |  | Model/Software Details |  |  |  |  | Key
Test Name |  |  | 030006-OffMed-Run04 | Model Revision no. | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name |  |  | 030006-OffMed-Run04.cibd | Version of Ruleset (Trunk rev. No.) | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone |  |  | CZ-06 | CBECC Software | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type |  |  | Medium Office | Date Tested | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category |  |  | Exterior Envelope | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type |  |  | NewComplete |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Building Geometry
Opaque
Type | Construction Assembly Name |  | Slope Category | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType | ConsType | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl | ConsAssmRef:ExtSolAbs
Exterior Wall | NACM_Metal Framed Wall | - | - | MetalFrameWall | 0.136 | - | - | - | -
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 | Layers -2 | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem | CodeItem | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Metal Framed Wall |  | Stucco - 7/8 in. | Building Paper - 1/16 in. | Expanded Polystyrene - EPS - 1 1/4 in. R5.2 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Simulation
Error: The area weighted average u-factor of new Metal Frame Walls in the project. '0.139', exceed the maximum allowable value, '0.105', violating Section 120.7. evaluating rule: Set CHECKCODE Proj:MtlFrmWallUFac[7] (15:'ContructAssembly.rule' line 6413) |  |  | Simulation Aborts

## 040006-OffLrg-Run05 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 040006-OffLrg-Run05 | Model Revision no. | 4000 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 040006-OffLrg-Run05 .cibd | Version of Ruleset (Trunk rev. No.) | Rel (828) |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3d (828) |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office | Date Tested | 2016-04-14 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.52 | 0.52 | 0.52 | 0.52 |  | 0.52
Baseline
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4

## 040006-OffLrg-Run06 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 040006-OffLrg-Run06 | Model Revision no. | 4000 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 040006-OffLrg-Run06 .cibd | Version of Ruleset (Trunk rev. No.) | Rel (828) |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3d (828) |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office | Date Tested | 2016-04-14 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.46 | 0.5 | 0.45 | 0.39 |  | 0.5
Baseline
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.4 | 0.45 | 0.4 | 0.35 |  | 0.4

## 080006-Whse-Run07 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 080006-Whse-Run07 | Model Revision no. | 4000 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006-Whse-Run07.cibd | Version of Ruleset (Trunk rev. No.) | Rel (828) |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3d (828) |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse | Date Tested | 2016-04-14 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Skylight | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Building Geometry
Fenestrations
Type | Skylight to Roof Ratio (Frac) | Skylight Curb | Skylight Glazing | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| CondSRR | FenConsRef:SkyltCurb | FenConsRef:SkyltGlz | FenConsRef:Ufactor |  | FenConsRef:SHGC | FenConsRef:VT
Skylight | 0.07 | CurbMounted | Glass | 0.55 |  | 0.2 | 0.4
Baseline
Building Geometry
Fenestrations
Type | Skylight to Roof Ratio (Frac) | Skylight Curb | Skylight Glazing | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| CondSRR | FenConsRef:SkyltCurb | FenConsRef:SkyltGlz | FenConsRef:Ufactor |  | FenConsRef:SHGC | FenConsRef:VT
Skylights | 0.05 | CurbMounted | Glass | 0.58 |  | 0.25 | 0.49

## 080006-Whse-Run08 (hidden)
| General Details |  | Model/Software Details |  |  |  |  | Key
| Test Name | 080006-Whse-Run08 | Model Revision no. | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
| Model File Name | 080006-Whse-Run08.cibd | Version of Ruleset (Trunk rev. No.) | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
| Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
| Building Type | Warehouse | Date Tested | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
| Test Category | Skylight | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type |  | NewComplete |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Daylighting
Fenestrations
| Type |  | Skylight to Roof Ratio (Frac)
CondSRR
| Skylight |  | 0.14
| Daylight Area | Space Function | Daylight Control Type | Total Floor Area (ft2) |  | Skylit Daylit Area (ft2) |  | Skylit Daylighting Control Lighting Fraction (frac)
|  |  | Spc:DayltgCtrlType | FlrArea |  | SkylitDaylitArea |  | SkylitDayltgCtrlLtgFrac
| Zone1 Office | Office (Greater than 250 square feet in floor area) | Continuous | 2549.75 | - | - | - | -
| Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Continuous | 12448.8 |  | 12300.4 |  | 0.98808
| Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Continuous | 34496.7 |  | 34324.2 |  | 0.995
Baseline
Daylighting
Fenestrations
| Type |  | Skylight to Roof Ratio (Frac)
CondSRR
| Skylight |  | 0.05
| Daylight Area | Space Function | Daylight Control Type | Total Floor Area (ft2) |  | Skylit Daylit Area (ft2) |  | Skylit Daylighting Control Lighting Fraction (frac)
|  |  | Spc:DayltgCtrlType | FlrArea |  | SkylitDaylitArea |  | SkylitDayltgCtrlLtgFrac
| Zone1 Office | Office (Greater than 250 square feet in floor area) | Continuous | 2549.75 | - | - | - | -
| Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Continuous | 12448.8 |  | 12441 |  | 0.99
| Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Continuous | 34496.7 |  | 34175.5 |  | 0.99

## 040006-OffLrg-Run11
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 040006-OffLrg-Run11 |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 040006-OffLrg-Run11.cibd |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Space Function |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
|  |  | Compliance Type |  | NewComplete |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed | [35 empty] | vvv Insert below | [33 empty] | vvv Insert below
Internal Load Components | [35 empty] | Space Interior Loads Electric Use Report | [33 empty] | Space Interior Loads Electric Use Report
Space | [40 empty] | Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated | [17 empty] | Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated
Space Name | Space Function |  | Space Floor Area (ft2) |  | People Density (ppl/1000ft2) |  | People (total number) |  | Occupancy Density - Schedule Name |  | Sensible Heat/person (Btu/h-person) |  | Latent Heat/person (Btu/h-person) |  | Lighting Power Density (W/ft2) |  | LPD - Schedule Name |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name |  | Hot Water Load/person (gal/h-person) |  | SHW Schedule |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Simulated Ventilation (cfm) |  | Cooling Thermostat Schedule |  | Heating Thermostat Schedule | Space |  |  |  |  | Interior Lighting |  |  |  | Interior Lighting |  |  |  | Receptacle |  |  |  | Process |  |  |  | Commercial Refrigeration | [12 empty] | Space |  |  |  |  | Interior Lighting |  |  |  | Interior Lighting |  |  |  | Receptacle |  |  |  | Process |  |  |  | Commercial Refrigeration
Spc |  |  |  |  | OccDens |  |  |  | OccSchRef:Name |  | OccSensHtRt |  | OccLatHtRt |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | RecptPwrDens |  | RecptSchRef:Name |  | Spc:HotWtrHtgRt |  | Spc:HotWtrHtgSchRef |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZnRef:ClgTstatSchRef |  | ThrmlZnRef:HtgTstatSchRef | Name | Conditioning Type | Space Function | Floor Area | Multiplier | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | [9 empty] | Name | Conditioning Type | Space Function | Floor Area | Multiplier | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use
Basement Spc | Office (Greater than 250 square feet in floor area) |  | 38353 |  | 5 |  | 191.77 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 5753 |  | OfficeClgSetPt |  | OfficeHtgSetPt |  |  |  | (ft2) |  | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | [12 empty] | (ft2) |  | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh)
Core_bottom | Retail Merchandise Sales, Wholesale Showroom |  | 27257.6 |  | 16.665 |  | 454.25 |  | RetailOccupancy |  | 250 |  | 200 |  | 1 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 15 |  | 0.2 |  | 6814 |  | RetailClgSetPt |  | RetailHtgSetPt
GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 3373.61 |  | 33.335 |  | 112.46 |  | RetailOccupancy |  | 250 |  | 250 |  | 1.5 |  | RetailLights |  | 0.5 |  | RetailReceptacle |  | 0.09 |  | RetailServiceHotWater |  | 15 |  | 0.15 |  | 1687 |  | RetailClgSetPt |  | RetailHtgSetPt
Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas |  | 2174.05 |  | 5 |  | 10.87 |  | RetailOccupancy |  | 250 |  | 250 |  | 0.5 |  | RetailLights |  | 0.2 |  | RetailReceptacle |  | 0 |  | RetailServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | RetailClgSetPt |  | RetailHtgSetPt
Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom |  | 3373.63 |  | 16.665 |  | 56.22 |  | RetailOccupancy |  | 250 |  | 200 |  | 1 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 15 |  | 0.2 |  | 843 |  | RetailClgSetPt |  | RetailHtgSetPt
Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom |  | 2174.04 |  | 16.665 |  | 36.23 |  | RetailOccupancy |  | 250 |  | 200 |  | 1 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 15 |  | 0.2 |  | 543 |  | RetailClgSetPt |  | RetailHtgSetPt
Core_mid | Medical and Clinical Care |  | 27257.6 |  | 5 |  | 136.29 |  | HealthOccupancy |  | 250 |  | 200 |  | 1 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.2 |  | 5452 |  | HealthClgSetPt |  | HealthHtgSetPt
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_1 | Medical and Clinical Care |  | 3373.61 |  | 5 |  | 16.87 |  | HealthOccupancy |  | 250 |  | 200 |  | 1 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.2 |  | 675 |  | HealthClgSetPt |  | HealthHtgSetPt
Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas |  | 2174.05 |  | 5 |  | 10.87 |  | HealthOccupancy |  | 250 |  | 250 |  | 0.5 |  | HealthLights |  | 0.2 |  | HealthReceptacle |  | 0 |  | HealthServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | HealthClgSetPt |  | HealthHtgSetPt
Perimeter_mid_ZN_3 | Medical and Clinical Care |  | 3373.63 |  | 5 |  | 16.87 |  | HealthOccupancy |  | 250 |  | 200 |  | 1 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.2 |  | 675 |  | HealthClgSetPt |  | HealthHtgSetPt
Perimeter_mid_ZN_4 | Medical and Clinical Care |  | 2174.04 |  | 5 |  | 10.87 |  | HealthOccupancy |  | 250 |  | 200 |  | 1 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.2 |  | 435 |  | HealthClgSetPt |  | HealthHtgSetPt
Core_hi | Office (Greater than 250 square feet in floor area) |  | 27257.6 |  | 5 |  | 136.288 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.16197 |  | 4415 |  | OfficeClgSetPt |  | OfficeHtgSetPt
HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) |  | 3373.61 |  | 5 |  | 16.87 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 506 |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas |  | 2174.05 |  | 5 |  | 10.87 |  | OfficeOccupancy |  | 250 |  | 250 |  | 0.5 |  | OfficeLights |  | 0.2 |  | OfficeReceptacle |  | 0 |  | OfficeServiceHotWater |  | 0 |  | 0 |  | 326 |  | NONE |  | NONE
Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) |  | 3373.63 |  | 5 |  | 16.87 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 506 |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 2174.04 |  | 5 |  | 10.87 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | OfficeClgSetPt |  | OfficeHtgSetPt
Core_top | Convention, Conference, Multipurpose and Meeting Center Areas |  | 27257.6 |  | 33.335 |  | 908.63 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.2 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 15 |  | 0.15 |  | 13630 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas |  | 3373.61 |  | 33.335 |  | 112.46 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.2 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 15 |  | 0.15 |  | 1687 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas |  | 2174.05 |  | 5 |  | 10.87 |  | AssemblyOccupancy |  | 250 |  | 250 |  | 0.5 |  | AssemblyLights |  | 0.2 |  | AssemblyReceptacle |  | 0 |  | AssemblyServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas |  | 3373.63 |  | 33.335 |  | 112.46 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.2 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 15 |  | 0.15 |  | 1687 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas |  | 2174.04 |  | 33.335 |  | 72.47 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.2 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 15 |  | 0.15 |  | 1087 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Ventilation
Building Story
Name | Floor Multiplier |  | Floor Area (ft2) |  | Ventilation (cfm)
Basement | 1 |  | 38353 |  | 5753
GroundFloor | 1 |  | 38353 |  | 10214
MidFloor | 5 |  | 191764.9 |  | 7562
HiFloor | 5 |  | 191764.9 |  | 5753
TopFloor | 1 |  | 38353 |  | 18416
Baseline
Internal Load Components | [35 empty] | Space Loads Report | [33 empty] | Space Loads Report
Space | [35 empty] | Space | [5 empty] | Occupancy |  |  |  |  | Service Hot Water |  | Ventilation | [5 empty] | Infiltration |  |  | Thermal Zone | [11 empty] | Space | [5 empty] | Occupancy |  |  |  |  | Service Hot Water |  | Ventilation | [5 empty] | Infiltration |  |  | Thermal Zone
Space Name | Space Function |  | Space Floor Area (ft2) |  | People Density (ppl/1000ft2) |  | People (total number) |  | Occupancy Density - Schedule Name |  | Sensible Heat/person (Btu/h-person) |  | Latent Heat/person (Btu/h-person) |  | Lighting Power Density (W/ft2) |  | LPD - Schedule Name |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name |  | Hot Water Load/person (gal/h-person) |  | SHW Schedule |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Cooling Thermostat Schedule |  | Heating Thermostat Schedule | Name | Conditioning Type | Space Function | Floor Area | Story Name | Multiplier | Density | Number | Schedule Name | Sensible Heat Rate | Latent Heat Rate | SHW Use | Schedule Name | Prop. DsgnVentPerArea | Prop. DsgnVentPerPerson | Code VentPerArea | Code VentPerPerson | Sim. Area Flow | Sim. Person Flow | Method | Schedule Name | Design Infiltration Rate | Clg Tstat Sch | Htg Tstat Sch | [10 empty] | Name | Conditioning Type | Space Function | Floor Area | Story Name | Multiplier | Density | Number | Schedule Name | Sensible Heat Rate | Latent Heat Rate | SHW Use | Schedule Name | Prop. DsgnVentPerArea | Prop. DsgnVentPerPerson | Code VentPerArea | Code VentPerPerson | Sim. Area Flow | Sim. Person Flow | Method | Schedule Name | Design Infiltration Rate | Clg Tstat Sch | Htg Tstat Sch
Spc |  |  |  |  | OccDens |  |  |  | OccSchRef:Name |  | OccSensHtRt |  | OccLatHtRt |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | RecptPwrDens |  | RecptSchRef:Name |  | Spc:HotWtrHtgRt |  | Spc:HotWtrHtgSchRef |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZnRef:ClgTstatSchRef |  | ThrmlZnRef:HtgTstatSchRef |  |  |  | (ft2) |  |  | (ppl/1000ft2) | (people) |  | (Btu/h-person) | (Btu/h-person) | (gal/min) |  | (cfm/ft2) | (cfm/person) | (cfm/ft2) | (cfm/person) | (cfm) | (cfm) |  |  | (cfm/ft2) | [15 empty] | (ft2) |  |  | (ppl/1000ft2) | (people) |  | (Btu/h-person) | (Btu/h-person) | (gal/min) |  | (cfm/ft2) | (cfm/person) | (cfm/ft2) | (cfm/person) | (cfm) | (cfm) |  |  | (cfm/ft2)
Basement Spc | Office (Greater than 250 square feet in floor area) |  | 38353 |  | 5 |  | 191.8 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 5753 |  | OfficeClgSetPt |  | OfficeHtgSetPt
Core_bottom | Retail Merchandise Sales, Wholesale Showroom |  | 27257.61 |  | 16.665 |  | 454.2 |  | RetailOccupancy |  | 250 |  | 200 |  | 1.2 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 15 |  | 0.2 |  | 6813 |  | RetailClgSetPt |  | RetailHtgSetPt
GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | -
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 3373.61 |  | 33.335 |  | 112.5 |  | RetailOccupancy |  | 250 |  | 250 |  | 1.5 |  | RetailLights |  | 0.5 |  | RetailReceptacle |  | 0.09 |  | RetailServiceHotWater |  | 15 |  | 0.15 |  | 1688 |  | RetailClgSetPt |  | RetailHtgSetPt
Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas |  | 2174.05 |  | 5 |  | 10.9 |  | RetailOccupancy |  | 250 |  | 250 |  | 0.6 |  | RetailLights |  | 0.2 |  | RetailReceptacle |  | 0 |  | RetailServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | RetailClgSetPt |  | RetailHtgSetPt
Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom |  | 3373.63 |  | 16.665 |  | 56.2 |  | RetailOccupancy |  | 250 |  | 200 |  | 1.2 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 15 |  | 0.2 |  | 843 |  | RetailClgSetPt |  | RetailHtgSetPt
Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom |  | 2174.04 |  | 16.665 |  | 36.2 |  | RetailOccupancy |  | 250 |  | 200 |  | 1.2 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 15 |  | 0.2 |  | 543 |  | RetailClgSetPt |  | RetailHtgSetPt
Core_mid | Medical and Clinical Care |  | 27257.6 |  | 5 |  | 136.3 |  | HealthOccupancy |  | 250 |  | 200 |  | 1.2 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.15216 |  | 4147 |  | HealthClgSetPt |  | HealthHtgSetPt
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | -
Perimeter_mid_ZN_1 | Medical and Clinical Care |  | 3373.61 |  | 5 |  | 16.9 |  | HealthOccupancy |  | 250 |  | 200 |  | 1.2 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.15216 |  | 513 |  | HealthClgSetPt |  | HealthHtgSetPt
Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas |  | 2174.05 |  | 5 |  | 10.9 |  | HealthOccupancy |  | 250 |  | 250 |  | 0.6 |  | HealthLights |  | 0.2 |  | HealthReceptacle |  | 0 |  | HealthServiceHotWater |  | 0 |  | 0.11412 |  | 248 |  | HealthClgSetPt |  | HealthHtgSetPt
Perimeter_mid_ZN_3 | Medical and Clinical Care |  | 3373.63 |  | 5 |  | 16.9 |  | HealthOccupancy |  | 250 |  | 200 |  | 1.2 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.15216 |  | 513 |  | HealthClgSetPt |  | HealthHtgSetPt
Perimeter_mid_ZN_4 | Medical and Clinical Care |  | 2174.04 |  | 5 |  | 10.9 |  | HealthOccupancy |  | 250 |  | 200 |  | 1.2 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.15216 |  | 331 |  | HealthClgSetPt |  | HealthHtgSetPt
Core_hi | Office (Greater than 250 square feet in floor area) |  | 27257.6 |  | 5 |  | 136.3 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.16197 |  | 4415 |  | OfficeClgSetPt |  | OfficeHtgSetPt
HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | -
Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) |  | 3373.61 |  | 5 |  | 16.9 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 506 |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas |  | 2174.05 |  | 5 |  | 10.9 |  | OfficeOccupancy |  | 250 |  | 250 |  | 0.6 |  | OfficeLights |  | 0.2 |  | OfficeReceptacle |  | 0 |  | OfficeServiceHotWater |  | 0 |  | 0 |  | 0 |  | NONE |  | NONE
Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) |  | 3373.63 |  | 5 |  | 16.9 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 506 |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 2174.04 |  | 5 |  | 10.9 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | OfficeClgSetPt |  | OfficeHtgSetPt
Core_top | Convention, Conference, Multipurpose and Meeting Center Areas |  | 27257.6 |  | 33.335 |  | 908.6 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.4 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 15 |  | 0.15 |  | 13629 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas |  | 3373.61 |  | 33.335 |  | 112.5 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.4 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 15 |  | 0.15 |  | 1688 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas |  | 2174.05 |  | 5 |  | 10.9 |  | AssemblyOccupancy |  | 250 |  | 250 |  | 0.6 |  | AssemblyLights |  | 0.2 |  | AssemblyReceptacle |  | 0 |  | AssemblyServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas |  | 3373.63 |  | 33.335 |  | 112.5 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.4 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 15 |  | 0.15 |  | 1688 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas |  | 2174.04 |  | 33.335 |  | 72.5 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.4 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 15 |  | 0.15 |  | 1088 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | -
Ventilation
Building Story | [35 empty] | Space Interior Lighting Report | [33 empty] | Space Interior Lighting Report
Name | Floor Multiplier |  | Floor Area (ft2) |  | Ventilation (cfm) | [30 empty] | Space |  |  |  |  | Regulated | [7 empty] | Non-Regulated | [20 empty] | Space |  |  |  |  | Regulated | [10 empty] | Non-Regulated
[36 empty] | Name | Conditioning Type | Space Function | Lighting Status | Floor Area | Lighting Specification Method | Installed Power | Schedule Name | Schedule | Lighting System Count | Lighting Control Credit | Simulated Power | Simulated LPD | Power | Schedule Name | Schedule | LPD | [17 empty] | Name | Conditioning Type | Space Function | Lighting Status | Floor Area | Lighting Specification Method | Installed Power | Schedule Name | Schedule | Lighting System Count | Lighting Control Credit | General Lighting Power | Area Category Allowances | Tailored Allowances | Simulated Power | Simulated LPD | Power | Schedule Name | Schedule
Basement | 1 |  | 38353 |  | 5753 | [34 empty] | (ft2) |  | (Watts) |  | (FLH) |  | (Watts) | (Watts) | (Watts/ft2) | (Watts) |  | (FLH) | (Watts/ft2) | [21 empty] | (ft2) |  | (Watts) |  | (FLH) |  | (Watts) | (Watts) | (Watts) | (Watts) | (Watts) | (Watts/ft2) | (Watts) |  | (FLH)
GroundFloor | 1 |  | 38353 |  | 10214
MidFloor | 5 |  | 191764.9 |  | 7562
HiFloor | 5 |  | 191764.9 |  | 5753
TopFloor | 1 |  | 38353 |  | 18416
[70 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
[36 empty] | Space Daylighting | [33 empty] | Space Daylighting
[36 empty] | Name | SpcFunc | FlrArea | DayltgCtrlType | MandMinDaylitArea | MinDimLtgFrac | MinDimPwrFrac | NumOfCtrlSteps | SkylitDaylitArea | SkylitDayltgCtrlLtgPwr | SkylitDayltgCtrlLtgFrac | SkylitDayltgIllumSetpt | SkylitDayltgIllumSetptAdjFac | SkylitDayltgAdjIllumSetpt |  | PriSideDayltgRefPtCoord[1] | PriSideDayltgRefPtCoord[2] | PriSideDayltgRefPtCoord[3] | PriSideDaylitArea | PriSideDayltgCtrlLtgPwr | PriSideDayltgCtrlLtgFrac | PriSideDayltgIllumSetpt | PriSideDayltgIllumSetptAdjFac | PriSideDayltgAdjIllumSetpt |  | SecSideDayltgRefPtCoord[1] | SecSideDayltgRefPtCoord[2] | SecSideDayltgRefPtCoord[3] | SecSideDaylitArea | SecSideDayltgCtrlLtgPwr | SecSideDayltgCtrlLtgFrac | SecSideDayltgIllumSetpt | SecSideDayltgIllumSetptAdjFac | SecSideDayltgAdjIllumSetpt | Name | SpcFunc | FlrArea | DayltgCtrlType | MandMinDaylitArea | MinDimLtgFrac | MinDimPwrFrac | NumOfCtrlSteps | SkylitDaylitArea | SkylitDayltgCtrlLtgPwr | SkylitDayltgCtrlLtgFrac | SkylitDayltgIllumSetpt | SkylitDayltgIllumSetptAdjFac | SkylitDayltgAdjIllumSetpt |  | PriSideDayltgRefPtCoord[1] | PriSideDayltgRefPtCoord[2] | PriSideDayltgRefPtCoord[3] | PriSideDaylitArea | PriSideDayltgCtrlLtgPwr | PriSideDayltgCtrlLtgFrac | PriSideDayltgIllumSetpt | PriSideDayltgIllumSetptAdjFac | PriSideDayltgAdjIllumSetpt |  | SecSideDayltgRefPtCoord[1] | SecSideDayltgRefPtCoord[2] | SecSideDayltgRefPtCoord[3] | SecSideDaylitArea | SecSideDayltgCtrlLtgPwr | SecSideDayltgCtrlLtgFrac | SecSideDayltgIllumSetpt | SecSideDayltgIllumSetptAdjFac | SecSideDayltgAdjIllumSetpt
[36 empty] | Space | [7 empty] | Skylit Zone | [6 empty] | Primary Sidelit Daylit Zone | [9 empty] | Secondary Sidelit Daylit Zone | [8 empty] | Space | [7 empty] | Skylit Zone | [6 empty] | Primary Sidelit Daylit Zone | [9 empty] | Secondary Sidelit Daylit Zone
[36 empty] | Name | Space Function | Floor Area | Control Type | MinDayltg per 140.3c | Min. Dim. Ltg. Frac. | Min Dim. Pwr. Frac. | Switched # Ctrl. Steps | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point | Name | Space Function | Floor Area | Control Type | MinDayltg per 140.3c | Min. Dim. Ltg. Frac. | Min Dim. Pwr. Frac. | Switched # Ctrl. Steps | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point
[38 empty] | (ft2) |  | (ft2) |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  | (ft2) |  | (ft2) |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux)
[36 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[36 empty] | BuildingStory | [33 empty] | BuildingStory
[38 empty] | Floor Area (including multipliers) |  |  |  |  | Ventilation (Design) |  |  | Ventilation (For Balance) | [5 empty] | General |  | Comm. Kitchen |  | Parking Garage |  | Laboratory | [13 empty] | Floor Area (including multipliers) |  |  |  |  | Ventilation (Design) |  |  | Ventilation (For Balance) | [5 empty] | General |  | Comm. Kitchen |  | Parking Garage |  | Laboratory
[36 empty] | Name | Multiplier | Total | Cond. NRes | Cond. Res | Total Cond. | Number | Total | Code Min. | Exhaust | Total | Code Min. | Tot:Min Ratio | Exhaust | Vent:Exh Ratio | Vent Mult. | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | [10 empty] | Name | Multiplier | Total | Cond. NRes | Cond. Res | Total Cond. | Number | Total | Code Min. | Exhaust | Total | Code Min. | Tot:Min Ratio | Exhaust | Vent:Exh Ratio | Vent Mult. | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust
[38 empty] | (ft2) | (ft2) | (ft2) | (ft2) | (people) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) |  | (cfm) |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | [12 empty] | (ft2) | (ft2) | (ft2) | (ft2) | (people) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) |  | (cfm) |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
[36 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[36 empty] | Space | [33 empty] | Space
[43 empty] | Occupancy |  |  | Ventilation |  | Design Input (By Component) |  |  |  |  | Minimum Req. (By Component) |  |  |  | Simulated |  | Exhaust |  |  | ForBalance | [14 empty] | Occupancy |  |  | Ventilation |  | Design Input (By Component) |  |  |  |  | Minimum Req. (By Component) |  |  |  | Simulated |  | Exhaust |  |  | ForBalance
[36 empty] | Name | Story Name | Condg Type | Space Function | Thermal Zone | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Per Space | Calculated Flow | Per Occupant | Per Area | Per Volume | Calculated Flow |  |  | Calculated Flow | Lab Exh Type | Max Kitchen | Ventilation | Exhaust | [6 empty] | Name | Story Name | Condg Type | Space Function | Thermal Zone | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Per Space | Calculated Flow | Per Occupant | Per Area | Per Volume | Calculated Flow |  |  | Calculated Flow | Lab Exh Type | Max Kitchen | Ventilation | Exhaust
[41 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm) | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) |  | (cfm) | (cfm) | (cfm) | [11 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm) | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) |  | (cfm) | (cfm) | (cfm)
[36 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[36 empty] | ThermalZone | [33 empty] | ThermalZone
[43 empty] | Occupancy |  |  |  | Ventilation |  | Design Value (Total) |  |  |  |  | Minimum Req. (Total) |  |  |  | Simulated |  |  | Exhaust | [15 empty] | Occupancy |  |  |  | Ventilation |  | Design Value (Total) |  |  |  |  | Minimum Req. (Total) |  |  |  | Simulated |  |  | Exhaust
[36 empty] | Name | Story Name | Type | Ventilation Source | Pri. HVAC System | Ventilation System | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Calculated Flow |  | Per Occupant | Per Area | Per Volume | Calculated Flow | Per Occupant | Per Area | Calculated Flow | Calculated Flow | ExhSysRef | ExhOperMode | ExhCtrlMthd | ExhBalancedSchRef |  |  |  |  | Name | Story Name | Type | Ventilation Source | Pri. HVAC System | Ventilation System | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Calculated Flow |  | Per Occupant | Per Area | Per Volume | Calculated Flow | Per Occupant | Per Area | Calculated Flow | Calculated Flow | ExhSysRef | ExhOperMode | ExhCtrlMthd | ExhBalancedSchRef
[41 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) | (cfm) | [13 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) | (cfm)

## 030006-OffMed-Run12 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run12 |  | Model Revision no. |  | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run12.cibd |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Simulated Lighting Power Density (LPD) (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | Spc:IntLtgSpecMthd
Core_bottom | Waiting Area |  | 0.75 |  | 0.2 |  | 0.95 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_2 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_3 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_4 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area |  | 0.75 |  | 0.2 |  | 0.95 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_2 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_3 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_4 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area |  | 0.75 |  | 0.2 |  | 0.95 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_2 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_3 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_4 | Lobby, Main Entry |  | 0.5 | - | - |  | 0.5 |  | OfficeLights |  | Tailored Method
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Simulated Lighting Power Density (LPD) (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | Spc:IntLtgSpecMthd
Core_bottom | Waiting Area |  | 0.8 |  | 0.2 |  | 1 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_2 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_3 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_4 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area |  | 0.8 |  | 0.2 |  | 1 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_2 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_3 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_4 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area |  | 0.8 |  | 0.2 |  | 1 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_2 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_3 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_4 | Lobby, Main Entry |  | 0.8 | - | - |  | 0.8 |  | OfficeLights |  | Tailored Method
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Note on G40: Sandeep: Standards_Section 140.6: TAilored Method- The additional allowed power for ornamental/special effects lighting for each applicable area shall be the smaller of: a. The product of the allowed ornamental/special effects lighting power determined in accordance with Section 140.6(c)3Kiii, times floor square footage determined in accordance with Section 140.6(c)3Kiv; {or (0.5*10586.7) = 5293.35 W} b. The actual power of allowed ornamental/special effects lighting. {Installed power - 2112 W} Hence modeled 2112W or 2112/10586.7 = 0.2 W/ft2
Note on G46: Sandeep: Standards_Section 140.6: TAilored Method- The additional allowed power for ornamental/special effects lighting for each applicable area shall be the smaller of: a. The product of the allowed ornamental/special effects lighting power determined in accordance with Section 140.6(c)3Kiii, times floor square footage determined in accordance with Section 140.6(c)3Kiv; {or (0.5*10586.7) = 5293.35 W} b. The actual power of allowed ornamental/special effects lighting. {Installed power - 2112 W} Hence modeled 2112W or 2112/10586.7 = 0.2 W/ft2
Note on G52: Sandeep: Standards_Section 140.6: TAilored Method- The additional allowed power for ornamental/special effects lighting for each applicable area shall be the smaller of: a. The product of the allowed ornamental/special effects lighting power determined in accordance with Section 140.6(c)3Kiii, times floor square footage determined in accordance with Section 140.6(c)3Kiv; {or (0.5*10586.7) = 5293.35 W} b. The actual power of allowed ornamental/special effects lighting. {Installed power - 2112 W} Hence modeled 2112W or 2112/10586.7 = 0.2 W/ft2

## 030006-OffMed-Run13 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run13 |  | Model Revision no. |  | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run13.cibd |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name
Core_bottom | Waiting Area |  | 0.6 | - | - |  | 1.2 |  | 0.1 |  | 1.9 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_2 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_4 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area |  | 0.6 | - | - |  | 1.2 |  | 0.1 |  | 1.9 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_2 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_4 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area |  | 0.6 | - | - |  | 1.2 |  | 0.1 |  | 1.9 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_2 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_4 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.91 |  | OfficeLights |  | Tailored Method
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name
Core_bottom | Waiting Area |  | 0.8 | - | - |  | 0.5 |  | 0.1 |  | 1.4 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_2 | Lobby, Main Entry |  | 0.8 |  | 0.09 | - | - | - | - |  | 0.89 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_bot_ZN_4 | Lobby, Main Entry |  | 0.8 |  | 0.09 | - | - | - | - |  | 0.89 |  | OfficeLights |  | Tailored Method
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area |  | 0.8 | - | - |  | 0.5 |  | 0.1 |  | 1.4 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_2 | Lobby, Main Entry |  | 0.8 |  | 0.09 | - | - | - | - |  | 0.89 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_mid_ZN_4 | Lobby, Main Entry |  | 0.8 |  | 0.09 | - | - | - | - |  | 0.89 |  | OfficeLights |  | Tailored Method
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area |  | 0.8 | - | - |  | 0.5 |  | 0.1 |  | 1.4 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_2 | Lobby, Main Entry |  | 0.8 |  | 0.09 | - | - | - | - |  | 0.89 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_3 | Lobby, Main Entry |  | 0.8 |  | 0.1 | - | - | - | - |  | 0.9 |  | OfficeLights |  | Tailored Method
Perimeter_top_ZN_4 | Lobby, Main Entry |  | 0.8 |  | 0.09 | - | - | - | - |  | 0.89 |  | OfficeLights |  | Tailored Method
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## 020006-OffSml-Run14 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020006-OffSml-Run14 |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 020006-OffSml-Run14.cibd |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function |  | Installed Lighitng Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor | Lighting Power Density (Simulated) (W/ft2) | Lighting Schedule
Spc | SpcFunc |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF | Spc:IntLPDReg | IntLtgRegSchRef
Perimeter_ZN_1 | Office (Greater than 250 square feet in floor area) |  | 1152 |  | 1094.4 |  | DemandResponsiveControl |  | 0.05 | 0.9 | OfficeLights
Perimeter_ZN_2 | Office (Greater than 250 square feet in floor area) |  | 640 |  | 608 |  | DemandResponsiveControl |  | 0.05 | 0.84 | OfficeLights
Perimeter_ZN_3 | Office (Greater than 250 square feet in floor area) |  | 1152 |  | 1094.4 |  | DemandResponsiveControl |  | 0.05 | 0.9 | OfficeLights
Perimeter_ZN_4 | Office (Greater than 250 square feet in floor area) |  | 640 |  | 608 |  | DemandResponsiveControl |  | 0.05 | 0.84 | OfficeLights
Core_bottom | Office (Greater than 250 square feet in floor area) |  | 1408 |  | 1337.6 |  | DemandResponsiveControl |  | 0.05 | 0.83 | OfficeLights
Baseline
Internal Load Components
Space
Space Name | Space Function |  | Installed Lighitng Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor | Lighting Power Density (Simulated) (W/ft2) | Lighting Schedule
Spc | SpcFunc |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF | Spc:IntLPDReg | IntLtgRegSchRef
Perimeter_ZN_1 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Perimeter_ZN_2 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Perimeter_ZN_3 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Perimeter_ZN_4 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Core_bottom | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | 0.75 | OfficeLights
Note on K13: Sandeep: The Proposed Transform does not utilize the PAF, the evaluation for the same has already been made and only the final LPD is relevant

## 080006-Whse-Run15 (hidden)
Note: Reference positions of the daylight control sensors are not being checked.
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 080006-Whse-Run15 |  | Model Revision no. |  | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006-Whse-Run15.cibd |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting Control |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Daylighting
Space
Space Name | Space Function |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | Continuous | - | - | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 10730.4 |  | 5000 |  | 250 |  | 250
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 34302 |  | 15000 |  | 250 |  | 250
Space Name | Space Function |  | Primary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint
Spc |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 538.667 |  | 150 |  | 400 |  | 400
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Space Name | Space Function |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 421.333 | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Baseline
Daylighting
Space
Space Name | Space Function |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | Continuous | - | - | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 10730.4 |  | 6438.25 |  | 250 |  | 250
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 34387.5 |  | 20632.5 |  | 250 |  | 250
Space Name | Space Function |  | Primary Sidelit Daylit Area |  | Controlled General Lighting Power |  | Illuminance Setpoint |  | Adjusted Illuminance Setpoint
|  |  | (ft2) |  | (W) |  | (lux) |  | (lux)
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 538.667 |  | 404 |  | 400 |  | 400
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Space Name | Space Function |  | Secondary Sidelit Daylit Area |  | Controlled General Lighting Power |  | Illuminance Setpoint |  | Adjusted Illuminance Setpoint
|  |  | (ft2) |  | (W) |  | (lux) |  | (lux)
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 421.333 |  | 316 |  | 287.5 |  | 1150
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -

## 050006-RetlMed-Run16 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 050006-RetlMed-Run16 |  |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 050006-RetlMed-Run16.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Retail |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting Control |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function | Space Floor Area (ft2) |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | Allowance Area (ft2)
Spc |  |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 |  | 0.6 | - | - |  | 0.6 | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 |  | 1.2 | - | - |  | 1.2 | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 1.5 | - | - |  | 1.5 | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 1.6 |  | 0.75 |  | 2.35 |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 1.2 | - | - |  | 1.2 | - | -
Daylighting
Space
Space Name | Space Function | Space Floor Area (ft2) |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 |  | Continuous |  | 16742.6 |  | 20091.1 |  | 950 |  | 950
Front_Entry | Lobby, Main Entry | 129.167 |  | ContinuousPlusOff | - | - | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | Continuous | - | - | - | - | - | - | - | -
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | Continuous | - | - | - | - | - | - | - | -
Space Name | Space Function | Space Floor Area (ft2) |  | Primary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint
Spc |  |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | - | - | - | - | - | - | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 114.3 |  | 171.45 |  | 200 |  | 300
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 718.1 |  | 1216 |  | 950 |  | 1425
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 718.1 |  | 861.69 |  | 950 |  | 1425
Space Name | Space Function | Space Floor Area (ft2) |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | - | - | - | - | - | - | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 14.8 | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 721.5 |  | 2592 |  | 950 |  | 1900
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 721.5 |  | 865.81 |  | 950 |  | 1900
Baseline
Internal Load Components
Space
Space Name | Space Function | Space Floor Area (ft2) |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | Allowance Area (ft2)
Spc |  |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 |  | 0.6 | - | - |  | 0.6 | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 |  | 1.2 | - | - |  | 1.2 | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 1.5 | - | - |  | 1.5 | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 1.5 |  | 0.65 |  | 2.1487 |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 1.2 | - | - |  | 1.2 | - | -
Daylighting
Space
Spc
Space Name | Space Function | Space Floor Area (ft2) |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 |  | Continuous |  | 16742.6 |  | 20091.1 |  | 950 |  | 950
Front_Entry | Lobby, Main Entry | 129.167 |  | Continuous | - | - | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | Continuous | - | - | - | - | - | - | - | -
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | Continuous | - | - | - | - | - | - | - | -
Space Name | Space Function | Space Floor Area (ft2) |  | Primary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | - | - | - | - | - | - | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 114.297 |  | 171.4455 |  | 200 |  | 300
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 718.075 |  | 1542.9134 |  | 950 |  | 1425
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 718.075 |  | 861.69 |  | 950 |  | 1425
Space Name | Space Function | Space Floor Area (ft2) |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | - | - | - | - | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | - | - | - | - | - | - | - | -
Front_Entry | Lobby, Main Entry | 129.167 |  | 14.77 | - | - | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 721.51 |  | 1550.2941 |  | 950 |  | 1900
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 |  | 721.51 |  | 865.812 |  | 950 |  | 1900

## 020006-OffSml-Run18
General Details |  | Model/Software Details |  |  |  |  | Key
Test Name | 020006-OffSml-Run18 | Model Revision no. | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 020006-OffSml-Run18.cibd | Version of Ruleset (Trunk rev. No.) | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office | Date Tested | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name | Type | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys | AirSys:Type | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Core_ZN Thermal Zone | CoreZnPSZ AirSys | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | Perim1ZnPSZ AirSys | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnPSZ AirSys | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg | CoilClg:Type | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
CoreZnPSZ AirSys | CoreZnCoolingCoil | DirectExpansion | 13 | - | - |  | CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
Perim1ZnPSZ AirSys | Perim1ZnCoolingCoil | DirectExpansion | 13 | - | - |  | CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnPSZ AirSys | Perim2ZnCoolingCoil | DirectExpansion | 13 | - | - |  | CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil | DirectExpansion | 13 | - | - |  | CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil | DirectExpansion | 13 | - | - |  | CoilClgDXEER13SEER16EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Type | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
CoreZnPSZ AirSys | CoreZnHeatingCoil | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim1ZnPSZ AirSys | Perim1ZnHeatingCoil | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim2ZnPSZ AirSys | Perim2ZnHeatingCoil | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Control Method | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
Zone:SysServed | Fan: | Fan:CtrlMthd | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
CoreZnPSZ AirSys | CoreZnSupplyFan | Constant Volume | BrakeHorsePower |  | 1.6 | - | - | - | - | 2 | 0.865
Perim1ZnPSZ AirSys | Perim1ZnSupplyFan | Constant Volume | BrakeHorsePower |  | 1.12 | - | - | - | - | 1.5 | 0.855
Perim2ZnPSZ AirSys | Perim2ZnSupplyFan | Constant Volume | BrakeHorsePower |  | 0.8 | - | - | - | - | 1 | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan | Constant Volume | BrakeHorsePower |  | 1.2 | - | - | - | - | 1.5 | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan | Constant Volume | BrakeHorsePower |  | 0.8 | - | - | - | - | 1 | 0.855
Thermal Zone - Name | Conditioning Type | Cooling Thermostat Setpoint | Heating Thermostat Setpoint |  | Economizer Integration
ThrmlZn | ThrmlZn:Type | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef |  | OACtrl:EconoIntegration
Core_ZN Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Perimeter_ZN_1 Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Perimeter_ZN_2 Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Perimeter_ZN_3 Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Perimeter_ZN_4 Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Baseline
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name | Type | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys | AirSys:Type | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Core_ZN Thermal Zone | BaseAirSys3 | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | BaseAirSys3-2 | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | BaseAirSys3-3 | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | BaseAirSys3-4 | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | BaseAirSys3-5 | SZAC | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg | CoilClg:Type | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg | DirectExpansion | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-2 | BaseSys3 CoilClg-2 | DirectExpansion | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-3 | BaseSys3 CoilClg-3 | DirectExpansion | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-4 | BaseSys3 CoilClg-4 | DirectExpansion | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-5 | BaseSys3 CoilClg-5 | DirectExpansion | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Type | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-2 | BaseSys3 CoilHtg-2 | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-3 | BaseSys3 CoilHtg-3 | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-4 | BaseSys3 CoilHtg-4 | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-5 | BaseSys3 CoilHtg-5 | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
Zone:SysServed | Fan: | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan | Constant Volume | StaticPressure |  | 1134.38 |  | 0.89384 |  | 0.5 | 2.5 | 1 | 0.855
BaseAirSys3-2 | BaseSys3 Fan-2 | Constant Volume | StaticPressure |  | 1225.09 |  | 0.96532 |  | 0.5 | 2.5 | 1 | 0.855
BaseAirSys3-3 | BaseSys3 Fan-3 | Constant Volume | StaticPressure |  | 630.706 |  | 0.49697 |  | 0.5 | 2.5 | 0.5 | 0.855
BaseAirSys3-4 | BaseSys3 Fan-4 | Constant Volume | StaticPressure |  | 876.896 |  | 0.69096 |  | 0.5 | 2.5 | 0.75 | 0.855
BaseAirSys3-5 | BaseSys3 Fan-5 | Constant Volume | StaticPressure |  | 693.119 |  | 0.54615 |  | 0.5 | 2.5 | 0.75 | 0.855
Thermal Zone - Name | Conditioning Type | Cooling Thermostat Setpoint | Heating Thermostat Setpoint |  | Economizer Integration
ThrmlZn | ThrmlZn:Type | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef |  | OACtrl:EconoIntegration
Core_ZN Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Perimeter_ZN_1 Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Perimeter_ZN_2 Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Perimeter_ZN_3 Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Perimeter_ZN_4 Thermal Zone | Conditioned | OfficeClgSetPt | OfficeHtgSetPt | - | -
Note on G68: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on G86: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on M86: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on O86: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on Q86: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on S86: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.

## 030006-OffMed-Run19
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run19 |  |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 030006-OffMed-Run19.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Complete |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space Name | Space Function | Space Floor Area (ft2) |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name
Spc |  |  |  | RecptPwrDens |  | RecptSchRef:Name
Core_bottom | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | -
Core_mid | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | -
Core_top | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor | BottomVAV | New |  | Bottom Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | Mid VAV | New |  | Mid Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | Top VAV | New |  | Top Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Core_bottom Thermal Zone | Core_bottomZnPSZ AirSys | New |  | Bottom Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Core_mid Thermal Zone | Core_midZnPSZ AirSys | New |  | Mid Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Core_top Thermal Zone | Core_topZnPSZ AirSys | New |  | Top Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | New |  | DirectExpansion |  | 12.96 |  | 13.09 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | New |  | DirectExpansion |  | 12.96 |  | 13.09 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | New |  | DirectExpansion |  | 12.96 |  | 13.09 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_bottomZnPSZ AirSys | Core_bottomZnCoolingCoil | New |  | DirectExpansion |  | 13.65 |  | 13.79 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_midZnPSZ AirSys | Core_midZnCoolingCoil | New |  | DirectExpansion |  | 13.65 |  | 13.79 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_topZnPSZ AirSys | Core_topZnCoolingCoil | New |  | DirectExpansion |  | 13.65 |  | 13.79 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating | New |  | HotWater
Mid VAV | Mid VAV CoilHeating | New |  | HotWater
Top VAV | Top VAV CoilHeating | New |  | HotWater
BottomVAV | (All ReheatCoils) | New |  | HotWater
Mid VAV | (All ReheatCoils) | New |  | HotWater
Top VAV | (All ReheatCoils) | New |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Power adjustment curve
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
Bottom Floor | BottomVAV SupplyFan | New |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 6.21 | - | - | - | - |  | 7.5 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Mid Floor | MidVAV SupplyFan | New |  | VariableSpeedDrive |  | Static Pressure |  | 10850 |  | 7.8917 |  | 0.65 |  | 3 |  | 10 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Top Floor | TopVAV SupplyFan | New |  | VariableSpeedDrive |  | Static Pressure |  | 10200 |  | 9.3767 |  | 0.6 |  | 3.5 |  | 10 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Core_bottom Thermal Zone | Core_bottomZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
Core_mid Thermal Zone | Core_midZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
Core_top Thermal Zone | Core_topZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV |  | New |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV |  | New |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV |  | New |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Core_bottomZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Core_midZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Core_topZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Perimeter Zones) | Conditioned | New |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Core Zones) | Conditioned | New |  | DataClgSetpt |  | DataHtgSetpt
(All Plenum) | Plenum | New | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 |  | New |  | 1700000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Baseline
Internal Load Components
Space Name | Space Function | Space Floor Area (ft2) |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name
Spc |  |  |  | RecptPwrDens |  | RecptSchRef:Name
Core_bottom | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_mid | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_top | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Core_bottom Thermal Zone | BaseAirSys11 | New |  | Bottom Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
Core_mid Thermal Zone | BaseAirSys11-2 | New |  | Mid Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
Core_top Thermal Zone | BaseAirSys11-3 | New |  | Top Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 10.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11 | BaseSys11 CoilClg | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11-2 | BaseSys11 CoilClg-2 | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11-3 | BaseSys11 CoilClg-3 | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index | Power adjustment curve
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx | (Pwr_fPLRCrvRef)
Bottom Floor (Peripheral Zones) | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 7240.95 |  | 6.6565 |  | 0.6 |  | 3.5 |  | 7.5 |  | 0.917 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Mid Floor (Peripheral Zones) | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 8421.42 |  | 7.7417 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Top Floor (Peripheral Zones) | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 8856.41 |  | 8.1415 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Core_bottom Thermal Zone | BaseSys11 Fan | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 38115.2 |  | 23.2955 |  | 0.62 |  | 2.4045 |  | 20 |  | 0.93 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Core_mid Thermal Zone | BaseSys11 Fan-2 | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 37962.7 |  | 23.2023 |  | 0.62 |  | 2.4045 |  | 20 |  | 0.93 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Core_top Thermal Zone | BaseSys11 Fan-3 | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 38555.9 |  | 23.7168 |  | 0.62 |  | 2.4201 |  | 25 |  | 0.936 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Bottom Floor (Peripheral Zones) | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 6876.49 |  | 2.0319 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
Mid Floor (Peripheral Zones) | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 8056.95 |  | 2.3807 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
Top Floor (Peripheral Zones) | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 8491.95 |  | 2.5092 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Peripheral Zones) | Conditioned | New |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Core Zones) | Conditioned | New |  | DataClgSetpt |  | DataHtgSetpt
(All Plenum) | Plenum | New | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 135215 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Note on H131: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H149: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N149: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P149: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R149: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T149: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Execpt when the 'Power-Per-Flow' modeling method is used.
Note on P151: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on P152: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on P153: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification
Note on F180: Sandeep: The boiler is sized to be 25% larger than the peak loads of the baseline building. Baseline boilers shall be sized using weather files containing 99.6% heating design temperatures and 0.5% dry-bulb and 1% wet-bulb cooling design temperatures.
Note on H180: Sandeep: Boilers for the baseline design are assumed to have the minimum efficiency as listed in Table E-4 of the 2009 CEC Appliance Efficiency Standards.

## 040006-OffLrg-Run20
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 040006-OffLrg-Run20 |  |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 040006-OffLrg-Run20.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Complete |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
[9 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Basement Floor | BsmntZnPSZ AirSys | New |  | Basement Floor/Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Bottom Floor | BaseAirSys6-Bot | New |  | Bottom Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys6-Mid | New |  | Mid Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Hi Floor | BaseAirSys6-Hi | New |  | Hi Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys6-Top | New |  | Top Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BsmntZnPSZ AirSys | BsmntZnCoolingCoil | New |  | DirectExpansion |  | 11.4 |  | 11.517 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys6-Bot | BaseSys6 CoilClg-Bot | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Mid | BaseSys6 CoilClg-Mid | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Hi | BaseSys6 CoilClg-Hi | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Top | BaseSys6 CoilClg-Top | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating |  |  | HotWater
Mid VAV | Mid VAV CoilHeating |  |  | HotWater
Hi VAV | Hi VAV CoilHeating |  |  | HotWater
Top VAV | Top VAV CoilHeating |  |  | HotWater
BottomVAV | (All ReheatCoils) |  |  | HotWater
Mid VAV | (All ReheatCoils) |  |  | HotWater
Hid VAV | (All ReheatCoils) |  |  | HotWater
Top VAV | (All ReheatCoils) |  |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Basement Floor | BsmntZnSupplyFan | New |  | ConstantVolume |  | StaticPressure |  | 190000 |  | 169.0293 |  | 0.62 |  | 3.5 |  | 200 |  | 0.962
Bottom Floor | BaseSys6 Fan-Bot | New |  | VariableSpeedDrive |  | StaticPressure |  | 38624.3 |  | 44.1787 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Mid Floor | BaseSys6 Fan-Mid | New |  | VariableSpeedDrive |  | StaticPressure |  | 40232.3 |  | 46.018 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Hi Floor | BaseSys6 Fan-Hi | New |  | VariableSpeedDrive |  | StaticPressure |  | 40232.3 |  | 46.018 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Top Floor | BaseSys6 Fan-Top | New |  | VariableSpeedDrive |  | StaticPressure |  | 42188.3 |  | 48.2553 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BsmntZnPSZ AirSys |  |  |  | NoEconomizer |  | UNDEFINED
BaseAirSys6-Bot |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Mid |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Hi |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Top |  |  |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Basement Floor | Conditioned |  |  | DataClgSetpt |  | DataHtgSetpt
Bottom, Mid, Hi and Top Floors | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 2887230 |  | 0.82 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Centrifugal |  | Electric |  | Fluid |  | 5268800 |  | 5.86 (0.6 kW/ton, 20 EER) |  | 0.4 |  | 0.1
Base Chlr-2 | BaseChWSystem | New |  | Centrifugal |  | Electric |  | Fluid |  | 5268800 |  | 5.86 (0.6 kW/ton, 20 EER) |  | 0.4 |  | 0.1
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Base Chlr-2 | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment |  |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 144.31 |  | 2.74 (19 W/gpm) |  | 5 |  | 63.2 |  | 0.895 | - | -
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 144.31 |  | 2.74 (19 W/gpm) |  | 5 |  | 63.2 |  | 0.895 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 1229.88 |  | 16.01 (13 W/gpm) |  | 20 |  | 45 |  | 0.93 | - | -
Base CW Pump-2 | Base Tower-2 | New |  | OnDemand |  | ConstantSpeed |  | 1229.88 |  | 16.01 (13 W/gpm) |  | 20 |  | 45 |  | 0.93 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 526.68 |  | 8.15 (15.5 W/gpm) |  | 15 |  | 53.172 |  | 0.924 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
Base ChW Pump-2 | Base Chlr-2 | New |  | OnDemand |  | VariableSpeed |  | 526.68 |  | 8.15 (15.5 W/gpm) |  | 15 |  | 53.172 |  | 0.924 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 6151760 |  | 1229.88 |  | 20.5 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Base Tower-2 | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 6151760 |  | 1229.88 |  | 20.5 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Baseline
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys6 | New |  | Bottom Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys6-2 | New |  | Mid Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Hi Floor | BaseAirSys6-3 | New |  | Hi Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys6-4 | New |  | Top Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Basement Floor | BaseAirSys10 | New |  | Basement Floor/Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys6 | BaseSys6 CoilClg | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-2 | BaseSys6 CoilClg-2 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-3 | BaseSys6 CoilClg-3 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-4 | BaseSys6 CoilClg-4 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys10 | BaseSys10 CoilClg | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys6 | BaseSys6 CoilHtg |  |  | HotWater
BaseAirSys6-2 | BaseSys6 CoilHtg-2 |  |  | HotWater
BaseAirSys6-3 | BaseSys6 CoilHtg-3 |  |  | HotWater
BaseAirSys6-4 | BaseSys6 CoilHtg-4 |  |  | HotWater
BaseAirSys6/6-2/6-3/6-4 | (All BaseVAVReheatCoils) |  |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx
Bottom Floor | BaseSys6 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 38114 |  | 43.5951 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945 | - | -
Mid Floor | BaseSys6 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 32044.4 |  | 36.6526 |  | 0.62 |  | 4.5 |  | 40 |  | 0.941 | - | -
Hi Floor | BaseSys6 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 32026.6 |  | 36.6323 |  | 0.62 |  | 4.5 |  | 40 |  | 0.941 | - | -
Top Floor | BaseSys6 Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 27676.7 |  | 31.6568 |  | 0.62 |  | 4.5 |  | 40 |  | 0.941 | - | -
Basement Floor | BaseSys10 Fan | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 142672 |  | 89.4494 |  | 0.62 |  | 2.4666 |  | 75 |  | 0.954 |  | 0.49
Bottom Floor | BaseRelief Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 36196.3 |  | 11.4084 |  | 0.5 |  | 1 |  | 15 |  | 0.924 | - | -
Mid Floor | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 22456.2 |  | 7.0778 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917 | - | -
Hi Floor | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 22438.3 |  | 7.0722 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917 | - | -
Top Floor | BaseRelief Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 25759.1 |  | 8.1188 |  | 0.5 |  | 1 |  | 10 |  | 0.917 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseSys6 OACtrl |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-2 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-3 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-4 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys10 OACtrl |  | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Basement Floor | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
Bottom, Mid, Hi and Top Floors | Conditioned |  |  | DataClgSetpt |  | DataHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 2073590 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Centrifugal |  | Electric |  | Fluid |  | 6631440 |  | 5.96 (0.59 kW/ton, 20.34 EER) | - | - |  | 0.1
Base Chlr-2 | BaseChWSystem | New |  | Centrifugal |  | Electric |  | Fluid |  | 6631440 |  | 5.96 (0.59 kW/ton, 20.34 EER) | - | - |  | 0.1
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Base Chlr-2 | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment |  |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 103.64 |  | 1.97 (19 W/gpm) |  | 3 |  | 63.2 |  | 0.895 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 1548.21 |  | 20.02 (12.9 W/gpm) |  | 30 |  | 45 |  | 0.936 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 662.892 |  | 10.92 (16.5 W/gpm) |  | 15 |  | 56.5786 |  | 0.924 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 103.64 |  | 1.97 (19 W/gpm) |  | 3 |  | 63.2 |  | 0.895 | - | -
Base ChW Pump-2 | Base Chlr-2 | New |  | OnDemand |  | VariableSpeed |  | 662.892 |  | 10.92 (16.5 W/gpm) |  | 15 |  | 56.5786 |  | 0.924 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base CW Pump-2 | Base Tower-2 | New |  | OnDemand |  | ConstantSpeed |  | 1548.21 |  | 20.02 (12.9 W/gpm) |  | 30 |  | 45 |  | 0.936 | - | -
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 7744000 |  | 1548.21 |  | 25.804 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Base Tower-2 | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 7744000 |  | 1548.21 |  | 25.804 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Note on P73: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on N75: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412
Note on N76: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412
Note on L87: Sandeep: Pump Motor Power-Per-Unit-Flow: 19 W/gpm for heating hot water and service hot water pumps
Note on L88: Sandeep: Pump Motor Power-Per-Unit-Flow: 19 W/gpm for heating hot water and service hot water pumps
Note on L89: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P89 for the calculation method Impeller Efficiency: 0.7
Note on L90: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P90 for the calculation method Impeller Efficiency: 0.7
Note on L91: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P91, for the calculation method Impeller Efficiency: 0.7.
Note on L92: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P92, for the calculation method Impeller Efficiency: 0.7.
Note on H130: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N130: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P130: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R130: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T130: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.
Note on F160: Sandeep: The boiler is sized to be 25% larger than the peak loads of the baseline building. Baseline boilers shall be sized using weather files containing 99.6% heating design temperatures and 0.5% dry-bulb and 1% wet-bulb cooling design temperatures.
Note on P165: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on R165: Sandeep: The standard design 'Chiller Min Unloading Ratio' is determined based on the 'Chiller Type'. Screw = 15% Centrifugal = 10% See ACM ' Default Minimum Unloading Ratios Table-50 for further details
Note on F167: Sandeep: The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons.
Note on H167: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on J167: Sandeep: Standard Design The baseline chiller is always assumed to have a water-cooled condenser, although the chiller type will change depending on the design capacity.
Note on L167: Sandeep: 151106: Auto-sized. The full load output of the chiller operating at rating temperatures and flows including adjustment for pump heat and the project sizing ratio.
Note on N167: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412 Chiller Type: Centrifugal, Path B Efficiency Cap <150 Tons = 0.639 kW/Ton Cap <300 Tons = 0.639 kW/Ton Cap <600 Tons = 0.600 kW/Ton Cap >=600 Tons = 0.590 kW/Ton Use the minimum efficiency requirements from Tables 110.2-D Path B. If Chiller Type is Screw, use the efficiency for Positive Displacement chillers from Table 110.2-D.
Note on F168: Sandeep: 'The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons.
Note on H168: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on J168: Sandeep: Standard Design The baseline chiller is always assumed to have a water-cooled condenser, although the chiller type will change depending on the design capacity.
Note on L168: Sandeep: 151106: Auto-sized. The full load output of the chiller operating at rating temperatures and flows including adjustment for pump heat and the project sizing ratio.
Note on N168: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412 Chiller Type: Centrifugal, Path B Efficiency Cap <150 Tons = 0.639 kW/Ton Cap <300 Tons = 0.639 kW/Ton Cap <600 Tons = 0.600 kW/Ton Cap >=600 Tons = 0.590 kW/Ton Use the minimum efficiency requirements from Tables 110.2-D Path B. If Chiller Type is Screw, use the efficiency for Positive Displacement chillers from Table 110.2-D.
Note on F177: Sandeep: The baseline system pumps are assumed to operate in On-Demand mode. The chilled water and condenser pumps are tied to the chiller operation, cycling on and off with the chiller, and the heating hot water pumps are tied to the boiler operation.
Note on H177: Sandeep: The chilled water pumps shall be modeled as variable-speed, variable flow, and the condenser water pumps shall be modeled as fixed speed. The hot water pumps shall be modeled as fixed-speed, variable flow, riding the curve.
Note on J177: Sandeep: Please refer to the reporting file - '040006-OffLrg-Run20 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formulae commented in the cells below
Note on N177: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on R177: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table-31 available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on J179: Sandeep: Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on L179: Sandeep: Pump Motor Power-Per-Unit-Flow: 19 W/gpm for heating hot water and service hot water pumps
Note on P179: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L179) Impeller Efficiency: 0.7
Note on J180: Sandeep: Cooling Tower Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 10 degF
Note on L180: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow capacity: Autosized Total Head: Refer to P182), for the calculation method Impeller Efficiency:0.7
Note on P180: Sandeep: For condenser water pumps, Head: 45 ft
Note on J181: Sandeep: Chiller Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 20 degF
Note on L181: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P185, for the calculation method Impeller Efficiency: 0.7.
Note on P181: Sandeep: For chilled water pumps, 40 ft plus an additional allowance of 0.03 ft/ton, but not to exceed 100 ft. (See formula in the cell)
Note on J182: Sandeep: Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on L182: Sandeep: Pump Motor Power-Per-Unit-Flow: 19 W/gpm for heating hot water and service hot water pumps
Note on P182: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L182) Impeller Efficiency: 0.7
Note on J183: Sandeep: Chiller Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 20 degF
Note on L183: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow Capacity: Autosized, Total Head: Refer cell - P186, for the calculation method Impeller Efficiency: 0.7.
Note on P183: Sandeep: For chilled water pumps, 40 ft plus an additional allowance of 0.03 ft/ton, but not to exceed 100 ft. (See formula in the cell)
Note on J184: Sandeep: Cooling Tower Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 10 degF
Note on L184: Sandeep: Pump power is calculated using the formula below - (Flow Capacity*Total Head/3960/(Impeller Efficiency*MtrEff)*745.6/1000) where, Flow capacity: Autosized Total Head: Refer to P183), for the calculation method Impeller Efficiency:0.7
Note on P184: Sandeep: For condenser water pumps, Head: 45 ft
Note on N189: Sandeep: The cooling tower fan horsepower is 60 gpm/hp.
Note on N190: Sandeep: The cooling tower fan horsepower is 60 gpm/hp.

## 080006-Whse-Run21 (hidden)
General Details |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 080006-Whse-Run21 |  | Model Revision no. | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006-Whse-Run21.cibd |  | Version of Ruleset (Trunk rev. No.) | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse |  | Date Tested | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC |  | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [5 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name |  | Type | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  | AirSys:Type | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Zone1 Office Thermal Zone | OfficeZnPSZAirSys |  | SZAC | WarehouseHVACAvail |  | 55 |  | 95 |  | NoSATControl
Zone2 Fine Storage Thermal Zone | FineSto_ZnPSZAirSys |  | HV | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
Zone3 Bulk Storage Thermal Zone | BulkSto_ZnPSZAirSys |  | HV | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name |  | Type | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  | CoilClg:Type | CoilClg:DXEER |  | CoilClg:DXIEER |  |  |  | (DXEIR_fTempCrvRef) | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
OfficeZnPSZAirSys | OfficeZnCoolingCoil |  | DirectExpansion | 11.2 |  | 11.4 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXEIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name |  | Type | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
OfficeZnPSZAirSys | OfficeZnHeatingCoil |  | Furnace (Natural Gas) | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
FineSto_ZnPSZAirSys | FineSto_ZnHeatingCoil |  | Furnace (Natural Gas) | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
BulkSto_ZnPSZAirSys | BulkSto_ZnHeatingCoil |  | Furnace (Natural Gas) | 0.81 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name |  | Control Method | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
Fan:SysServed | Fan: |  | Fan:CtrlMthd | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
OfficeZnPSZAirSys | OfficeZnSupplyFan |  | Constant Volume | BreakHorsePower |  | 2 | - | - | - | - | 5 | 0.89
FineSto_ZnPSZAirSys | FineSto_ZnSupplyFan |  | Constant Volume | BreakHorsePower |  | 5.5 | - | - | - | - | 10 | 0.92
BulkSto_ZnPSZAirSys | BulkSto_ZnSupplyFan |  | Constant Volume | BreakHorsePower |  | 20 | - | - | - | - | 30 | 0.92
Thermal Zone - Name | Conditioning Type |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Zone1 Office Thermal Zone | Conditioned |  | WarehouseClgSetPt | WarehouseHtgSetPt
Zone2 Fine Storage Thermal Zone | Conditioned | - | - | WarehouseHtgSetPt
Zone3 Bulk Storage Thermal Zone | Conditioned | - | - | WarehouseHtgSetPt
Baseline
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name |  | Type | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  | AirSys:Type | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Zone1 Office Thermal Zone | BaseAirSys3 |  | SZAC | WarehouseHVACAvail |  | 55 |  | 95 |  | NoSATControl
Zone2 Fine Storage Thermal Zone | BaseAirSys9 |  | HV | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
Zone3 Bulk Storage Thermal Zone | BaseAirSys9-2 |  | HV | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name |  | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  | CoilClg:Type | CoilClg:DXEER |  |  |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg |  | DirectExpansion | 11 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name |  | Type | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys9 | BaseSys9 CoilHtg |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys9-2 | BaseSys9 CoilHtg-2 |  | Furnace (Natural Gas) | 0.8 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name |  | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
Fan:SysServed | Fan: |  | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan |  | Constant Volume | StaticPressure |  | 3074.22 |  | 2.4224 |  | 0.6 | 3 | 3 | 0.895
BaseAirSys9 | BaseSys9 Fan |  | Constant Volume | StaticPressure | XX | 6920.69 |  | 5.4532 |  | 0.6 | 3 | 7.5 | 0.917
BaseAirSys9-2 | BaseSys9 Fan-2 |  | Constant Volume | StaticPressure |  | 30844.7 |  | 27.4403 |  | 0.62 | 3.5 | 30 | 0.936
BaseAirSys3 | BaseRelief Fan |  | VariableSpeedDrive | StaticPressure |  | 2946.74 |  | 0.87071 |  | 0.4 | 0.75 | 1 | 0.855
Thermal Zone - Name | Conditioning Type |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Zone1 Office Thermal Zone | Conditioned |  | WarehouseClgSetPt | WarehouseHtgSetPt
Zone2 Fine Storage Thermal Zone | Conditioned | - | - | WarehouseHtgSetPt
Zone3 Bulk Storage Thermal Zone | Conditioned | - | - | WarehouseHtgSetPt
Note on E15: Sandeep: 151214_v3d: Changed from SZAC to HV. (no changes in energy results or .xml or .idf files were seen)
Note on G54: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on G66: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on M66: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on O66: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on Q66: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on S66: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.

## 070015-HotSml-Run22
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 070015-HotSml-Run22 |  |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 070015-HotSml-Run22.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | NewComplete | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Common Areas: Floor 1 | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 2 | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 3 | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 4 | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Zone: KitchenFlr1 | KitchenMUA | New |  | Zone: KitchenFlr1 |  | SZAC |  | RestaurantHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl
GuestRoom101 Thermal Zone | GuestRoom101_Pkdg1Ph-SZAC | New |  | Residential Unit: GuestRoom 101 |  | SZAC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
GuestRoom102 Thermal Zone | GuestRoom102_Split1Ph-SZAC | New |  | Residential Unit: GuestRoom 102 |  | SZAC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
GuestRoom103 Thermal Zone | GuestRoom103_Pkgd1Ph-SZHP | New |  | Residential Unit: GuestRoom 103 |  | SZHP |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
GuestRoom104 Thermal Zone | GuestRoom104_Split1Ph-SZHP | New |  | Residential Unit: GuestRoom 104 |  | SZHP |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
Residential Units: All Floors (other than zones above) | Residential Units: FPFC (All) (other than zones above) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
Zone: KitchenFlr1 | KitchenExhaust | New |  | Zone: KitchenFlr1 |  | Exhaust |  | RestaurantHVACAvail | - | - | - | - |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 9.9 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 11 |  | 11.2 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
GuestRoom101_Pkdg1Ph-SZAC | GuestRoom101_Dx CoilClg | New |  | DirectExpansion |  | 10.8 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
GuestRoom102_Split1Ph-SZAC | GuestRoom102_Dx CoilClg | New |  | DirectExpansion |  | 12.2 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
GuestRoom103_Pkgd1Ph-SZHP | GuestRoom103_Dx CoilClg | New |  | DirectExpansion |  | 11.4072 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
GuestRoom104_Split1Ph-SZHP | GuestRoom104_Dx CoilClg | New |  | DirectExpansion |  | 11.4072 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Residential Units: FPFC (All) | Residential Units: FPFC CoilClg (All) | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | - | - | -
KitchenMUA | Kitchen CoilClg | New |  | DirectExpansion |  | 10.8446 | - | - | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
GuestRoom101_Pkdg1Ph-SZAC | GuestRoom101_Furnace Htg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
GuestRoom102_Split1Ph-SZAC | GuestRoom102_Furnace Htg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
GuestRoom103_Pkgd1Ph-SZHP | GuestRoom103_HP CoilHtg | New |  | Electric | - | - | - | - | - | -
GuestRoom104_Split1Ph-SZHP | GuestRoom104_HP CoilHtg | New |  | Electric | - | - | - | - | - | -
Residential Units: FPFC (All) | Residential Units: FPFC CoilHtg (All) | New |  | HotWater | - | - | - | - | - | -
KitchenMUA | KitchenCoilHtg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 12396.3 |  | 12.6035 |  | 0.62 |  | 4 |  | 15 |  | 0.924
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1646.78 |  | 1.5571 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1674.51 |  | 1.5833 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1721.44 |  | 1.6277 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Residential Units: Floor1 | GuestRoom101_Supply Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom102_Supply Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom103_Supply Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom104_Supply Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom105_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom201_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom202_205_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom206_208_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom209_212_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom213_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom214_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom215_218_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom219_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom220_223_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom224_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom301_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom302_305_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom306_308_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom309_312_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom313_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom314_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom315_318_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom319_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom320_323_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom324_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom401_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom402_405_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom406_408_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom409_412_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom413_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom414_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom415_418_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom419_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom420_423_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom424_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Zone: KitchenFlr1 | Kitchen Fan | New |  | ConstantVolume |  | StaticPressure |  | 864.069 |  | 0.68085 |  | 0.5 |  | 2.5 |  | 0.75 |  | 0.855
Zone: KitchenFlr1 | KitchExh Fan | New |  | ConstantVolume |  | StaticPressure |  | 1050 |  | 0.49641 |  | 0.5 |  | 1.5 |  | 0.5 |  | 0.855
AirSystem - Name | OA - Control Name | Status |  | Economizer Control |  | Economizer Integration
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
KitchenMUA | Kitchen OAControl | New |  | DifferentialDryBulb |  | Integrated
Ventilation and Thermostat Schedules
Thermal Zone - Name | Conditioning Type | Status |  | Space Floor Area (ft2) |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Exhaust Flow (cfm) | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  |  |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZn:VentPerAreaSim | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
CorridorFlr1 Thermal Zone | Conditioned | New |  | 1620 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 8.1 |  | 0 |  | 0.15 |  | 243 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr2 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr3 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr4 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
EmployeeLoungeFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
ExerciseCenterFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontLoungeFlr1 Thermal Zone | Conditioned | New |  | 1755.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 125.4 |  | 15 |  | 0.15 |  | 1881 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontOfficeFlr1 Thermal Zone | Conditioned | New |  | 1404 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 7 |  | 0 |  | 0.15 |  | 211 | - | - | OfficeClgSetpt | OfficeHtgSetpt
LaundryRoomFlr1 Thermal Zone | Conditioned | New |  | 1053 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 5.3 |  | 0 |  | 0.15 |  | 158 | - | - | OfficeClgSetpt | OfficeHtgSetpt
MechanicalRoomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 3 |  | 0.5 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
KitchenFlr1 Thermal Zone | Conditioned | New |  | 864.1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.2 |  | 0 |  | 0.15 |  | 130 |  | 1050 | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr1 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr2 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr3 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr4 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr1 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr2 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr3 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr4 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RestroomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
Space Name | Conditioning Type | Status |  | Thermal Zone - Name |  | Space Function |  | Space Floor Area (ft2) |  | Number of Residential Living or Hotel/Motel units in a modeled space |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerArea (cfm/ft2) | Calculated Ventilation (cfm) | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
Spc:Name | ThrmlZn:Type |  |  | ThrmlZn:Name |  | SpcFunc |  |  |  | Spc:ResLivingUnitCnt |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerAreaSim |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
GuestRoom101 | Conditioned | New |  | GuestRoom101 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom102 | Conditioned | New |  | GuestRoom102 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom103 | Conditioned | New |  | GuestRoom103 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom104 | Conditioned | New |  | GuestRoom104 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom105 | Conditioned | New |  | GuestRoom105 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom201 | Conditioned | New |  | GuestRoom201 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom202_205 | Conditioned | New |  | GuestRoom202_205 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom206_208 | Conditioned | New |  | GuestRoom206_208 Thermal Zone |  | Hotel/Motel Guest Room |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | 0.079358 | 90 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom209_212 | Conditioned | New |  | GuestRoom209_212 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom213 | Conditioned | New |  | GuestRoom213 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom214 | Conditioned | New |  | GuestRoom214 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom215_218 | Conditioned | New |  | GuestRoom215_218 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom219 | Conditioned | New |  | GuestRoom219 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom220_223 | Conditioned | New |  | GuestRoom220_223 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom224 | Conditioned | New |  | GuestRoom224 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom301 | Conditioned | New |  | GuestRoom301 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom302_305 | Conditioned | New |  | GuestRoom302_305 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom306_308 | Conditioned | New |  | GuestRoom306_308 Thermal Zone |  | Hotel/Motel Guest Room |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | 0.079358 | 90 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom309_312 | Conditioned | New |  | GuestRoom309_312 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.085464 | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom313 | Conditioned | New |  | GuestRoom313 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom314 | Conditioned | New |  | GuestRoom314 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom315_318 | Conditioned | New |  | GuestRoom315_318 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom319 | Conditioned | New |  | GuestRoom319 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom320_323 | Conditioned | New |  | GuestRoom320_323 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | 0.08547 | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom324 | Conditioned | New |  | GuestRoom324 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | 0.08547 | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom401 | Conditioned | New |  | GuestRoom401 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed | - | - |  | 1 |  | 0.074245 | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom402_405 | Conditioned | New |  | GuestRoom402_405 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404.1 |  | 4 |  | Forced |  | Sum |  | Fixed | - | - |  | 4 |  | 0.074244 | 104.246 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom406_408 | Conditioned | New |  | GuestRoom406_408 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1134.1 |  | 3 |  | Forced |  | Sum |  | Fixed | - | - |  | 3 |  | 0.073226 | 83.046 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom409_412 | Conditioned | New |  | GuestRoom409_412 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404.1 |  | 4 |  | Forced |  | Sum |  | Fixed | - | - |  | 4 |  | 0.074244 | 104.246 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom413 | Conditioned | New |  | GuestRoom413 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed | - | - |  | 1 |  | 0.074245 | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom414 | Conditioned | New |  | GuestRoom414 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed | - | - |  | 1 |  | 0.074245 | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom415_418 | Conditioned | New |  | GuestRoom415_418 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404 |  | 4 |  | Forced |  | Sum |  | Fixed | - | - |  | 4 |  | 0.074245 | 104.24 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom419 | Conditioned | New |  | GuestRoom419 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed | - | - |  | 1 |  | 0.074245 | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom420_423 | Conditioned | New |  | GuestRoom420_423 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404 |  | 4 |  | Forced |  | Sum |  | Fixed | - | - |  | 4 |  | 0.074245 | 104.24 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom424 | Conditioned | New |  | GuestRoom424 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Sum |  | Fixed | - | - |  | 1 |  | 0.074245 | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 363000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Electric |  | Fluid |  | 348000 |  | 4.4 (0.8 kW/ton, 15 EER) |  | 0.6 |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Water-Side Economizer Name |  | Status |  | Type |  | Economizer Integration
(HX:Name) |  |  |  | (HX:Type) |  | (HX:EconoIntegration)
WS-Economizer |  | New |  | CounterFlow |  | Integrated
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 18.14 |  | 0.34 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 18.14 |  | 0.34 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 85.4 |  | 1.2 (14 W/gpm) |  | 1.5 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 34.79 |  | 0.45 (12.9 W/gpm) |  | 0.75 |  | 40.87 |  | 0.855 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 427163 |  | 85.4 |  | 1.42 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Baseline
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Common Areas: Floor 1 | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 2 | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 3 | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 4 | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Zone: KitchenFlr1 | BaseAirSys13 | New |  | Zone: KitchenFlr1 |  | SZAC |  | RestaurantHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | ZnSys:ClgCtrl
Residential Units: All Floors | Residential Units: FPFC (All) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 11 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys13 | BaseSys13 CoilClg | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys2 | Residential Units: BaseSys2 CoilClg (All) | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys13 | BaseSys13 CoilHtg | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys2 | Residential Units: BaseSys2 CoilHtg (All) | New |  | HotWater | - | - |  | 1.25 | - | -
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 8327.22 |  | 7.6551 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | -
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1488.5 |  | 1.4074 |  | 0.5 |  | 3 |  | 1.5 |  | 0.865 | - | -
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1494.68 |  | 1.4133 |  | 0.5 |  | 3 |  | 1.5 |  | 0.865 | - | -
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1743.07 |  | 1.6482 |  | 0.5 |  | 3 |  | 2 |  | 0.865 | - | -
Zone: KitchenFlr1 | BaseSys13 Fan | New |  | ConstantVolume |  | Static Pressure |  | 862.065 |  | 0.67927 |  | 0.5 |  | 2.5 |  | 0.75 |  | 0.855 | - | -
Residential Units: All Floors | BaseSys2 Fan | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 182.72 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-2 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 185.56 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-3 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 179.45 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-4 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 171.63 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-5 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 172.22 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-6 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 223.55 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-7 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 163.53 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-8 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 162.613 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-9 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 150.352 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-10 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 152.02 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-11 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 145.4 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-12 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 142.477 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-13 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 144.9 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-14 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 141.738 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-15 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 143.77 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-16 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 212.71 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-17 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 153.777 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-18 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 163.7 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-19 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 151.47 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-20 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 152.33 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-21 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 146.07 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-22 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 145.145 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-23 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 144.35 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-24 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 143.735 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-25 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 142.84 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-26 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 240.28 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-27 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 176.135 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-28 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 195.507 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-29 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 175.133 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-30 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 175.36 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-31 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 165.19 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-32 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 163.68 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-33 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 163.4 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-34 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 161.785 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-35 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 161.36 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Common Areas: Floor 1 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 7926.25 |  | 2.3421 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | -
Common Areas: Floor 2 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 1381.85 |  | 0.40831 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
Common Areas: Floor 3 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 1388.02 |  | 0.41014 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
Common Areas: Floor 4 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 1636.41 |  | 0.48353 |  | 0.4 |  | 0.75 |  | 0.5 |  | 0.855 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys13 | BaseSys13 OACtrl | New | - | - | - | -
BaseAirSys2 | - | New | - | - | - | -
Ventilation and Thermostat Schedules
Thermal Zone - Name | Conditioning Type | Status |  | Space Floor Area (ft2) |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Calculated Ventilation (cfm) |  | Exhaust Flow (cfm) | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  |  |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZn:VentPerAreaSim | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
CorridorFlr1 Thermal Zone | Conditioned | New |  | 1620 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 8.1 |  | 0 |  | 0.15 |  | 243 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr2 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr3 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
CorridorFlr4 Thermal Zone | Conditioned | New |  | 1350 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 6.8 |  | 0 |  | 0.15 |  | 203 | - | - | OfficeClgSetpt | OfficeHtgSetpt
EmployeeLoungeFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
ExerciseCenterFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontLoungeFlr1 Thermal Zone | Conditioned | New |  | 1755.1 |  | Forced |  | Maximum |  | CO2Sensors |  | 142.9 |  | 125.4 |  | 15 |  | 0.15 |  | 1881 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontOfficeFlr1 Thermal Zone | Conditioned | New |  | 1404 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 7 |  | 0 |  | 0.15 |  | 211 | - | - | OfficeClgSetpt | OfficeHtgSetpt
LaundryRoomFlr1 Thermal Zone | Conditioned | New |  | 1053 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 5.3 |  | 0 |  | 0.15 |  | 158 | - | - | OfficeClgSetpt | OfficeHtgSetpt
MechanicalRoomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 3 |  | 0.5 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
KitchenFlr1 Thermal Zone | Conditioned | New |  | 864.1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.2 |  | 0 |  | 0.15 |  | 130 |  | 1050 | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr1 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr2 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr3 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStairsFlr4 Thermal Zone | Conditioned | New |  | 216 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr1 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr2 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr3 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
FrontStorageFlr4 Thermal Zone | Conditioned | New |  | 135 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 0.7 |  | 0 |  | 0.15 |  | 20 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStairsFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr1 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr2 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr3 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RearStorageFlr4 Thermal Zone | Conditioned | New |  | 216.1 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.1 |  | 0 |  | 0.15 |  | 32 | - | - | OfficeClgSetpt | OfficeHtgSetpt
RestroomFlr1 Thermal Zone | Conditioned | New |  | 351 |  | Forced |  | Maximum |  | Fixed |  | 10 |  | 1.8 |  | 0 |  | 0.15 |  | 53 | - | - | OfficeClgSetpt | OfficeHtgSetpt
Space Name | Conditioning Type | Status |  | Thermal Zone - Name |  | Space Function |  | Space Floor Area (ft2) |  | Number of Residential Living or Hotel/Motel units in a modeled space |  | Ventilation Source |  | Specification Method |  | Control |  | People Density (ppl/1000ft2) |  | People (total number) |  | Infiltration Method | Required Ventilation - Simulated as Infiltration (cfm) | Infiltration Schedule | Exhaust Flow (cfm) | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
Spc:Name | ThrmlZn:Type |  |  | ThrmlZn:Name |  | SpcFunc |  |  |  | Spc:ResLivingUnitCnt |  | ThrmlZn:VentSrc |  | (VentSpecMthd) |  | (VentCtrlMthd) |  | OccDens |  |  |  | (InfMthd index="1") | (DsgnInfRt index="1") | (InfSchRef index="1") | ThrmlZn:ExhFlowSim | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
GuestRoom101 | Conditioned | New |  | GuestRoom101 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom102 | Conditioned | New |  | GuestRoom102 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom103 | Conditioned | New |  | GuestRoom103 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom104 | Conditioned | New |  | GuestRoom104 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom105 | Conditioned | New |  | GuestRoom105 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom201 | Conditioned | New |  | GuestRoom201 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom202_205 | Conditioned | New |  | GuestRoom202_205 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom206_208 | Conditioned | New |  | GuestRoom206_208 Thermal Zone |  | Hotel/Motel Guest Room |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | FlowSpace | 90 | On | 90 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom209_212 | Conditioned | New |  | GuestRoom209_212 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom213 | Conditioned | New |  | GuestRoom213 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom214 | Conditioned | New |  | GuestRoom214 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom215_218 | Conditioned | New |  | GuestRoom215_218 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom219 | Conditioned | New |  | GuestRoom219 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom220_223 | Conditioned | New |  | GuestRoom220_223 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom224 | Conditioned | New |  | GuestRoom224 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom301 | Conditioned | New |  | GuestRoom301 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom302_305 | Conditioned | New |  | GuestRoom302_305 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom306_308 | Conditioned | New |  | GuestRoom306_308 Thermal Zone |  | Hotel/Motel Guest Room |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 2.84 |  | FlowSpace | 90 | On | 90 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom309_312 | Conditioned | New |  | GuestRoom309_312 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom313 | Conditioned | New |  | GuestRoom313 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom314 | Conditioned | New |  | GuestRoom314 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom315_318 | Conditioned | New |  | GuestRoom315_318 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom319 | Conditioned | New |  | GuestRoom319 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom320_323 | Conditioned | New |  | GuestRoom320_323 Thermal Zone |  | Hotel/Motel Guest Room |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 3.51 |  | FlowSpace | 120 | On | 120 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom324 | Conditioned | New |  | GuestRoom324 Thermal Zone |  | Hotel/Motel Guest Room |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed |  | 5 |  | 0.88 |  | FlowSpace | 30 | On | 30 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom401 | Conditioned | New |  | GuestRoom401 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 1 |  | FlowSpace | 26.06 | On | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom402_405 | Conditioned | New |  | GuestRoom402_405 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed | - | - |  | 4 |  | FlowSpace | 104.246 | On | 104.246 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom406_408 | Conditioned | New |  | GuestRoom406_408 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1134.1 |  | 3 |  | Forced |  | Maximum |  | Fixed | - | - |  | 3 |  | FlowSpace | 83.046 | On | 83.046 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom409_412 | Conditioned | New |  | GuestRoom409_412 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404.1 |  | 4 |  | Forced |  | Maximum |  | Fixed | - | - |  | 4 |  | FlowSpace | 104.246 | On | 104.246 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom413 | Conditioned | New |  | GuestRoom413 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 1 |  | FlowSpace | 26.06 | On | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom414 | Conditioned | New |  | GuestRoom414 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 1 |  | FlowSpace | 26.06 | On | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom415_418 | Conditioned | New |  | GuestRoom415_418 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed | - | - |  | 4 |  | FlowSpace | 104.24 | On | 104.24 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom419 | Conditioned | New |  | GuestRoom419 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 1 |  | FlowSpace | 26.06 | On | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom420_423 | Conditioned | New |  | GuestRoom420_423 Thermal Zone |  | High-Rise Residential Living Spaces |  | 1404 |  | 4 |  | Forced |  | Maximum |  | Fixed | - | - |  | 4 |  | FlowSpace | 104.24 | On | 104.24 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
GuestRoom424 | Conditioned | New |  | GuestRoom424 Thermal Zone |  | High-Rise Residential Living Spaces |  | 351 |  | 1 |  | Forced |  | Maximum |  | Fixed | - | - |  | 1 |  | FlowSpace | 26.06 | On | 26.06 | ResidentialLivingClgSetpt | ResidentialLivingHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 247826 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Chiller Fuel Type |  | Condenser Type |  | Chiller Capacity (Btu/h) |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:FuelSrc |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Electric |  | Fluid |  | 315973 |  | 4.4 (0.8 kW/ton) 15 EER | - | - |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 12.39 |  | 0.24 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 77.541 |  | 1.09 (14 W/gpm) |  | 1.5 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 31.585 |  | 0.41 (12.8 W/gpm) |  | 0.5 |  | 40.7899 |  | 0.855 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 12.39 |  | 0.24 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Rated Capacity |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:ModCtrl |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 387850 |  | 77.54 |  | 1.3 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Note on B23: Sandeep: 150630_SDS: Added in cycle v3c.
Note on P118: Sandeep: Multiplier of 0.5 has been added.
Note on V150: Sandeep: Multiplier of 0.5 has been added.
Note on P195: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on N197: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412
Note on H239: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H263: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N263: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P263: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R263: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T263: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.
Note on P322: Sandeep: Multiplier of 0.5 has been added.
Note on V354: Sandeep: Multiplier of 0.5 has been added.
Note on F394: Sandeep: The boiler is sized to be 25% larger than the peak loads of the baseline building. Baseline boilers shall be sized using weather files containing 99.6% heating design temperatures and 0.5% dry-bulb and 1% wet-bulb cooling design temperatures.
Note on F399: Sandeep: The baseline building chiller is based on the design capacity of the standard design <= 300 tons - 1 Water Cooled Screw Chiller >300, <600 tons - 2 Water Cooled Screw Chiller >=600 tons - A minimum of two Water-cooled centrifugal chillers, sized to keep the unit size below 800 tons.
Note on H399: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on J399: Sandeep: Standard Design The baseline chiller is always assumed to have a water-cooled condenser, although the chiller type will change depending on the design capacity.
Note on L399: Sandeep: Auto-sized. The full load output of the chiller operating at rating temperatures and flows including adjustment for pump heat and the project sizing ratio.
Note on P399: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on R399: Sandeep: The standard design 'Chiller Min Unloading Ratio' is determined based on the 'Chiller Type'. Screw = 15% See ACM ' Default Minimum Unloading Ratios Table-50 for further details
Note on H401: Sandeep: Standard Design The baseline chiller fuel source is always Electric.
Note on N401: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412
Note on F409: Sandeep: The baseline system pumps are assumed to operate in On-Demand mode. The chilled water and condenser pumps are tied to the chiller operation, cycling on and off with the chiller, and the heating hot water pumps are tied to the boiler operation.
Note on H409: Sandeep: The chilled water pumps shall be modeled as variable-speed, variable flow, and the condenser water pumps shall be modeled as fixed speed. The hot water pumps shall be modeled as fixed-speed, variable flow, riding the curve.
Note on J409: Sandeep: Please refer to the reporting file - '070015-HotSml-Run22 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formulae commented in the cells below
Note on N409: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on R409: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table-31 available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on J411: Sandeep: Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on P411: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L411) Impeller Efficiency: 0.7
Note on J412: Sandeep: Cooling Tower Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 10 degF
Note on P412: Sandeep: For condenser water pumps, Head: 45 ft
Note on J413: Sandeep: Chiller Rated Capacity/500.19/Design Supply Water DeltaT where, the cooling capacity of the heat rejection device is calculated at full load and rated conditions, adjusted for pump heat and the project cooling sizing ratio. The Design Supply Water DeltaT for cooling towers is 20 degF
Note on P413: Sandeep: For chilled water pumps, 40 ft plus an additional allowance of 0.03 ft/ton, but not to exceed 100 ft. (See formula in the cell)
Note on J414: Sandeep: Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on P414: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L414) Impeller Efficiency: 0.7
Note on N419: Sandeep: The cooling tower fan horsepower is 60 gpm/hp.

## 030006-OffMed-Run23
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run23 |  |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 030006-OffMed-Run23.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope, Fenestration and HVAC |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Alteration | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.065 |  | 0.8 |  | 0.8 |  | 0.1 |  | 0.9
Exterior Wall | NACM_Metal Framed Wall_New | Altered | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | Exisiting | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New |  | Top Floor-South Window |  | FixedWindow |  | 0.4 |  | 0.33 |  | 0.5
Window | FixedWindow_Unaltered | Exisiting |  | All Other |  | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3081 |  | 0.33 |  | 0.33 |  | 0.33 |  | 0.22
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Metal Framed Wall | Exisiting/ Altered |  | Stucco - 7/8 in. |  | Building Paper - 1/16 in. |  | Expanded Polystyrene - EPS - 3 in. R13 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Roof | NACM_Roof | Altered |  | Metal Standing Seam - 1/16 in. |  | Expanded Polystyrene - EPS - 3 1/2 in. R15 | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Flr / All Zone | BottomVAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Flr / All Zone | Mid VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / All Zone (Except Zone 4) | Top VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / Zone 4 | Perimeter_top_ZN_4 New AirSys | New |  | Top Floor - Zone 4 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 |  | 9.9 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 |  | 9.9 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 |  | 9.9 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perimeter_top_ZN_4 New AirSys | Perim_top_4Zn CoolingCoil | New |  | DirectExpansion |  | 13 | - | - | - | - |  | CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BottomVAV | Bottom VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | CoreBottomReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom4ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | Mid VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | CoreMidReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid4ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | Top VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | CoreTopReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Perimeter_top_ZN_4 New AirSys | Perim_top_4Zn HeatingCoil | New |  | Furnace (Natural Gas) |  | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Zone:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BottomVAV | BottomVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 20.45 | - | - | - | - |  | 25 |  | 0.936
Mid VAV | MidVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 20.8 | - | - | - | - |  | 25 |  | 0.936
Top VAV | TopVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 18.76 | - | - | - | - |  | 20 |  | 0.93
Perimeter_top_ZN_4 New AirSys | Perim_top_4ZnSupplyFan | New |  | Constant Volume |  | BrakeHorsePower | - | - |  | 1.23 | - | - | - | - |  | 1.5 |  | 0.865
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV | BottomVAV Economizer | Exisiting |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV | MidVAV OACtrl | Exisiting |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV | Top VAV OACtrl | Exisiting |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Perimeter_top_ZN_4 New AirSys | Perime1OAControl | New | - | - | - | - | - | - | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 |  | Exisiting |  | 600000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 29.99 |  | 0.59 (19.68 W/gpm) |  | 0.8 |  | 65.857 |  | 0.9 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresWoodFramingAndOtherRoofU075 | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU098 | Altered | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | Exisiting | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Fenestrations | [11 empty] | 0.7125
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance |  | 65.857
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting |  | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3081 |  | 0.33 |  | 0.33 |  | 0.33 |  | 0.22
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU098 | Altered |  | Stucco - 7/8 in. |  | Compliance Insulation R8.07 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | Exisiting |  | Stucco - 7/8 in. |  | Building Paper - 1/16 in. |  | Expanded Polystyrene - EPS - 3 in. R13 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofU075 | Altered |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R12.55 | - | - | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  | AirSys:Type |  | AirSys:AvailSchRef |  |  |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Flr / All Zone | BottomVAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Flr / All Zone | Mid VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / All Zone (Except Zone 4) | Top VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / Zone 4 | BaseAirSys3 | New |  | Top Floor - Zone 4 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BottomVAV | Bottom VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | CoreBottomReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom4ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | Mid VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | CoreMidReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid4ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | Top VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | CoreTopReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) |  | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BottomVAV | BottomVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 20.45 | - | - | - | - |  | 25 |  | 0.936
Mid VAV | MidVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 20.8 | - | - | - | - |  | 25 |  | 0.936
Top VAV | TopVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 18.76 | - | - | - | - |  | 20 |  | 0.93
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume |  | StaticPressure |  | 1125.69 |  | 0.88595 |  | 0.5 |  | 2.5 |  | 1 |  | 0.855
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV | BottomVAV Economizer | Existing |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV | MidVAV OACtrl | Existing |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV | Top VAV OACtrl | Existing |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
BaseAirSys3 | BaseSys3 OACtrl | New | - | - | - | - | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 |  | Exisiting |  | 600000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 29.9886 |  | 0.59 (19.68 W/gpm) |  | 0.8 |  | 65.86 |  | 0.9 | - | -
Note on B17: Sandeep: 140811: underground wall not being tested, not documented
Note on H73: Sandeep: =0.0051427*(79)+0.3989
Note on L107: Sandeep: Pump Power is revised based on the recalculated pump head. Refer note in cell P107 for more information on the recalulated pump head values.
Note on P107: Sandeep: The MotorBHP calculated for pump 'HotWater Pump' is less than the ACM required value for the user-specified MotorHP. The Proposed TotHd will be revised to 65.9 ft for compliance analysis. Based on the calculation below MinMtrBHP / FlowCap * 3960 * ImpellerEff Where, MinMtrBHP = The minimum Proposed model MtrBHP is Max(User calc MtrBHP, 95% x MHPi-1) (The minimum allowed MtrBHP used in the Proposed model simulation based on user specified MtrHP.) Flow Cap = Based on Boiler Capacity Impeller Efficiency = 0.7
Note on H146: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H173: Sandeep: =0.0051427*(79)+0.3989
Note on N176: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P176: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R176: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T176: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.
Note on H181: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on P207: Sandeep: The MotorBHP calculated for pump 'HotWater Pump' is less than the ACM required value for the user-specified MotorHP. The Proposed TotHd will be revised to 65.9 ft for compliance analysis. Based on the calculation below MinMtrBHP / FlowCap * 3960 * ImpellerEff Where, MinMtrBHP = The minimum Proposed model MtrBHP is Max(User calc MtrBHP, 95% x MHPi-1) (The minimum allowed MtrBHP used in the Proposed model simulation based on user specified MtrHP.) Flow Cap = Based on Boiler Capacity Impeller Efficiency = 0.7

## 020006-OffSml-Run24
General Details |  |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 020006-OffSml-Run24 |  |  | Model Revision no. | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 020006-OffSml-Run24.cibd |  |  | Version of Ruleset (Trunk rev. No.) | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration and HVAC |  |  | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Alteration | [6 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered |  | Top Floor-South Window | FixedWindow |  | 0.4 |  | 0.33 |  | 0.5
Window | FixedWindow_Unaltered | Exisiting |  | All Other | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.21 | 0.2 |  | 0.2 |  | 0.24 |  | 0.2
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Core_ZN Thermal Zone | CoreZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | Perim1ZnPSZ AirSys_New | New |  | Bottom Floor - Zone 1 | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
CoreZnPSZ AirSys | CoreZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnPSZ AirSys | Perim2ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 |  |  |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim1ZnPSZ AirSys_New | Perim1ZnCoolingCoil | New |  | DirectExpansion | 13 | - | - |  | CoilClgDXEER13SEER18EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
CoreZnPSZ AirSys | CoreZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim2ZnPSZ AirSys | Perim2ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim1ZnPSZ AirSys_New | Perim1ZnHeatingCoil | New |  | Furnace (Natural Gas) | 0.80414 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
Fan:SysServed | Fan: |  |  | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
CoreZnPSZ AirSys | CoreZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower | - | - |  | 1.6 | - | - | - | - | 2 | 0.865
Perim2ZnPSZ AirSys | Perim2ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower | - | - |  | 0.8 | - | - | - | - | 1 | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower | - | - |  | 1.2 | - | - | - | - | 1.5 | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower | - | - |  | 0.8 |  |  |  |  | 1 | 0.855
Perim1ZnPSZ AirSys_New | Perim1ZnSupplyFan | New |  | Constant Volume | BrakeHorsePower | - | - |  | 1.12 | - | - | - | - | 1.5 | 0.855
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
Fan:ZnServed | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_4 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered |  | FixedWindow | 0.47 |  | 0.31 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting |  | FixedWindow | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.21 | 0.2 |  | 0.2 |  | 0.24 |  | 0.2
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Core_ZN Thermal Zone | CoreZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | Exisiting |  |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | BaseAirSys3 | New |  | Bottom Floor - Zone 1 | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
CoreZnPSZ AirSys | CoreZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnPSZ AirSys | Perim2ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion | 10.8446 |  | 1.15 |  | CoilClgDXEER11SEER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
CoreZnPSZ AirSys | CoreZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim2ZnPSZ AirSys | Perim2ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
Fan:SysServed | Fan: |  |  | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
CoreZnPSZ AirSys | CoreZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower | - | - |  | 1.6 | - | - | - | - | 2 | 0.865
Perim2ZnPSZ AirSys | Perim2ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower | - | - |  | 0.8 | - | - | - | - | 1 | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower | - | - |  | 1.2 | - | - | - | - | 1.5 | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower | - | - |  | 0.8 | - | - | - | - | 1 | 0.855
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume | StaticPressure |  | 1449.12 |  | 1.1405 |  | 0.5 |  | 2.5 | 1.5 | 0.865
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_4 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Note on H92: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on N110: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P110: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R110: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T110: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.
Note on H116: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.

## 020006-OffSml-Run25 (hidden)
General Details |  |  | Model/Software Details |  |  |  | Key
Test Name | 020006-OffSml-Run25 |  | Model Revision no. | 4000 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006-OffSml-Run25.cibd |  | Version of Ruleset (Trunk rev. No.) | Rel (828) |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2013-3d (828) |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested | 2016-04-14 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration |  | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Alteration |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Relevant Position | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC | FenConsRef:VT
Window | FixedWindow_Altered | Altered | South Window | FixedWindow | 0.4 |  | 0.33 | 0.5
Window | FixedWindow_Unaltered | Exisiting | All Other | FixedWindow | 0.55 |  | 0.56 | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered | FixedWindow | 0.47 | 0.31 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting | FixedWindow | 0.55 | 0.56 |  | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2

## 020006-OffSml-Run26 (hidden)
General Details |  |  | Model/Software Details |  |  |  | Key
Test Name | 020006-OffSml-Run26 |  | Model Revision no. | 4000 |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006-OffSml-Run26.cibd |  | Version of Ruleset (Trunk rev. No.) | Rel (828) |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2013-3d (828) |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested | 2016-04-14 |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration |  | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Alteration |  |  |  |  | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Relevant Position | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC | FenConsRef:VT
Window | FixedWindow_Altered | New | South Window | FixedWindow | 0.35 |  | 0.32 | 0.53
Window | FixedWindow_Unaltered | Exisiting | All Other | FixedWindow | 0.55 |  | 0.56 | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New | FixedWindow | 0.36 | 0.25 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting | FixedWindow | 0.55 | 0.56 |  | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.4 | 0.19 | 0.19 |  | 0.89 | 0.19

## 050006-RetlMed-Run27 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 050006-RetlMed-Run27 |  |  | Model Revision no. |  | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 050006-RetlMed-Run27.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration and HVAC |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Addition | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 | New |  | South Windows (All Windows) |  | FixedWindow |  | 0.35 |  | 0.32 |  | 0.53
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3716 |  | 0 |  | 0 |  | 0.4603 |  | 0
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Front_Entry | Lobby, Main Entry | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.6 |  | 0.75 |  | 2.35 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.15 | - | - |  | 1.15 |  | RetailLights |  | Area Category Method | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Bottom Floor / All Zones | SouthAddtn AirSys | New |  | All additions |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
SouthAddtn AirSys | SouthAddtn CoolingCoil | New |  | DirectExpansion |  | 11 |  | 11.2 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
SouthAddtn AirSys | SouthAddtn HeatingCoil | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
Fan:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
SouthAddtn AirSys | SouthAddtn SupplyFan | New |  | Constant Volume |  | BrakeHorsePower | - | - |  | 3.2 | - | - | - | - | 3 | 0.895
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
SouthAddtn AirSys | SouthAddtn OAControl | New |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 | New |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3716 |  | 0 |  | 0 |  | 0.4603 |  | 0
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Front_Entry | Lobby, Main Entry | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.5 |  | 0.65 |  | 2.15 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl
Bottom Floor / All Zones | BaseAirSys3 | New |  | All additions |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion |  | 10.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) |  | 0.8 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
Fan:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume |  | StaticPressure |  | 6308.69 |  | 4.9651 |  | 0.6 |  | 3 | 5 | 0.895
BaseAirSys3 | BaseRelief Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 6146.36 |  | 1.814 |  | 0.4 |  | 0.75 | 2 | 0.865
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
SouthAddtn AirSys | BaseSys3 OACtrl | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Note on H89: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H99: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N99: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P99: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R99: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T99: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.

## 050006-RetlMed-Run28
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 050006-RetlMed-Run28 |  |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 050006-RetlMed-Run28.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope, Fenestration and HVAC |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | Existing Addition and Alteration | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | Altered metal bldg roof | Altered |  | Low |  | MetalBuildingRoof |  | 0.034 |  | 0.75 |  | 0.75 |  | 0.08 |  | 0.92
Roof | Other Altered Roof | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.021 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Low |  | WoodFramingAndOtherRoof |  | 1.282 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.039 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | Altered metal frame wall | Altered | - | - |  | MetalFrameWall |  | 0.053 | - | - | - | - | - | - | - | -
Exterior Wall | Altered metal building wall | Altered | - | - |  | MetalBuildingWall |  | 0.052 | - | - | - | - | - | - | - | -
Exterior Wall | New heavy mass wall | New | - | - |  | MassHeavyWall |  | 0.051 | - | - | - | - | - | - | - | -
Exterior Wall | Altered light mass wall | Altered | - | - |  | MassLightWall |  | 0.046 | - | - | - | - | - | - | - | -
Exterior Wall | Altered heavy mass wall | Altered | - | - |  | MassHeavyWall |  | 0.051 | - | - | - | - | - | - | - | -
Exterior Wall | Base_CZ12-NonresMetalFrameWallU062_New | New | - | - |  | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | -
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | Altered metal bldg roof | Altered |  | Metal standing seam roof, R-0 |  | Air - Cavity - Wall Roof Ceiling - 4 in. or more |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 | - | - | - | - | - | -
Roof | Other Altered Roof | Altered |  | Built-up roofing - 3/8 in. |  | Expanded Polystyrene - EPS - 6 1/10 in. R25 |  | Wood, Roof24in OC, 2x6, cav. R-19 |  | Air - Cavity - Wall Roof Ceiling - 4 in. or more |  | Acoustic Tile - 3/4 in. | - | -
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Metal Standing Seam - 1/16 in. | - | - | - | - | - | - | - | - | - | -
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039 | New |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R24.86 | - | - | - | - | - | - | - | -
Exterior Wall | Altered metal frame wall | Altered |  | Stucco - 7/8 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall | Altered metal building wall | Altered |  | Metal Siding - 1/16 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Plywood 3/4in | - | - | - | -
Exterior Wall | New heavy mass wall | New |  | Stucco - 7/8 in. |  | Concrete - 140 lb/ft3 - 6 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Exterior Wall | Altered light mass wall | Altered |  | Stucco - 7/8 in. |  | Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. |  | Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in.
Exterior Wall | Altered heavy mass wall | Altered |  | Stucco - 7/8 in. |  | Concrete - 140 lb/ft3 - 6 in. |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Exterior Wall | Base_CZ12-NonresMetalFrameWallU062 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R13.99 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall (UnConditioned) | Base_CZ12-NonresMetalFrameWallU062 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R13.99 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | -
Fenestrations
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.07 |  | 0 |  | 0 |  | 0.25 |  | 0
|  | Type |  | Skylight to Roof Ratio (Frac)
CondSRR
|  | Skylights |  | 0.02
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Exisiting |  | 0.5 | - | - |  | 0.5 |  | RetailLights |  | AreaCategoryMethod | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | Exisiting |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | AreaCategoryMethod | - | -
Front_Entry | Lobby, Main Entry | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | AreaCategoryMethod | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.6 |  | 0.75 |  | 2.35 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.15 | - | - |  | 1.15 |  | RetailLights |  | AreaCategoryMethod | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor / Exisiting Zones | BaseAirSys5 | Exisiting |  | Exisiting Zones |  | PVAV |  | RetailHVACAvail |  | 60 |  | 60 |  | WarmestReset |  | 60 |  | 55
Bottom Floor / Addition Zones | SouthAddtn AirSys | Exisiting |  | All South Zones |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | Exisiting |  | DirectExpansion |  | 9.8 |  | 9.9 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
SouthAddtn AirSys | SouthAddtn CoolingCoil | Exisiting |  | DirectExpansion |  | 11 |  | 11.2 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | Exisiting |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil | Exisiting |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil-2 | Exisiting |  | HotWater | - | - | - | - | - | -
SouthAddtn AirSys | SouthAddtn HeatingCoil | Exisiting |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Bottom Floor / Exisiting Zones | BaseSys5 Fan | Exisiting |  | VariableSpeedDrive |  | Static Pressure | - | - |  | 21.67 |  | 0.62 |  | 4 |  | 25 |  | 0.936
Bottom Floor / Addition Zones | SouthAddtn SupplyFan | Exisiting |  | Constant Volume |  | BrakeHorsePower | - | - |  | 3.2 | - | - | - | - |  | 3.5 |  | 0.895
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | Exisiting |  | DifferentialDryBulb |  | Integrated
SouthAddtn AirSys |  | Exisiting |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Back_Space | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Core_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | Exisiting |  | 240681 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | Exisiting |  | OnDemand |  | ConstantSpeed |  | 12.03 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base HW Pump-2 | Base Blr-2 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 12.03 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresMetalBuildingRoofU065 | Altered |  | Low |  | MetalBuildingRoof |  | 0.065 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofU075 | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Low |  | WoodFramingAndOtherRoof |  | 1.282 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU098 | Altered | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Exterior Wall | MetalBldgWallU113 | Altered | - | - |  | MetalBuildingWall |  | 0.113 | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | New | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Exterior Wall | MassLightWallU440 | Altered | - | - |  | MassLightWall |  | 0.44 | - | - | - | - | - | - | - | -
Exterior Wall | MassHeavyWallU690 | Altered | - | - |  | MassHeavyWall |  | 0.69 | - | - | - | - | - | - | - | -
Exterior Wall (UnConditioned) | MetalFrameWallUnconditioned | New |  |  |  | MetalFrameWall |  | 0.971
Exterior Wall | MetalFrameWallU098 | New | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | FlatNonresMetalBuildingRoofU065 | Altered |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R14.60 | - | - | - | - | - | - | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofU075 | Altered |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R12.55 | - | - | - | - | - | - | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Metal Standing Seam - 1/16 in. | - | - | - | - | - | - | - | - | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R12.55 | - | - | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | Altered |  | Stucco - 7/8 in. |  | Compliance Insulation R8.07 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Wall | MetalBldgWallU113 | Altered |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R8.00 | - | - | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R8.07 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Wall | MassLightWallU440 | Altered |  | Concrete - 140 lb/ft3 - 4 in. |  | Compliance Insulation R0.02 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Wall | MassHeavyWallU690 | Altered |  | Concrete - 140 lb/ft3 - 8 in. |  | Compliance Insulation R0.01 | - | - | - | - | - | - | - | - | - | -
Exterior Wall (UnConditioned) | MetalFrameWallUnconditioned | New |  | Stucco - 7/8 in. | - | - | - | - | - | - | - | - | - | - | - | -
Fenestrations
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.07 |  | 0 |  | 0 |  | 0.25 |  | 0
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | Exisiting |  | 0.5 | - | - |  | 0.5 |  | RetailLights |  | Area Category Method | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | Exisiting |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
Front_Entry | Lobby, Main Entry | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.5 |  | 0.65 |  | 2.15 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | New |  | 1.2 | - | - |  | 1.2 |  | RetailLights |  | Area Category Method | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor / Exisiting Zones | BaseAirSys5 | Exisiting |  | Exisiting Zones |  | PVAV |  | RetailHVACAvail |  | 60 |  | 60 |  | WarmestReset |  | 60 |  | 55
Bottom Floor / Addition Zones | SouthAddtn AirSys | Exisiting |  | All South Zones |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | Exisiting |  | DirectExpansion |  | 9.8 |  | 9.9 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
SouthAddtn AirSys | SouthAddtn CoolingCoil | Exisiting |  | DirectExpansion |  | 11 |  | 11.2 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | Existing |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil | Existing |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil-2 | Existing |  | HotWater | - | - | - | - | - | -
SouthAddtn AirSys | SouthAddtn HeatingCoil | Existing |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Bottom Floor / Exisiting Zones | BaseSys5 Fan | Exisiting |  | VariableSpeedDrive |  | Static Pressure | - | - |  | 21.67 |  | 0.62 |  | 4 |  | 25 |  | 0.936
Bottom Floor / Addition Zones | SouthAddtn SupplyFan | Exisiting |  | Constant Volume |  | BrakeHorsePower | - | - |  | 3.2 | - | - | - | - |  | 3.5 |  | 0.895
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | Exisiting |  | DifferentialDryBulb |  | Integrated
SouthAddtn AirSys |  | Exisiting |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Back_Space | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Core_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | Exisiting |  | 240681 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | Exisiting |  | OnDemand |  | ConstantSpeed |  | 12.03 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Base HW Pump-2 | Base Blr-2 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 12.03 |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Note on J15: Sandeep: 151217_v3d: The effective R-value of the 'RoofMetalStandingSeam' has been revised and reduced.
Note on N185: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P185: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on T185: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.

## 030006-OffMed-Run29 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run29 |  |  | Model Revision no. |  | 4000 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run29.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope and HVAC |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | New Envelope | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.065 |  | 0.78 |  | 0.78 |  | 0.75 |  | 0.25
Exterior Wall | NACM_Metal Framed Wall | New | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Exterior Floor | NACM_Conc Raised Flr | New | - | - |  | MassFloor |  | 0.039 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 |  |  | FixedWindow |  | 0.35 |  | 0.32 |  | 0.53
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | NACM_Roof | New |  | Metal Standing Seam - 1/16 in. |  | Expanded Polystyrene - EPS - 3 1/2 in. R15 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | New |  | Stucco - 7/8 in. |  | Building Paper - 1/16 in. |  | Expanded Polystyrene - EPS - 3 in. R13 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | -
Exterior Floor | NACM_Conc Raised Flr | New |  | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 |  | Concrete - 80 lb/ft3 - 4 in. |  | Metal Deck - 1/16 in. |  | OSB - Oriented Strand Board - 5/8 in. |  | Carpet - 3/4 in. | - | -
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Spaces) | Office (Greater than 250 square feet in floor area) | Future |  | 0.75 |  | OfficeLights
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd |  | AirSys:ClRstSupHi | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power | Motor Efficiency
Fan:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP | Fan:MtrEff
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 14718.9 |  | 14.965 |  | 0.62 |  | 4 |  | 15 | 0.924
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14222.9 |  | 14.4607 |  | 0.62 |  | 4 |  | 15 | 0.924
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14857 |  | 15.1054 |  | 0.62 |  | 4 |  | 20 | 0.93
BaseRelief Fan | BaseAirSys5 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13825.1 |  | 4.3574 |  | 0.5 |  | 1 |  | 5 | 0.895
BaseRelief Fan-2 | BaseAirSys5-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13329.1 |  | 4.2011 |  | 0.5 |  | 1 |  | 5 | 0.895
BaseRelief Fan-3 | BaseAirSys5-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13963.2 |  | 4.401 |  | 0.5 |  | 1 |  | 5 | 0.895
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 311701 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 15.58 |  | 0.296 (19 W/gpm) |  | 0.5 |  | 60.4 | 0.855 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU098 | New | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Exterior Floor | OtherFloorU071 | New | - | - |  | OtherFloor |  | 0.071 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 |  |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6 |  | Layers -7
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | Metal Standing Seam - 1/16 in. |  | Compliance Insulation R12.55 | - | - | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | New |  | Stucco - 7/8 in. |  | Compliance Insulation R8.07 |  | Air - Metal Wall Framing - 16 or 24 in. OC |  | Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Floor | OtherFloorU071 | New |  | Compliance Insulation R9.83 |  | Plywood - 5/8 in. |  | Carpet - 3/4 in. | - | - | - | - | - | - | - | -
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Spaces) | Office (Greater than 250 square feet in floor area) | Future |  | 0.75 |  | OfficeLights
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power | Motor Efficiency
Fan:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP | Fan:MtrEff
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 15421.3 |  | 15.6791 |  | 0.62 |  | 4 |  | 20 | 0.93
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14121.2 |  | 14.3573 |  | 0.62 |  | 4 |  | 15 | 0.924
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 15433.2 |  | 15.6912 |  | 0.62 |  | 4 |  | 20 | 0.93
BaseAirSys5 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 14527.5 |  | 4.5788 |  | 0.5 |  | 1 |  | 5 | 0.895
BaseAirSys5-2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13227.4 |  | 4.169 |  | 0.5 |  | 1 |  | 5 | 0.895
BaseAirSys5-3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14539.4 |  | 4.5826 |  | 0.5 |  | 1 |  | 5 | 0.895
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 339919 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 16.99 |  | 0.32 (19 W/gpm) |  | 0.5 |  | 60.4 | 0.855 | - | -
Note on H131: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H146: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N146: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P146: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R146: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T146: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.
Note on B151: Sandeep: 140821: System Relief fan first accounted for in rev. 2432,
Note on F170: Sandeep: The boiler is sized to be 25% larger than the peak loads of the baseline building. Baseline boilers shall be sized using weather files containing 99.6% heating design temperatures and 0.5% dry-bulb and 1% wet-bulb cooling design temperatures.
Note on H175: Sandeep: The baseline system pumps are assumed to operate in On-Demand mode. The chilled water and condenser pumps are tied to the chiller operation, cycling on and off with the chiller, and the heating hot water pumps are tied to the boiler operation.
Note on J175: Sandeep: The chilled water pumps shall be modeled as variable-speed, variable flow, and the condenser water pumps shall be modeled as fixed speed. The hot water pumps shall be modeled as fixed-speed, variable flow, riding the curve.
Note on L175: Sandeep: Please refer to the reporting file - '030006-OffMed-Run29 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formulae commented in the cells below
Note on P175: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T175: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table-31 available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on L177: Sandeep: Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on R177: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L177) Impeller Efficiency: 0.7

## 030006-OffMed-Run30
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run30 |  |  | Model Revision no. |  | 4000 |  |  |  | Use cell to check if values are verified
Model File Name | 030006-OffMed-Run30.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | Rel (828) |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3d (828) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  | 2016-04-14 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC and Partial Lighting |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Compliance Type | New Mechanical and Partial Lighting | [7 empty] | 1 | Value of the cell is directly or indirectly dependent on auto-sized properties of the Baseline transform. Refer to the note in the cell or in the column header.
Proposed
Internal Load Components
Space
Space Name | Space Function | Status |  | Installed Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor |  | Lighting Power Density (Simulated) (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF |  | Spc:IntLPDReg |  | IntLtgRegSchRef:Name
(All Levels - Core Zones) | Office (Greater than 250 square feet in floor area) | New |  | 8448 |  | 5068.8 |  | OccupantSensingControls-1to125SF |  | 0.4 |  | 0.48 |  | OfficeLights
(All Levels - South Zones - Zone 1) | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - |  | 0.8 |  | OfficeLights
(All Levels - All other Zones) | Office (Greater than 250 square feet in floor area) | Existing | - | - | - | - | - | - | - | - |  | 1.2 |  | OfficeLights
Daylighting
Space - Name | Space Function | Status |  | Primary Sidelit - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux) |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Core_bottom | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 952.362 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 952.362 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 952.362 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor | BottomVAV | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | Mid VAV | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | Top VAV | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | Cooling Efficiency (IEER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg:DXIEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | New |  | DirectExpansion |  | 13.1 |  | 13.23 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | New |  | DirectExpansion |  | 13.1 |  | 13.23 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | New |  | DirectExpansion |  | 13.1 |  | 13.23 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating | New |  | HotWater
Mid VAV | Mid VAV CoilHeating | New |  | HotWater
Top VAV | Top VAV CoilHeating | New |  | HotWater
BottomVAV | (All ReheatCoils) | New |  | HotWater
Mid VAV | (All ReheatCoils) | New |  | HotWater
Top VAV | (All ReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Zone:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BottomVAV | BottomVAV SupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 14.085 | - | - | - | - |  | 15 |  | 0.9
Mid VAV | MidVAV SupplyFan | New |  | ConstantVolume |  | Static Pressure |  | 17875.9 |  | 12.9866 |  | 0.65 |  | 3 |  | 15 |  | 0.9
Top VAV | TopVAV SupplyFan | New |  | ConstantVolume |  | Static Pressure |  | 17875.9 |  | 18.1534 |  | 0.62 |  | 4 |  | 20 |  | 0.9
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl: |  | OACtrl:
BottomVAV |  | New |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV |  | New |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV |  | New |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 | New |  |  | 700000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | New |  | 1 |  | OnDemand |  | ConstantSpeed |  | 34.9867 |  | 1.18 (33.74 W/gpm) |  | 2 |  | 112.9029 |  | 0.9 | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (Simulated) (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Levels - Core Zones) | Office (Greater than 250 square feet in floor area) | New |  | 0.75 |  | OfficeLights
(All Levels - South Zones - Zone 1) | Office (Greater than 250 square feet in floor area) | New |  | 0.75 |  | OfficeLights
(All Levels - All other Zones) | Office (Greater than 250 square feet in floor area) | Existing |  | 1.2 |  | OfficeLights
Daylighting
Space - Name | Space Function | Status |  | Primary Sidelit - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux) |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Core_bottom | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 892.84 |  | 287.5 |  | 287.5 |  | 1040.8 |  | 780.598 |  | 287.5 |  | 1150
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 892.84 |  | 287.5 |  | 287.5 |  | 1040.8 |  | 780.598 |  | 287.5 |  | 1150
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | New |  | 1190.45 |  | 892.84 |  | 287.5 |  | 287.5 |  | 1040.8 |  | 780.598 |  | 287.5 |  | 1150
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | Existing |  | 1190.45 |  | 1428.54 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | Existing |  | 774.255 |  | 929.106 |  | 287.5 |  | 287.5 | - | - | - | - | - | - | - | -
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | AirSys:ClgCtrl |  | AirSys:ClRstSupHi |  | AirSys: ClRstSupLow
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseSys5 CoilHtg | BaseSys5 CoilHtg | New |  | HotWater
BaseSys5 CoilHtg-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseSys5 CoilHtg-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 14319.8 |  | 14.5421 |  | 0.62 |  | 4 |  | 15 |  | 0.924
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 14805.2 |  | 15.035 |  | 0.62 |  | 4 |  | 20 |  | 0.93
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 17504.7 |  | 17.7764 |  | 0.62 |  | 4 |  | 20 |  | 0.93
BaseAirSys5 | BaseRelief Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 13426 |  | 4.2267 |  | 0.5 |  | 1 |  | 5 |  | 0.895
BaseAirSys5-2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 13911.4 |  | 4.3795 |  | 0.5 |  | 1 |  | 5 |  | 0.895
BaseAirSys5-3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 16610.9 |  | 5.2293 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 253774 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Design Flow Rate (gpm) |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:FlowCap |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 12.6839 |  | 0.24 (19 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Note on R93: Sandeep: The MotorBHP calculated for pump 'HotWater Pump' is less than the ACM required value for the user-specified MotorHP. The Proposed TotHd will be revised to112.9 ft for compliance analysis. Based on the calculation below MinMtrBHP / FlowCap * 3960 * ImpellerEff Where, MinMtrBHP = The minimum Proposed model MtrBHP is Max(User calc MtrBHP, 95% x MHPi-1) (The minimum allowed MtrBHP used in the Proposed model simulation based on user specified MtrHP.) Flow Cap = Based on Boiler Capacity Impeller Efficiency = 0.7
Note on H134: Sandeep: Min Req. Based on Coil Capacity < 65,000 Btu/hr: 13 SEER < 135,000 Btu/hr: 11.2 EERb < 240,000 Btu/hr: 11 EERb < 760,000 Btu/hr: 10 EERb > 760,00 Btu/hr: 9.7 EERb (Standards - Table 110.2-A: b - Deduct 0.2 from the required EER's and IEER's for units with the heating section other than electric resistance heat)
Note on H149: Sandeep: The baseline building shall use the static pressure method for all HVAC systems except the four-pipe fan coil system, which shall use the power-per-unit-flow method.
Note on N149: Sandeep: The baseline Supply Fan Efficiency shall be based on the design supply flow rate <2,000cfm = 50% <10,000cfm = 60% >10,000cfm = 62% For the four-pipe fan coil system, not applicable. The baseline Return/Relief Fan Efficiency shall be based on the design supply flow rate <10,000cfm = 40% >10,000cfm = 50%
Note on P149: Sandeep: The baseline Supply Fan 'Total Static' shall be based on the design supply flow rate, Single Zone or Multiple Zone system, and the number of stories. Refer: Supply Fan Static Pressure in the ACM for further clarification The baseline Return/Relief Design Static Pressure shall be based on the design supply flow rate <10,000cfm =0.75 >10,000cfm = 1
Note on R149: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the calculated MtrBHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T149: Sandeep: The motor efficiency in the standard model is determined from Minimum Nominal Efficiency for Electric Motors (Table 31) for the next motor size greater than the bhp. Except when the 'Power-Per-Flow' modeling method is used.
Note on F173: Sandeep: The boiler is sized to be 25% larger than the peak loads of the baseline building. Baseline boilers shall be sized using weather files containing 99.6% heating design temperatures and 0.5% dry-bulb and 1% wet-bulb cooling design temperatures.
Note on H178: Sandeep: The baseline system pumps are assumed to operate in On-Demand mode. The chilled water and condenser pumps are tied to the chiller operation, cycling on and off with the chiller, and the heating hot water pumps are tied to the boiler operation.
Note on J178: Sandeep: The chilled water pumps shall be modeled as variable-speed, variable flow, and the condenser water pumps shall be modeled as fixed speed. The hot water pumps shall be modeled as fixed-speed, variable flow, riding the curve.
Note on L178: Sandeep: Please refer to the reporting file - '030006-HotSml-Run30 - ab - HVACPrimary.csv', for the reported design flow rate. Alternately can be calculated using the formulae commented in the cells below
Note on P178: Sandeep: The next motor size shall be chosen from the list of standard motor sizes based on the auto-calculated MtrHP Standard Motor sizes: 1/12, 1/8, ¼, ½, ¾, 1, 1.5, 2, 3, 5, 7.5, 10, 15, 20, 25, 30, 40, 50, 60, 75, 100, 125, 150, 200.
Note on T178: Sandeep: The Pump Motor efficiency is found using the Minimum Nominal Efficiency for Electric Motors Table-31 available in the NACM, for the next larger motor size than the calculated standard design brake horsepower
Note on L180: Sandeep: Boiler Capacity/500.19/DesignSupplyWaterDeltaT Where, Heat output of the boiler is calculated at full load and rated conditions. The Design Supply Water DeltaT for boilers is 40 degF
Note on R180: Sandeep: The pump total head for HW pumps is calculated using the formula below- (Power-Per-Unit-Flow/745.6*3960*Motor Efficiency* Impeller Efficiency) where, Power per Unit Flow for HW pumps:19 W/gpm (refer Cell L180) Impeller Efficiency: 0.7