## Documentation Main Sheet (hidden)
General Details | Model/Software Details
Test Name | Model Revision no. | 3169
Model File Name | Version of Ruleset (Trunk rev. No.) | v3b
Climate Zone | CBECC Software | CBECC-Com 2013-3b (717)
| Date Tested | 2015-04-06
| Testing Performed by | Sandeep Doddaballapur

## Test Status Summary
Ruleset Implementation Tests - Test Specification Status | [10 empty] | Status of Example Test Files - Detailed Geometry |  | Status of Example Test Files - Simplified Geometry
Test No | Building Type | Test Name | Compliance Type | Category | Test Criteria | Notes | Streamlined Set v3 -> v3a |  | Streamlined Set v3a -> v3b |  | Example Test File Status | Example Test File Path | Example Test File Status | Example Test File Path
1 | Small Office | 020006-OffSml-Run01 | NewComplete | Exterior Envelope | Envelope and window assembly performance | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006-OffSml-Run01\020006-OffSml-Run01.cibd | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006S-OffSml-Run01\020006S-OffSml-Run01.cibd
2 | Small Office | 020006-OffSml-Run02 | NewComplete | Exterior Envelope | Envelope and window assembly performance | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020015-OffSml-Run02\020015-OffSml-Run02.cibd | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020015S-OffSml-Run02\020015S-OffSml-Run02.cibd
3 | Small Hotel | 070015-HotSml-Run03 | NewComplete | Exterior Envelope | Envelope and window assembly performance |  |  |  | X | Baseline fenestration properties changes, for 'Operable' windows. | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 070015-HotSml-Run03\070015-HotSml-Run03.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test
4 | Medium Office | 030006-OffMed-Run04 | NewComplete | Exterior Envelope | Envelope minimum requirements | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 030006-OffMed-Run04\030006-OffMed-Run04.cibd | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 030006S-OffMed-Run04\030006S-OffMed-Run04.cibd
5 | Large Office | 040006-OffLrg-Run05 | NewComplete | Fenestration | Window Wall Ratio (WWR) | [5 empty] | Status: Verified Date:12/23/14 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 040006-OffLrg-Run05\040006-OffLrg-Run05.cibd | Status: Test Not Performed Date: Version:
6 | Large Office | 040006-OffLrg-Run06 | NewComplete | Fenestration | Window Wall Ratio (WWR) | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 040006-OffLrg-Run06\040006-OffLrg-Run06.cibd | Status: Test Not Performed Date: Version:
7 | Warehouse | 080006-Whse-Run07 | NewComplete | Skylight | Skylight to Roof Ratio (SRR) and Skylight Performance | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 080006-Whse-Run07\080006-Whse-Run07.cibd | Status: Test Not Performed Date: Version:
8 | Warehouse | 080006-Whse-Run08 | NewComplete | Skylight | Skylight to Roof Ratio (SRR) and Daylit Area | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters |  |  |  |  | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 080006-Whse-Run08\080006-Whse-Run08.cibd | Status: Test Not Performed Date: Version:
9 | Warehouse |  |  | Skylight | SRR and Daylit Area | Adding/Enlarging Skylights to meet 140.3C daylit area requirements currently not supported |  |  |  |  | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
10 | Medium Office |  |  | Space Function | Internal Loads- Complete Bldg method | Complete Building test method currently not supported |  |  |  |  | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
11 | Large Office | 040006-OffLrg-Run11 | NewComplete | Space Function | Internal loads - Space-by-Space |  |  |  | X | - Occupancy density for 'Lobby, Main Entry' changed - Ventilation rates at the thermal zones have changed. Model Updates: - Core_hi: - VentPerPerson and VentPerArea set to '0' - VentPerSpc set tp 4415 - Perimeter_hi_ZN_2: - CondgType changed to 'IndirectlyConditioned' - Perimeter_hi_ZN_2 Thermal Zone: - Type changed to 'Unconditioned' - VentSrc set to 'None' - VentSpecMthd set to 'NoVentilation' - Core_hi Thermal Zone: - VentSpecMthd set to 'Sum' | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 040006-OffLrg-Run11\040006-OffLrg-Run11.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test
12 | Medium Office | 030006-OffMed-Run12 | NewComplete | Lighting | Lighting - tailored lighting method | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 030006-OffMed-Run12\030006-OffMed-Run12.cibd | Status: Test Not Performed Date: Version:
13 | Medium Office | 030006-OffMed-Run13 | NewComplete | Lighting | Lighting - tailored lighting method | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 030006-OffMed-Run13\030006-OffMed-Run13.cibd | Status: Test Not Performed Date: Version:
14 | Small Office | 020006-OffSml-Run14 | NewComplete | Lighting | Lighting - Power Adjustment Factors (PAF) rules |  |  |  |  | Interior Lighting system: SchRef is no longer a required user input. Appendix 3c has been updated | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006-OffSml-Run14\020006-OffSml-Run14.cibd | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006S-OffSml-Run14\020006S-OffSml-Run14.cibd
15 | Warehouse | 080006-Whse-Run15 | NewComplete | Lighting Control | Daylighting | Exclude Test for Simplified Geometry: Only daylighting parameters are tested. |  |  |  |  | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 080006-Whse-Run15\080006-Whse-Run15.cibd | Status: Date: Version: | Test Excluded for Simplified geometry
16 | Medium Retail | 050006-RetlMed-Run16 | NewComplete | Lighting Control | Lighting and daylighting | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters |  |  |  | Front_Retail Space 'Controlled General Lighting Power' is corrected to represent the installed watts and not the simulated Watts. | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 050006-RetlMed-Run16\050006-RetlMed-Run16.cibd | Status: Test Not Performed Date: Version:
17 | Large Office |  |  | Ext.Lighting/SHW | Ext. Lighting/SHW | Prescriptive Exterior Lighting Compliance not supported |  |  |  |  | Status: Test Not Performed Date: Version: | na | Status: Test Not Performed Date: Version: | na
18 | Small Office | 020006S-OffSml-Run18 | NewComplete | HVAC | HVAC - SZAC |  |  |  | X | - Core Zone: SZAC: Design supply air temperature changed. - Baseline fan capacities changed. | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006-OffSml-Run18\020006-OffSml-Run18.cibd | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006S-OffSml-Run18\020006S-OffSml-Run18.cibd | For this run CBECC will use the "Simplified Geometry" model.
19 | Medium Office | 030006-OffMed-Run19 | NewComplete | HVAC | HVAC - PVAV and CRAC |  | X | - Revised baseline IntWall/IntFlr construction - Revised baseline ThrmlZn: ClgDsgnSupAirTemp for interior 'Data' zones from 65 to 60 (Rules) | X | - All peripheral spaces 'SpaceType' changed from 'Lobby, Main Entry' to 'Office (250ft2 or greater) - Core Zone - Computer Rooms Heating Design Suppy Air Temperature: No Longer specified, SZAC system in the zone provides NO HEATING - User input EPD of 18W/ft2 for Core Space: Computer Room, less than the minimum for that space type, Proposed and Baselibe get updated to 20W/ft2 - Baseline DXEIR_fFlowCrvRef changed - Baseline fan capacities and other properties changed | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 030006-OffMed-Run19\030006-OffMed-Run19.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test
20 | Large Office | 040006-OffLrg-Run20 | NewComplete | HVAC | HVAC - VAV and CRAH |  | X | - Revised baseline IntWall/IntFlr construction - Revised baseline ThrmlZn: ClgDsgnSupAirTemp for interior 'Data' zones from 65 to 60 (Rules) | X | Basement Floor 'Design Suppy Air Temperature (Heating)' is not a valid input as the 'BsmntZnPSZ AirSys' is cooling only. | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 040006-OffLrg-Run20\040006-OffLrg-Run20.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test
21 | Warehouse | 080006-Whse-Run21 | NewComplete | HVAC | HVAC - SZAC and HV | [5 empty] | Status: Verified Date:141223 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 080006-Whse-Run21\080006-Whse-Run21.cibd | Status: Test Not Performed Date: Version:
22 | Hotel | 070015-HotSml-Run22 | NewComplete | HVAC | HVAC - PVAV, SZAC and FPFC |  | X | - Revised baseline IntWall/IntFlr construction - Baseline Kitchen Exhaust Fan: 'ExhOperMode' changed from 'CoupledTo System' to 'DecoupledFromSystem' - Baseline: Fan efficiencies and sizing changed | X | Design Suppy Air Temperature of he 'KitchenMUA' system has changed from 60 to 55. (proposed model) | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 070015-HotSml-Run22\070015-HotSml-Run22.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test
23 | Medium Office | 030006-OffMed-Run23 | ExistingAlteration | Existing Alteration | Window alteration and HVAC replacement |  | X | - Revised baseline IntWall/IntFlr construction - Design Suppy Air Temperature (Cooling) changed from 55 to 60 for office space with no vertical fenestration | X | - SZAC: Design supply air temperature changed. - Baseline fan capacities and other properties changed | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 030006-OffMed-Run23\030006-OffMed-Run23.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test
24 | Small Office | 020006-OffSml-Run24 | ExistingAlteration | Existing Alteration | Window alteration and HVAC replacement |  | X | - Revised baseline IntWall/IntFlr construction - Design Suppy Air Temperature (Cooling) changed from 55 to 60 for office spaces in the core zones. - Baseline: Fan BHP and capacities changed | X | - Core Zone: SZAC: Design supply air temperature changed. - Baseline fan capacities and other properties changed | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006-OffSml-Run24\020006-OffSml-Run24.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test
25 | Small Office | 020006-OffSml-Run25 | ExistingAlteration | Existing Alteration | Window alteration | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006-OffSml-Run25\020006-OffSml-Run25.cibd | Status: Test Not Performed Date: Version:
26 | Small Office | 020006-OffSml-Run26 | ExistingAlteration | Existing Alteration | Window alteration | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 020006-OffSml-Run26\020006-OffSml-Run26.cibd | Status: Test Not Performed Date: Version:
27 | Retail Medium | 050006-RetlMed-Run27 | ExistingAddition | Existing Addition | Addition modeled alone: Envelope performance, window assembly performance and HVAC - SZAC | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 050006-RetlMed-Run27\050006-RetlMed-Run27.cibd | Status: Test Not Performed Date: Version:
28 | Retail Medium | 050006-RetlMed-Run28 | ExistingAdditionAndAlteration | Existing Addition and Alteration | Addition modeled with an altered existing building: Envelope performance, Window Wall Ratio (WWR) and HVAC - SZAC |  | X | X | X | Rule modification for Existing/Alterations for altered lighting. Altered LPD in Front_Entry is < 85% of Baseline Lighting Power Allowance. Baseline LPD is set equal to proposed. | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 050006-RetlMed-Run28\050006-RetlMed-Run28.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test
29 | Medium Office | 030006-OffMed-Run29 | NewEnvelope | New Envelope | Envelope and correct assignment of proposed HVAC systems. | [5 empty] | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 030006-OffMed-Run29\030006-OffMed-Run29.cibd | Status: Test Not Performed Date: Version:
30 | Medium Office | 030006-OffMed-Run30 | NewMechanicalAndPartialLighting | New Mechanical and Partial Lighting | New/exisiting lighting and HVAC - PVAV | Modify Test for Simplified Geometry: Exclude Testing/Verification of Daylighting Parameters | X | - Revised baseline IntWall/IntFlr construction - Fan capacity, BHP, nameplate HP and efficiency changed. - Revised baseline roof construction | X | Economizer Lockout tempertaure setpoints are being evaluated. | Status: Verified Date: 04/06/15 Version: CBECC-Com 2013-3b (717) | svn\tags\CBECC-Com13_3a_687\CBECC-Com13\Projects\RulesetImplementationTests\ 030006-OffMed-Run30\030006-OffMed-Run30.cibd | Status: Test Not Performed Date: Version: |  | For this run CBECC will use the "Detailed Geometry" model. Test description same as corresponding Detailed Geometry test

## 020006S-OffSml-Run01 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020006S-OffSml-Run01 |  | Model Revision no. |  | 3169 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006S-OffSml-Run01.cibd |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | 2015-04-06 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof | X | Steep | X | WoodFramingAndOtherRoof | X | 0.044 | X | 0.78 | X | 0.78 | X | 0.75 | X | 0.25
Exterior Wall | NACM_Wood Framed Wall | - | - | X | WoodFramingAndOtherWall | X | 0.091 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Conc Raised FLr | - | - | X | MassFloor | X | 0.039 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit | - | - | X | OtherFloor | X | 0.07 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow | X | FixedWindow | X | 0.25 | X | 0.2 | X | 0.45
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Wood Framed Wall | X | 1.) Stucco - 7/8 in. | X | 2.) Building Paper - 1/16 in. | X | 3.) Insulation/Framing Layer - Wood, Wall16in OC, 2x4, cav. R-15 | X | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Roof | NACM_Roof | X | 1.) Asphalt roll roofing - 1/4 in. | X | 2.) Hardboard - HDF - 50 lb/ft3 - 3/4 in. | X | 3.) Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit | X | 1.) Plywood - 3/4 in. | X | 2.) Insulation/Framing Layer - Wood, Floor16in OC, 2x4, cav. R-15 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Conc Raised FLr | X | 1.) Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | X | 2.) Concrete - 80 lb/ft3 - 4 in. | X | 3.) Metal Deck - 1/16 in. | X | 4.) OSB - Oriented Strand Board - 5/8 in. | X | 5) Carpet - 3/4 in. | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | SteepNonresWoodFramingAndOtherRoofU075 | X | Steep | X | WoodFramingAndOtherRoof |  | 0.075 | X | 0.85 | X | 0.85 | X | 0.2 | X | 0.8
Exterior Wall | MetalFrameWallU098 | - | - | X | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU071 | - | - | X | OtherFloor |  | 0.071 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow | X | FixedWindow | X | 0.36 | X | 0.25 | X | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU098 | X | 1.) Stucco - 7/8 in. | X | 2.) Compliance Insulation R8.07 | X | 3.) Air - Metal Wall Framing - 16 or 24 in. OC | X | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Roof | SteepNonresWoodFramingAndOtherRoofU075 | X | 1.) Metal Standing Seam - 1/16 in. | X | 2.) Compliance Insulation R12.55 | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU071 | X | 1.) Compliance Insulation R9.83 | X | 2.) Plywood - 5/8 in. | X | 3.) Carpet - 3/4 in. | - | - | - | - | - | -
Note on H40: Sandeep: Values currenlty not being reported at the construction

## 020015S-OffSml-Run02 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020015S-OffSml-Run02 |  | Model Revision no. |  | 3169 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020015S-OffSml-Run02.cibd |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-15 |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | 2015-04-06 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.) |  | On/Below Grade Floor F-factor (Btu/h-°F-ft2) |  | Total Perimeter Area (ft2) |  | Total Perimeter exposed (ft)
| ConsAssmRef:Name |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs |  | ConsAssmRef:FFactor |  | UndgrFlr:Area |  | UndgrFlr:PerimExposed
Roof | NACM_Roof | X | Steep | X | WoodFramingAndOtherRoof | X | 0.053 | X | 0.7 | X | 0.7 | X | 0.6 | X | 0.4 | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | - | - | X | MetalFrameWall | X | 0.056 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit | - | - | X | OtherFloor | X | 0.07 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
On/Below Grade Floor | NACM_Slab Floor | - | - | - | NA (Slab -on grade) | - | - | - | - | - | - | - | - | - | - | X | 0.7 | X | 3891.16 | X | 300
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow | X | FixedWindow | X | 0.25 | X | 0.2 | X | 0.45
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Metal Framed Wall | X | 1.) Stucco - 7/8 in. | X | 2.) Building Paper - 1/16 in. | X | 3.) Expanded Polystyrene - EPS - 3 in. R13 | X | 4.) Insulation/Framing Layer - Metal, Wall 16in. OC, 2X6, Cav. R-19 | X | 5.) Gypsum Board - 1/2 in. | - | -
Roof | NACM_Roof | X | 1.) Asphalt roll roofing - 1/4 in. | X | 2.) Hardboard - HDF - 50 lb/ft3 - 3/4 in. | X | 3.) Expanded Polystyrene - EPS - 4 1/16 in. R17 | - | - | - | - | - | -
Above-grade Floor | NACM_Ext. Soffit | X | 1.) Plywood - 3/4 in. | X | 2.) Insulation/Framing Layer - Wood, Floor16in OC, 2x4, cav. R-15 | - | - | - | - | - | - | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.) |  | On/Below Grade Floor F-factor (Btu/h-°F-ft2) |  | Total Perimeter Area (ft2) |  | Total Perimeter exposed (ft)
| ConsAssmRef:Name |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs |  | ConsAssmRef:FFactor |  | UndgrFlr:Area |  | UndgrFlr:PerimExposed
Roof | SteepNonresWoodFramingAndOtherRoofU039 | X | Steep | X | WoodFramingAndOtherRoof |  | 0.039 | X | 0.85 | X | 0.85 | X | 0.2 | X | 0.8 | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU062 | - | - | X | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU039 | - | - | X | OtherFloor |  | 0.039 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
On/Below Grade Floor | SlabOnOrBelowGradeF073 | - | - | - | NA (Slab -on grade) | - | - | - | - | - | - | - | - | - | - | X | 0.73 | X | 3891.16 | X | 300
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow | X | FixedWindow | X | 0.36 | X | 0.25 | X | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU062 | X | 1.) Stucco 7/8 in. | X | 2.) Compliance Insulation R13.99 | X | 3.) Air - Metal Wall Framing - 16 or 24 in. OC | X | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Roof | SteepNonresWoodFramingAndOtherRoofU039 | X | 1.) Metal Standing Seam - 1/16 in. | X | 2.) Compliance Insulation R24.86 | - | - | - | - | - | - | - | -
Above-grade Floor | OtherFloorU039 | X | 1.) Compliance Insulation R21.39 | X | 2.) Plywood - 5/8 in. | X | 3.) Carpet - 3/4 in. | - | - | - | - | - | -
Note on H39: Sandeep: Values currenlty not being reported at the construction

## 070015S-HotSml-Run03 (hidden)
General Details |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 070015S-HotSml-Run03 |  | Model Revision no. |  |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 070015S-HotSml-Run03.cibd |  | Version of Ruleset (Trunk rev. No.) | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-15 |  | CBECC Software | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Hotel |  | Date Tested |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Exterior Envelope |  | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof |  | Low | WoodFramingAndOtherRoof |  | 0.055 |  | 0.7 |  | 0.7 |  | 0.6 |  | 0.4
Exterior Wall | NACM_Mtl Framed Wall | - | - | MetalFrameWall |  | 0.082 | - | - | - | - | - | - | - | -
Above-grade Floor | NACM_Ext.Conc Raised FLr | - | - | MassFloor |  | 0.058 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
| Window Non-res Fixed |  | FixedWindow | 0.25 |  | 0.2 |  | 0.47
| Window Res Operable |  | OperableWindow | 0.42 |  | 0.18 |  | 0.35
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | NACM_Roof |  | 1.) Metal Standing Seam - 1/16 in. | 2.) Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | 3.) Gypsum Board - 1/2 in. | - | - | - | - | - | -
Exterior Wall | NACM_Mtl Framed Wall |  | 1.) Stucco - 7/8 in. | 2.) Expanded Polystyrene - EPS - 2 7/16 in. R10 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 3/8 in. | - | - | - | -
Above-grade Floor | NACM_Ext.Conc Raised FLr |  | 1.) Metal Deck - 1/16 in. | 2.) Concrete - 80 lb/ft3 - 4 in. |  | 3.) Expanded Polystyrene - EPS - 1 7/8 in. R8.0 |  | 4.) Expanded Polyurethane - 3/4 in. R4.7 |  | 5.) Carpet - 3/4 in. | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name |  | Slope Category | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  | SlopeType | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Non-Residential Roof | FlatNonresWoodFramingAndOtherRoofU039 |  | Low | WoodFramingAndOtherRoof |  | 0.039 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Residential Roof | FlatResWoodFramingAndOtherRoofU028 |  | Low | WoodFramingAndOtherRoof |  | 0.028 |  | 0.85 |  | 0.85 |  | 0.55 |  | 0.45
NonResidential - Exterior Wall | MetalFrameWallU062 | - | - | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | -
Residential - Exterior Wall | MetalFrameWallU105 | - | - | MetalFrameWall |  | 0.105 | - | - | - | - | - | - | - | -
Residential and NonResidential - Above-grade Floor | OtherFloorU039 | - | - | OtherFloor |  | 0.039 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
| Window Non-res Fixed/Window Res Operable |  | FixedWindow | 0.36 |  | 0.25 |  | 0.42
| Window Non-res Fixed/Window Res Operable |  | OperableWindow | 0.46 |  | 0.22 |  | 0.32
Constructions/Layers
Opaque
Type | Construction Assembly Name |  | Layers -1 | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  | CodeItem | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
NonResidential - Exterior Wall | MetalFrameWallU062 |  | 1.) Stucco 7/8 in. | 2.) Compliance Insulation R13.99 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Residential - Exterior Wall | MetalFrameWallU105 |  | 1.) Stucco 7/8 in. | 2.) Compliance Insulation R7.39 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
NonResidential - Roof | FlatNonresWoodFramingAndOtherRoofU039 |  | 1.) Metal Standing Seam - 1/16 in. | 2.) Compliance Insulation R24.86 | - | - | - | - | - | - | - | -
Residential - Roof | FlatResWoodFramingAndOtherRoofU028 |  | 1.) Metal Standing Seam - 1/16 in. | 2.) Compliance Insulation R34.93 | - | - | - | - | - | - | - | -
Residential and NonResidential - Above-grade Floor | OtherFloorU039 |  | 1.) Compliance Insulation R21.39 | 2.) Plywood - 5/8 in. |  | 3.) Carpet - 3/4 in. | - | - | - | - | - | -
Note on H40: Sandeep: Values currenlty not being reported at the construction

## 040006S-OffLrg-Run05 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 040006S-OffLrg-Run05 | Model Revision no. |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 040006S-OffLrg-Run05 .cibd | Version of Ruleset (Trunk rev. No.) | v3b |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3b (717) |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office | Date Tested |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.52 | 0.52 | 0.52 | 0.52 |  | 0.52
Baseline
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4

## 040006S-OffLrg-Run06 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 040006S-OffLrg-Run06 | Model Revision no. |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 040006S-OffLrg-Run06 .cibd | Version of Ruleset (Trunk rev. No.) | v3b |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3b (717) |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office | Date Tested |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Fenestration | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.46 | 0.5 | 0.45 | 0.4 |  | 0.5
Baseline
Building Geometry
Fenestrations
Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) | South WWR (Frac) |  | West WWR (Frac)
| CondWWR | NorthCondWWR | EastCondWWR | SouthCondWWR |  | WestCondWWR
Window | 0.4 | 0.45 | 0.4 | 0.35 |  | 0.4

## 080006S-Whse-Run07 (hidden)
General Details |  | Model/Software Details |  |  |  | Key
Test Name | 080006S-Whse-Run07 | Model Revision no. |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006S-Whse-Run07.cibd | Version of Ruleset (Trunk rev. No.) | v3b |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3b (717) |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse | Date Tested |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Skylight | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Building Geometry
Fenestrations
Type | Skylight to Roof Ratio (Frac) | Overall U value (Btu/h-°F-ft2) | SHGC | Visual Transmittance
| CondSRR | FenConsRef:Ufactor | FenConsRef:SHGC | FenConsRef:VT
Skylight | 0.07 | 0.55 | 0.2 | 0.4
Baseline
Building Geometry
Fenestrations
Type | Skylight to Roof Ratio (Frac) | Overall U value (Btu/h-°F-ft2) | SHGC | Visual Transmittance
| CondSRR | FenConsRef:Ufactor | FenConsRef:SHGC | FenConsRef:VT
Skylights | 0.05 | 0.58 | 0.25 | 0.49

## 080006S-Whse-Run08 (hidden)
General Details |  | Model/Software Details |  |  | Key
Test Name | 080006S-Whse-Run08 | Model Revision no. |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006S-Whse-Run08.cibd | Version of Ruleset (Trunk rev. No.) | v3b | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3b (717) | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse | Date Tested |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Skylight | Testing Performed by | Sandeep Doddaballapur | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Daylighting
Fenestrations
Type |  | Skylight to Roof Ratio (Frac)
CondSRR
Skylight |  | 0.14
Baseline
Daylighting
Fenestrations
Type |  | Skylight to Roof Ratio (Frac)
CondSRR
Skylight |  | 0.05

## 040006S-OffLrg-Run11 (hidden)
General Details |  | Model/Software Details | [5 empty] | Key
Test Name | 040006S-OffLrg-Run11 | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 040006S-OffLrg-Run11.cibd | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Space Function | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed | [34 empty] | vvv Insert below | [33 empty] | vvv Insert below
Internal Load Components | [34 empty] | Space Interior Loads Electric Use Report | [33 empty] | Space Interior Loads Electric Use Report
Space | [39 empty] | Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated | [17 empty] | Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated |  |  |  | Non-Regulated
Space Name | Space Function | Space Floor Area (ft2) |  | People Density (ppl/1000ft2) |  | People (total number) |  | Occupancy Density - Schedule Name |  | Sensible Heat/person (Btu/h-person) |  | Latent Heat/person (Btu/h-person) |  | Lighting Power Density (W/ft2) |  | LPD - Schedule Name |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name |  | Hot Water Load/person (gal/h-person) |  | SHW Schedule |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  | Simulated Ventilation (cfm) |  | Cooling Thermostat Schedule |  | Heating Thermostat Schedule | Space |  |  |  |  | Interior Lighting |  |  |  | Interior Lighting |  |  |  | Receptacle |  |  |  | Process |  |  |  | Commercial Refrigeration | [12 empty] | Space |  |  |  |  | Interior Lighting |  |  |  | Interior Lighting |  |  |  | Receptacle |  |  |  | Process |  |  |  | Commercial Refrigeration
Spc |  |  |  | OccDens |  |  |  | OccSchRef:Name |  | OccSensHtRt |  | OccLatHtRt |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | RecptPwrDens |  | RecptSchRef:Name |  | Spc:HotWtrHtgRt |  | Spc:HotWtrHtgSchRef |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZnRef:ClgTstatSchRef |  | ThrmlZnRef:HtgTstatSchRef | Name | Conditioning Type | Space Function | Floor Area | Multiplier | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | [9 empty] | Name | Conditioning Type | Space Function | Floor Area | Multiplier | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use | Power Density | Schedule Name | Schedule | Energy Use
Basement Spc | Office (Greater than 250 square feet in floor area) | 38353 |  | 15 |  | 575.295 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 5753 |  | OfficeClgSetPt |  | OfficeHtgSetPt |  |  |  | (ft2) |  | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | [12 empty] | (ft2) |  | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh) | (W/ft2) |  | (FLH) | (kWh)
Core_bottom | Retail Merchandise Sales, Wholesale Showroom | 27257.6 |  | 33 |  | 899.5008 |  | RetailOccupancy |  | 250 |  | 200 |  | 1 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 7.5 |  | 0.2 |  | 6746 |  | RetailClgSetPt |  | RetailHtgSetPt | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 38353 | 1 | 0.75 | OfficeLights | 2253.1 | 64809.8 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 164275 | [17 empty] | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 38353 | 1 | 0.75 | OfficeLights | 2253.1 | 64809.8 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 164275
GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | 1 | 1 | RetailLights | 3459.4 | 94295.1 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 99118.3 | [17 empty] | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | 1 | 1.2 | RetailLights | 3459.4 | 113154 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 99118.3
Perimeter_bot_ZN_1 | Lobby, Main Entry | 3373.6 |  | 67 |  | 226.0312 |  | RetailOccupancy |  | 250 |  | 250 |  | 1.5 |  | RetailLights |  | 0.5 |  | RetailReceptacle |  | 0.09 |  | RetailServiceHotWater |  | 7.5 |  | 0.15 |  | 1695 |  | RetailClgSetPt |  | RetailHtgSetPt | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 1 | [29 empty] | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 1
Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.1 |  | 10 |  | 21.741 |  | RetailOccupancy |  | 250 |  | 250 |  | 0.5 |  | RetailLights |  | 0.2 |  | RetailReceptacle |  | 0 |  | RetailServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | RetailClgSetPt |  | RetailHtgSetPt | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | 3373.61 | 1 | 1.5 | RetailLights | 3459.4 | 17506 |  |  |  |  | 0.5 | RetailReceptacle | 3636.35 | 6133.82 | [17 empty] | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | 3373.61 | 1 | 1.5 | RetailLights | 3459.4 | 17506 |  |  |  |  | 0.5 | RetailReceptacle | 3636.35 | 6133.82
Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom | 3373.6 |  | 33 |  | 111.3288 |  | RetailOccupancy |  | 250 |  | 200 |  | 1 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 7.5 |  | 0.2 |  | 835 |  | RetailClgSetPt |  | RetailHtgSetPt | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 1 | 0.5 | RetailLights | 3459.4 | 3760.46 |  |  |  |  | 0.2 | RetailReceptacle | 3636.35 | 1581.12 | [17 empty] | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 1 | 0.6 | RetailLights | 3459.4 | 4512.55 |  |  |  |  | 0.2 | RetailReceptacle | 3636.35 | 1581.12
Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom | 2174 |  | 33 |  | 71.742 |  | RetailOccupancy |  | 250 |  | 200 |  | 1 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 7.5 |  | 0.2 |  | 538 |  | RetailClgSetPt |  | RetailHtgSetPt | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | 1 | 1 | RetailLights | 3459.4 | 11670.8 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 12267.7 | [17 empty] | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | 1 | 1.2 | RetailLights | 3459.4 | 14004.9 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 12267.7
Core_mid | Medical and Clinical Care | 27257.6 |  | 10 |  | 272.576 |  | HealthOccupancy |  | 250 |  | 200 |  | 1 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.2 |  | 5452 |  | HealthClgSetPt |  | HealthHtgSetPt | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | 1 | 1 | RetailLights | 3459.4 | 7520.86 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 7905.55 | [17 empty] | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | 1 | 1.2 | RetailLights | 3459.4 | 9025.03 |  |  |  |  | 1 | RetailReceptacle | 3636.35 | 7905.55
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Core_mid | DirectlyConditioned | Medical and Clinical Care | 27257.6 | 5 | 1 | HealthLights | 2806.45 | 382486 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 622660 | [17 empty] | Core_mid | DirectlyConditioned | Medical and Clinical Care | 27257.6 | 5 | 1.2 | HealthLights | 2806.45 | 458983 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 622660
Perimeter_mid_ZN_1 | Medical and Clinical Care | 3373.6 |  | 10 |  | 33.736 |  | HealthOccupancy |  | 250 |  | 200 |  | 1 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.2 |  | 675 |  | HealthClgSetPt |  | HealthHtgSetPt | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 5 | [29 empty] | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 5
Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.1 |  | 10 |  | 21.741 |  | HealthOccupancy |  | 250 |  | 250 |  | 0.5 |  | HealthLights |  | 0.2 |  | HealthReceptacle |  | 0 |  | HealthServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | HealthClgSetPt |  | HealthHtgSetPt | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | 3373.61 | 5 | 1 | HealthLights | 2806.45 | 47339.4 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 77065.1 | [17 empty] | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | 3373.61 | 5 | 1.2 | HealthLights | 2806.45 | 56807.3 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 77065.1
Perimeter_mid_ZN_3 | Medical and Clinical Care | 3373.6 |  | 10 |  | 33.736 |  | HealthOccupancy |  | 250 |  | 200 |  | 1 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.2 |  | 675 |  | HealthClgSetPt |  | HealthHtgSetPt | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 5 | 0.5 | HealthLights | 2806.45 | 15253.4 |  |  |  |  | 0.2 | HealthReceptacle | 3045.8 | 6621.72 | [17 empty] | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 5 | 0.6 | HealthLights | 2806.45 | 18304.1 |  |  |  |  | 0.2 | HealthReceptacle | 3045.8 | 6621.72
Perimeter_mid_ZN_4 | Medical and Clinical Care | 2174 |  | 10 |  | 21.74 |  | HealthOccupancy |  | 250 |  | 200 |  | 1 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.2 |  | 435 |  | HealthClgSetPt |  | HealthHtgSetPt | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | 3373.63 | 5 | 1 | HealthLights | 2806.45 | 47339.7 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 77065.6 | [17 empty] | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | 3373.63 | 5 | 1.2 | HealthLights | 2806.45 | 56807.6 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 77065.6
Core_hi | Office (Greater than 250 square feet in floor area) | 27257.6 |  | 15 |  | 408.864 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.16197 |  | 4415 |  | OfficeClgSetPt |  | OfficeHtgSetPt | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | 2174.04 | 5 | 1 | HealthLights | 2806.45 | 30506.6 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 49662.6 | [17 empty] | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | 2174.04 | 5 | 1.2 | HealthLights | 2806.45 | 36607.9 |  |  |  |  | 1.5 | HealthReceptacle | 3045.8 | 49662.6
HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 27257.6 | 5 | 0.75 | OfficeLights | 2253.1 | 230303 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 583756 | [17 empty] | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 27257.6 | 5 | 0.75 | OfficeLights | 2253.1 | 230303 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 583756
Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) | 3373.6 |  | 15 |  | 50.604 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 506 |  | OfficeClgSetPt |  | OfficeHtgSetPt | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 5 | [29 empty] | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 5
Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.1 |  | 10 |  | 21.741 |  | OfficeOccupancy |  | 250 |  | 250 |  | 0.5 |  | OfficeLights |  | 0.2 |  | OfficeReceptacle |  | 0 |  | OfficeServiceHotWater |  | 0 |  | 0 |  | 326 |  | NONE |  | NONE | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.61 | 5 | 0.75 | OfficeLights | 2253.1 | 28504.1 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 72250.1 | [17 empty] | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.61 | 5 | 0.75 | OfficeLights | 2253.1 | 28504.1 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 72250.1
Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) | 3373.6 |  | 15 |  | 50.604 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 506 |  | OfficeClgSetPt |  | OfficeHtgSetPt | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 5 | 0.5 | OfficeLights | 2253.1 | 12245.9 |  |  |  |  | 0.2 | OfficeReceptacle | 2855.5 | 6208 | [17 empty] | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 5 | 0.6 | OfficeLights | 2253.1 | 14695.1 |  |  |  |  | 0.2 | OfficeReceptacle | 2855.5 | 6208
Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) | 2174 |  | 15 |  | 32.61 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | OfficeClgSetPt |  | OfficeHtgSetPt | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.63 | 5 | 0.75 | OfficeLights | 2253.1 | 28504.3 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 72250.6 | [17 empty] | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.63 | 5 | 0.75 | OfficeLights | 2253.1 | 28504.3 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 72250.6
Core_top | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 |  | 67 |  | 1826.2592 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.2 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 7.5 |  | 0.15 |  | 13697 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 2174.04 | 5 | 0.75 | OfficeLights | 2253.1 | 18368.7 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 46559.7 | [17 empty] | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 2174.04 | 5 | 0.75 | OfficeLights | 2253.1 | 18368.7 |  |  |  |  | 1.5 | OfficeReceptacle | 2855.5 | 46559.7
Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.6 |  | 67 |  | 226.0312 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.2 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 7.5 |  | 0.15 |  | 1695 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | 1 | 1.2 | AssemblyLights | 3340.2 | 109255 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 104641 | [17 empty] | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | 1 | 1.4 | AssemblyLights | 3340.2 | 127464 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 104641
Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.1 |  | 10 |  | 21.741 |  | AssemblyOccupancy |  | 250 |  | 250 |  | 0.5 |  | AssemblyLights |  | 0.2 |  | AssemblyReceptacle |  | 0 |  | AssemblyServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | 1 | 1.2 | AssemblyLights | 3340.2 | 13522.2 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 12951.1 | [17 empty] | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | 1 | 1.4 | AssemblyLights | 3340.2 | 15776 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 12951.1
Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.6 |  | 67 |  | 226.0312 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.2 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 7.5 |  | 0.15 |  | 1695 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 1 | 0.5 | AssemblyLights | 3340.2 | 3630.88 |  |  |  |  | 0.2 | AssemblyReceptacle | 3838.95 | 1669.21 | [17 empty] | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | 1 | 0.6 | AssemblyLights | 3340.2 | 4357.06 |  |  |  |  | 0.2 | AssemblyReceptacle | 3838.95 | 1669.21
Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas | 2174 |  | 67 |  | 145.658 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.2 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 7.5 |  | 0.15 |  | 1092 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | 1 | 1.2 | AssemblyLights | 3340.2 | 13522.3 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 12951.2 | [17 empty] | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | 1 | 1.4 | AssemblyLights | 3340.2 | 15776.1 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 12951.2
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | - | - | - | - | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | 1 | 1.2 | AssemblyLights | 3340.2 | 8714.06 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 8346.01 | [17 empty] | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | 1 | 1.4 | AssemblyLights | 3340.2 | 10166.4 |  |  |  |  | 1 | AssemblyReceptacle | 3838.95 | 8346.01
[35 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 1 | [29 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | 1
Ventilation
Building Story
Name | Floor Multiplier | Floor Area (ft2) |  | Ventilation (cfm)
Basement | 1 | 38353 |  | 5753
GroundFloor | 1 | 38353 |  | 10141
MidFloor | 5 | 191764.9 |  | 7562
HiFloor | 5 | 191764.9 |  | 5753
TopFloor | 1 | 38353 |  | 18506
Baseline
Internal Load Components | [34 empty] | Space Loads Report | [33 empty] | Space Loads Report
Space | [34 empty] | Space | [5 empty] | Occupancy |  |  |  |  | Service Hot Water |  | Ventilation | [5 empty] | Infiltration |  |  | Thermal Zone | [11 empty] | Space | [5 empty] | Occupancy |  |  |  |  | Service Hot Water |  | Ventilation | [5 empty] | Infiltration |  |  | Thermal Zone
Space Name | Space Function | Space Floor Area (ft2) |  | People Density (ppl/1000ft2) |  | People (total number) |  | Occupancy Density - Schedule Name |  | Sensible Heat/person (Btu/h-person) |  | Latent Heat/person (Btu/h-person) |  | Lighting Power Density (W/ft2) |  | LPD - Schedule Name |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name |  | Hot Water Load/person (gal/h-person) |  | SHW Schedule |  | Simulated VentPerPerson (cfm/person) |  | Simulated VentPerArea (cfm/ft2) |  |  |  | Cooling Thermostat Schedule |  | Heating Thermostat Schedule | Name | Conditioning Type | Space Function | Floor Area | Story Name | Multiplier | Density | Number | Schedule Name | Sensible Heat Rate | Latent Heat Rate | SHW Use | Schedule Name | Prop. DsgnVentPerArea | Prop. DsgnVentPerPerson | Code VentPerArea | Code VentPerPerson | Sim. Area Flow | Sim. Person Flow | Method | Schedule Name | Design Infiltration Rate | Clg Tstat Sch | Htg Tstat Sch | [10 empty] | Name | Conditioning Type | Space Function | Floor Area | Story Name | Multiplier | Density | Number | Schedule Name | Sensible Heat Rate | Latent Heat Rate | SHW Use | Schedule Name | Prop. DsgnVentPerArea | Prop. DsgnVentPerPerson | Code VentPerArea | Code VentPerPerson | Sim. Area Flow | Sim. Person Flow | Method | Schedule Name | Design Infiltration Rate | Clg Tstat Sch | Htg Tstat Sch
Spc |  |  |  | OccDens |  |  |  | OccSchRef:Name |  | OccSensHtRt |  | OccLatHtRt |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | RecptPwrDens |  | RecptSchRef:Name |  | Spc:HotWtrHtgRt |  | Spc:HotWtrHtgSchRef |  | ThrmlZn:VentPerPersonSim |  | ThrmlZn:VentPerAreaSim |  |  |  | ThrmlZnRef:ClgTstatSchRef |  | ThrmlZnRef:HtgTstatSchRef |  |  |  | (ft2) |  |  | (ppl/1000ft2) | (people) |  | (Btu/h-person) | (Btu/h-person) | (gal/min) |  | (cfm/ft2) | (cfm/person) | (cfm/ft2) | (cfm/person) | (cfm) | (cfm) |  |  | (cfm/ft2) | [15 empty] | (ft2) |  |  | (ppl/1000ft2) | (people) |  | (Btu/h-person) | (Btu/h-person) | (gal/min) |  | (cfm/ft2) | (cfm/person) | (cfm/ft2) | (cfm/person) | (cfm) | (cfm) |  |  | (cfm/ft2)
Basement Spc | Office (Greater than 250 square feet in floor area) | 38353 |  | 15 |  | 575.295 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.15 |  | 5753 |  | OfficeClgSetPt |  | OfficeHtgSetPt | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 38353 | Basement | 1 | 15 | 575.295 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 10 | 0.15 | 7.5 | 5752.95 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 38353 | Basement | 1 | 15 | 575.295 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 10 | 0.15 | 7.5 | 5752.95 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
Core_bottom | Retail Merchandise Sales, Wholesale Showroom | 27257.6 |  | 33 |  | 899.5008 |  | RetailOccupancy |  | 250 |  | 200 |  | 1.2 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 7.5 |  | 0.2 |  | 6746 |  | RetailClgSetPt |  | RetailHtgSetPt | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | GroundFloor | 1 | 33 | 899.502 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.2475 | 7.5 | 0.2 | 7.5 | 5451.53 | 6746.27 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | GroundFloor | 1 | 33 | 899.502 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.2475 | 7.5 | 0.2 | 7.5 | 5451.53 | 6746.27 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | GroundFloor | 1 | -99996 | 0 | (null) | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | GroundFloor | 1 | -99996 | 0 | (null) | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Perimeter_bot_ZN_1 | Lobby, Main Entry | 3373.6 |  | 67 |  | 226.0312 |  | RetailOccupancy |  | 250 |  | 250 |  | 1.5 |  | RetailLights |  | 0.5 |  | RetailReceptacle |  | 0.09 |  | RetailServiceHotWater |  | 7.5 |  | 0.15 |  | 1695 |  | RetailClgSetPt |  | RetailHtgSetPt | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | 3373.61 | GroundFloor | 1 | 67 | 226.032 | RetailOccupancy | 250 | 250 | 0.09 | RetailServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 506.042 | 1695.24 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | 3373.61 | GroundFloor | 1 | 67 | 226.032 | RetailOccupancy | 250 | 250 | 0.09 | RetailServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 506.042 | 1695.24 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.1 |  | 10 |  | 21.741 |  | RetailOccupancy |  | 250 |  | 250 |  | 0.6 |  | RetailLights |  | 0.2 |  | RetailReceptacle |  | 0 |  | RetailServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | RetailClgSetPt |  | RetailHtgSetPt | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | GroundFloor | 1 | 10 | 21.7405 | RetailOccupancy | 250 | 250 | 0 | RetailServiceHotWater | 0.15 | 15 | 0.15 | 7.5 | 326.108 | 0 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | GroundFloor | 1 | 10 | 21.7405 | RetailOccupancy | 250 | 250 | 0 | RetailServiceHotWater | 0.15 | 15 | 0.15 | 7.5 | 326.108 | 0 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom | 3373.6 |  | 33 |  | 111.3288 |  | RetailOccupancy |  | 250 |  | 200 |  | 1.2 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 7.5 |  | 0.2 |  | 835 |  | RetailClgSetPt |  | RetailHtgSetPt | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | GroundFloor | 1 | 33 | 111.33 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.2475 | 7.5 | 0.2 | 7.5 | 674.727 | 834.975 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | GroundFloor | 1 | 33 | 111.33 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.2475 | 7.5 | 0.2 | 7.5 | 674.727 | 834.975 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom | 2174 |  | 33 |  | 71.742 |  | RetailOccupancy |  | 250 |  | 200 |  | 1.2 |  | RetailLights |  | 1 |  | RetailReceptacle |  | 0.18 |  | RetailServiceHotWater |  | 7.5 |  | 0.2 |  | 538 |  | RetailClgSetPt |  | RetailHtgSetPt | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | GroundFloor | 1 | 33 | 71.7432 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.2475 | 7.5 | 0.2 | 7.5 | 434.807 | 538.074 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt | [10 empty] | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | GroundFloor | 1 | 33 | 71.7432 | RetailOccupancy | 250 | 200 | 0.18 | RetailServiceHotWater | 0.2475 | 7.5 | 0.2 | 7.5 | 434.807 | 538.074 | FlowExteriorWallArea | RetailInfiltration | 0.0448 | RetailClgSetpt | RetailHtgSetpt
Core_mid | Medical and Clinical Care | 27257.6 |  | 10 |  | 272.576 |  | HealthOccupancy |  | 250 |  | 200 |  | 1.2 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.15216 |  | 4147 |  | HealthClgSetPt |  | HealthHtgSetPt | Core_mid | DirectlyConditioned | Medical and Clinical Care | 27257.6 | MidFloor | 5 | 10 | 272.576 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 20 | 0.15 | 7.5 | 5451.53 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Core_mid | DirectlyConditioned | Medical and Clinical Care | 27257.6 | MidFloor | 5 | 10 | 272.576 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 20 | 0.15 | 7.5 | 4147.42 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | MidFloor | 5 | -99996 | 0 | (null) | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | MidFloor | 5 | -99996 | 0 | (null) | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Perimeter_mid_ZN_1 | Medical and Clinical Care | 3373.6 |  | 10 |  | 33.736 |  | HealthOccupancy |  | 250 |  | 200 |  | 1.2 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.15216 |  | 513 |  | HealthClgSetPt |  | HealthHtgSetPt | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | 3373.61 | MidFloor | 5 | 10 | 33.7361 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 20 | 0.15 | 7.5 | 674.723 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | 3373.61 | MidFloor | 5 | 10 | 33.7361 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 20 | 0.15 | 7.5 | 513.316 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.1 |  | 10 |  | 21.741 |  | HealthOccupancy |  | 250 |  | 250 |  | 0.6 |  | HealthLights |  | 0.2 |  | HealthReceptacle |  | 0 |  | HealthServiceHotWater |  | 0 |  | 0.11412 |  | 248 |  | HealthClgSetPt |  | HealthHtgSetPt | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | MidFloor | 5 | 10 | 21.7405 | HealthOccupancy | 250 | 250 | 0 | HealthServiceHotWater | 0.15 | 15 | 0.15 | 7.5 | 326.108 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | MidFloor | 5 | 10 | 21.7405 | HealthOccupancy | 250 | 250 | 0 | HealthServiceHotWater | 0.15 | 15 | 0.15 | 7.5 | 248.097 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
Perimeter_mid_ZN_3 | Medical and Clinical Care | 3373.6 |  | 10 |  | 33.736 |  | HealthOccupancy |  | 250 |  | 200 |  | 1.2 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.15216 |  | 513 |  | HealthClgSetPt |  | HealthHtgSetPt | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | 3373.63 | MidFloor | 5 | 10 | 33.7363 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 20 | 0.15 | 7.5 | 674.727 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | 3373.63 | MidFloor | 5 | 10 | 33.7363 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 20 | 0.15 | 7.5 | 513.32 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
Perimeter_mid_ZN_4 | Medical and Clinical Care | 2174 |  | 10 |  | 21.74 |  | HealthOccupancy |  | 250 |  | 200 |  | 1.2 |  | HealthLights |  | 1.5 |  | HealthReceptacle |  | 0.24 |  | HealthServiceHotWater |  | 0 |  | 0.15216 |  | 331 |  | HealthClgSetPt |  | HealthHtgSetPt | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | 2174.04 | MidFloor | 5 | 10 | 21.7404 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 20 | 0.15 | 7.5 | 434.807 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt | [10 empty] | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | 2174.04 | MidFloor | 5 | 10 | 21.7404 | HealthOccupancy | 250 | 200 | 0.24 | HealthServiceHotWater | 0.2 | 20 | 0.15 | 7.5 | 330.793 | 0 | FlowExteriorWallArea | HealthInfiltration | 0.0448 | HealthClgSetpt | HealthHtgSetpt
Core_hi | Office (Greater than 250 square feet in floor area) | 27257.6 |  | 15 |  | 408.864 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.16197 |  | 4415 |  | OfficeClgSetPt |  | OfficeHtgSetPt | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 27257.6 | HiFloor | 5 | 15 | 408.865 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.16197 | 10.7982 | 0.15 | 7.5 | 4415 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 27257.6 | HiFloor | 5 | 15 | 408.865 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.16197 | 10.7982 | 0.15 | 7.5 | 4414.81 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | HiFloor | 5 | -99996 | 0 | (null) | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | HiFloor | 5 | -99996 | 0 | (null) | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) | 3373.6 |  | 15 |  | 50.604 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.14999 |  | 506 |  | OfficeClgSetPt |  | OfficeHtgSetPt | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.61 | HiFloor | 5 | 15 | 50.6042 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 10 | 0.15 | 7.5 | 506.042 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.61 | HiFloor | 5 | 15 | 50.6042 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 10 | 0.15 | 7.5 | 506.02 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.1 |  | 10 |  | 21.741 |  | OfficeOccupancy |  | 250 |  | 250 |  | 0.6 |  | OfficeLights |  | 0.2 |  | OfficeReceptacle |  | 0 |  | OfficeServiceHotWater |  | 0 |  | 0 |  | 0 |  | NONE |  | NONE | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | HiFloor | 5 | 10 | 21.7405 | OfficeOccupancy | 250 | 250 | 0 | OfficeServiceHotWater | 0 | 0 | 0.15 | 7.5 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | HiFloor | 5 | 10 | 21.7405 | OfficeOccupancy | 250 | 250 | 0 | OfficeServiceHotWater | 0 | 0 | 0.15 | 7.5 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) | 3373.6 |  | 15 |  | 50.604 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.14999 |  | 506 |  | OfficeClgSetPt |  | OfficeHtgSetPt | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.63 | HiFloor | 5 | 15 | 50.6045 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 10 | 0.15 | 7.5 | 506.045 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 3373.63 | HiFloor | 5 | 15 | 50.6045 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 10 | 0.15 | 7.5 | 506.024 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) | 2174 |  | 15 |  | 32.61 |  | OfficeOccupancy |  | 250 |  | 200 |  | 0.75 |  | OfficeLights |  | 1.5 |  | OfficeReceptacle |  | 0.18 |  | OfficeServiceHotWater |  | 0 |  | 0.14999 |  | 326 |  | OfficeClgSetPt |  | OfficeHtgSetPt | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 2174.04 | HiFloor | 5 | 15 | 32.6105 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 10 | 0.15 | 7.5 | 326.105 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt | [10 empty] | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | 2174.04 | HiFloor | 5 | 15 | 32.6105 | OfficeOccupancy | 250 | 200 | 0.18 | OfficeServiceHotWater | 0.15 | 10 | 0.15 | 7.5 | 326.091 | 0 | FlowExteriorWallArea | OfficeInfiltration | 0.0448 | OfficeClgSetpt | OfficeHtgSetpt
Core_top | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 |  | 67 |  | 1826.2592 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.4 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 7.5 |  | 0.15 |  | 13697 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | TopFloor | 1 | 67 | 1826.26 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 4088.65 | 13697 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | TopFloor | 1 | 67 | 1826.26 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 4088.65 | 13697 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.6 |  | 67 |  | 226.0312 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.4 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 7.5 |  | 0.15 |  | 1695 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | TopFloor | 1 | 67 | 226.032 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 506.042 | 1695.24 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | TopFloor | 1 | 67 | 226.032 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 506.042 | 1695.24 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.1 |  | 10 |  | 21.741 |  | AssemblyOccupancy |  | 250 |  | 250 |  | 0.6 |  | AssemblyLights |  | 0.2 |  | AssemblyReceptacle |  | 0 |  | AssemblyServiceHotWater |  | 0 |  | 0.15 |  | 326 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | TopFloor | 1 | 10 | 21.7405 | AssemblyOccupancy | 250 | 250 | 0 | AssemblyServiceHotWater | 0.15 | 15 | 0.15 | 7.5 | 326.108 | 0 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | TopFloor | 1 | 10 | 21.7405 | AssemblyOccupancy | 250 | 250 | 0 | AssemblyServiceHotWater | 0.15 | 15 | 0.15 | 7.5 | 326.108 | 0 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.6 |  | 67 |  | 226.0312 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.4 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 7.5 |  | 0.15 |  | 1695 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | TopFloor | 1 | 67 | 226.034 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 506.045 | 1695.25 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | TopFloor | 1 | 67 | 226.034 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 506.045 | 1695.25 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas | 2174 |  | 67 |  | 145.658 |  | AssemblyOccupancy |  | 245 |  | 155 |  | 1.4 |  | AssemblyLights |  | 1 |  | AssemblyReceptacle |  | 0.09 |  | AssemblyServiceHotWater |  | 7.5 |  | 0.15 |  | 1093 |  | AssemblyClgSetPt |  | AssemblyHtgSetPt | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | TopFloor | 1 | 67 | 145.66 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 326.105 | 1092.45 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt | [10 empty] | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | TopFloor | 1 | 67 | 145.66 | AssemblyOccupancy | 245 | 155 | 0.09 | AssemblyServiceHotWater | 0.5025 | 7.5 | 0.15 | 7.5 | 326.105 | 1092.45 | FlowExteriorWallArea | AssemblyInfiltration | 0.0448 | AssemblyClgSetpt | AssemblyHtgSetpt
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | TopFloor | 1 | -99996 | 0 | (null) | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE | [10 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | TopFloor | 1 | -99996 | 0 | (null) | -99996 | -99996 | -99996 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | FlowExteriorWallArea | On | 0.0448 | NONE | NONE
Ventilation
Building Story | [34 empty] | Space Interior Lighting Report | [33 empty] | Space Interior Lighting Report
Name | Floor Multiplier | Floor Area (ft2) |  | Ventilation (cfm) | [30 empty] | Space |  |  |  |  | Regulated | [9 empty] | Non-Regulated | [18 empty] | Space |  |  |  |  | Regulated | [9 empty] | Non-Regulated
[35 empty] | Name | Conditioning Type | Space Function | Lighting Status | Floor Area | Installed Power | Schedule Name | Schedule | Lighting System Count | Lighting Control Credit | Simulated Power | Simulated LPD | Power | Schedule Name | Schedule | LPD | Schedule Name | Schedule | LPD | [15 empty] | Name | Conditioning Type | Space Function | Lighting Status | Floor Area | Installed Power | Schedule Name | Schedule | Lighting System Count | Lighting Control Credit | General Lighting Power | Area Category Allowances | Tailored Allowances | Simulated Power | Simulated LPD | Power | Schedule Name | Schedule | LPD
Basement | 1 | 38353 |  | 5753 | [34 empty] | (ft2) | (Watts) |  | (FLH) |  | (Watts) | (Watts) | (Watts/ft2) | (Watts) |  | (FLH) | (Watts/ft2) |  | (FLH) | (Watts/ft2) | [19 empty] | (ft2) | (Watts) |  | (FLH) |  | (Watts) | (Watts) | (Watts) | (Watts) | (Watts) | (Watts/ft2) | (Watts) |  | (FLH) | (Watts/ft2)
GroundFloor | 1 | 38353 |  | 10141 | [30 empty] | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 38353 | 28764.7 | OfficeLights | 2253.1 | -99996 | 0 | 28764.7 | 0.75 | [22 empty] | Basement Spc | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 38353 | 0 | OfficeLights | 2253.1 | -99996 | 0 | 28764.7 | 0 | 0 | 28764.7 | 0.75
MidFloor | 5 | 191764.9 |  | 5753 | [30 empty] | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 27257.6 | 27257.6 | RetailLights | 3459.4 | -99996 | 0 | 27257.6 | 1 | [22 empty] | Core_bottom | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 27257.6 | 0 | RetailLights | 3459.4 | -99996 | 0 | 32709.2 | 0 | 0 | 32709.2 | 1.2
HiFloor | 5 | 191764.9 |  | 5753 | [30 empty] | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0 | [29 empty] | GroundFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
TopFloor | 1 | 38353 |  | 18506 | [30 empty] | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | New | 3373.61 | 5060.42 | RetailLights | 3459.4 | -99996 | 0 | 5060.42 | 1.5 | [22 empty] | Perimeter_bot_ZN_1 | DirectlyConditioned | Lobby, Main Entry | New | 3373.61 | 0 | RetailLights | 3459.4 | -99996 | 0 | 5060.42 | 0 | 0 | 5060.42 | 1.5
[35 empty] | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | 1087.03 | RetailLights | 3459.4 | -99996 | 0 | 1087.03 | 0.5 | [22 empty] | Perimeter_bot_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | 0 | RetailLights | 3459.4 | -99996 | 0 | 1304.43 | 0 | 0 | 1304.43 | 0.6
[35 empty] | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 3373.63 | 3373.63 | RetailLights | 3459.4 | -99996 | 0 | 3373.63 | 1 | [22 empty] | Perimeter_bot_ZN_3 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 3373.63 | 0 | RetailLights | 3459.4 | -99996 | 0 | 4048.36 | 0 | 0 | 4048.36 | 1.2
[35 empty] | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 2174.04 | 2174.04 | RetailLights | 3459.4 | -99996 | 0 | 2174.04 | 1 | [22 empty] | Perimeter_bot_ZN_4 | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | New | 2174.04 | 0 | RetailLights | 3459.4 | -99996 | 0 | 2608.84 | 0 | 0 | 2608.84 | 1.2
[35 empty] | Core_mid | DirectlyConditioned | Medical and Clinical Care | New | 27257.6 | 27257.6 | HealthLights | 2806.45 | -99996 | 0 | 27257.6 | 1 | [22 empty] | Core_mid | DirectlyConditioned | Medical and Clinical Care | New | 27257.6 | 0 | HealthLights | 2806.45 | -99996 | 0 | 32709.2 | 0 | 0 | 32709.2 | 1.2
[35 empty] | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0 | [29 empty] | MidFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
[35 empty] | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | New | 3373.61 | 3373.61 | HealthLights | 2806.45 | -99996 | 0 | 3373.61 | 1 | [22 empty] | Perimeter_mid_ZN_1 | DirectlyConditioned | Medical and Clinical Care | New | 3373.61 | 0 | HealthLights | 2806.45 | -99996 | 0 | 4048.34 | 0 | 0 | 4048.34 | 1.2
[35 empty] | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | 1087.03 | HealthLights | 2806.45 | -99996 | 0 | 1087.03 | 0.5 | [22 empty] | Perimeter_mid_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | 0 | HealthLights | 2806.45 | -99996 | 0 | 1304.43 | 0 | 0 | 1304.43 | 0.6
[35 empty] | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | New | 3373.63 | 3373.63 | HealthLights | 2806.45 | -99996 | 0 | 3373.63 | 1 | [22 empty] | Perimeter_mid_ZN_3 | DirectlyConditioned | Medical and Clinical Care | New | 3373.63 | 0 | HealthLights | 2806.45 | -99996 | 0 | 4048.36 | 0 | 0 | 4048.36 | 1.2
[35 empty] | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | New | 2174.04 | 2174.04 | HealthLights | 2806.45 | -99996 | 0 | 2174.04 | 1 | [22 empty] | Perimeter_mid_ZN_4 | DirectlyConditioned | Medical and Clinical Care | New | 2174.04 | 0 | HealthLights | 2806.45 | -99996 | 0 | 2608.84 | 0 | 0 | 2608.84 | 1.2
[35 empty] | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 27257.6 | 20443.2 | OfficeLights | 2253.1 | -99996 | 0 | 20443.2 | 0.75 | [22 empty] | Core_hi | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 27257.6 | 0 | OfficeLights | 2253.1 | -99996 | 0 | 20443.2 | 0 | 0 | 20443.2 | 0.75
[35 empty] | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0 | [29 empty] | HiFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
[35 empty] | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 3373.61 | 2530.21 | OfficeLights | 2253.1 | -99996 | 0 | 2530.21 | 0.75 | [22 empty] | Perimeter_hi_ZN_1 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 3373.61 | 0 | OfficeLights | 2253.1 | -99996 | 0 | 2530.21 | 0 | 0 | 2530.21 | 0.75
[35 empty] | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | 1087.03 | OfficeLights | 2253.1 | -99996 | 0 | 1087.03 | 0.5 | [22 empty] | Perimeter_hi_ZN_2 | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | 0 | OfficeLights | 2253.1 | -99996 | 0 | 1304.43 | 0 | 0 | 1304.43 | 0.6
[35 empty] | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 3373.63 | 2530.23 | OfficeLights | 2253.1 | -99996 | 0 | 2530.23 | 0.75 | [22 empty] | Perimeter_hi_ZN_3 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 3373.63 | 0 | OfficeLights | 2253.1 | -99996 | 0 | 2530.23 | 0 | 0 | 2530.23 | 0.75
[35 empty] | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 2174.04 | 1630.53 | OfficeLights | 2253.1 | -99996 | 0 | 1630.53 | 0.75 | [22 empty] | Perimeter_hi_ZN_4 | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | New | 2174.04 | 0 | OfficeLights | 2253.1 | -99996 | 0 | 1630.53 | 0 | 0 | 1630.53 | 0.75
[35 empty] | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 27257.6 | 32709.2 | AssemblyLights | 3340.2 | -99996 | 0 | 32709.2 | 1.2 | [22 empty] | Core_top | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 27257.6 | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 38160.7 | 0 | 0 | 38160.7 | 1.4
[35 empty] | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 3373.61 | 4048.34 | AssemblyLights | 3340.2 | -99996 | 0 | 4048.34 | 1.2 | [22 empty] | Perimeter_top_ZN_1 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 3373.61 | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 4723.06 | 0 | 0 | 4723.06 | 1.4
[35 empty] | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | 1087.03 | AssemblyLights | 3340.2 | -99996 | 0 | 1087.03 | 0.5 | [22 empty] | Perimeter_top_ZN_2 | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | New | 2174.05 | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 1304.43 | 0 | 0 | 1304.43 | 0.6
[35 empty] | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 3373.63 | 4048.36 | AssemblyLights | 3340.2 | -99996 | 0 | 4048.36 | 1.2 | [22 empty] | Perimeter_top_ZN_3 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 3373.63 | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 4723.09 | 0 | 0 | 4723.09 | 1.4
[35 empty] | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 2174.04 | 2608.84 | AssemblyLights | 3340.2 | -99996 | 0 | 2608.84 | 1.2 | [22 empty] | Perimeter_top_ZN_4 | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | New | 2174.04 | 0 | AssemblyLights | 3340.2 | -99996 | 0 | 3043.65 | 0 | 0 | 3043.65 | 1.4
[35 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0 | [29 empty] | TopFloor_Plenum | Plenum | Unoccupied-Exclude from Gross Floor Area | New | 0
[35 empty] | Space Daylighting | [33 empty] | Space Daylighting
[35 empty] | Name | SpcFunc | FlrArea | DayltgCtrlType | MandMinDaylitArea | MinDimLtgFrac | MinDimPwrFrac | NumOfCtrlSteps | SkylitDaylitArea | SkylitDayltgCtrlLtgPwr | SkylitDayltgCtrlLtgFrac | SkylitDayltgIllumSetpt | SkylitDayltgIllumSetptAdjFac | SkylitDayltgAdjIllumSetpt |  | PriSideDayltgRefPtCoord[1] | PriSideDayltgRefPtCoord[2] | PriSideDayltgRefPtCoord[3] | PriSideDaylitArea | PriSideDayltgCtrlLtgPwr | PriSideDayltgCtrlLtgFrac | PriSideDayltgIllumSetpt | PriSideDayltgIllumSetptAdjFac | PriSideDayltgAdjIllumSetpt |  | SecSideDayltgRefPtCoord[1] | SecSideDayltgRefPtCoord[2] | SecSideDayltgRefPtCoord[3] | SecSideDaylitArea | SecSideDayltgCtrlLtgPwr | SecSideDayltgCtrlLtgFrac | SecSideDayltgIllumSetpt | SecSideDayltgIllumSetptAdjFac | SecSideDayltgAdjIllumSetpt | Name | SpcFunc | FlrArea | DayltgCtrlType | MandMinDaylitArea | MinDimLtgFrac | MinDimPwrFrac | NumOfCtrlSteps | SkylitDaylitArea | SkylitDayltgCtrlLtgPwr | SkylitDayltgCtrlLtgFrac | SkylitDayltgIllumSetpt | SkylitDayltgIllumSetptAdjFac | SkylitDayltgAdjIllumSetpt |  | PriSideDayltgRefPtCoord[1] | PriSideDayltgRefPtCoord[2] | PriSideDayltgRefPtCoord[3] | PriSideDaylitArea | PriSideDayltgCtrlLtgPwr | PriSideDayltgCtrlLtgFrac | PriSideDayltgIllumSetpt | PriSideDayltgIllumSetptAdjFac | PriSideDayltgAdjIllumSetpt |  | SecSideDayltgRefPtCoord[1] | SecSideDayltgRefPtCoord[2] | SecSideDayltgRefPtCoord[3] | SecSideDaylitArea | SecSideDayltgCtrlLtgPwr | SecSideDayltgCtrlLtgFrac | SecSideDayltgIllumSetpt | SecSideDayltgIllumSetptAdjFac | SecSideDayltgAdjIllumSetpt
[35 empty] | Space | [7 empty] | Skylit Zone | [6 empty] | Primary Sidelit Daylit Zone | [9 empty] | Secondary Sidelit Daylit Zone | [8 empty] | Space | [7 empty] | Skylit Zone | [6 empty] | Primary Sidelit Daylit Zone | [9 empty] | Secondary Sidelit Daylit Zone
[35 empty] | Name | Space Function | Floor Area | Control Type | MinDayltg per 140.3c | Min. Dim. Ltg. Frac. | Min Dim. Pwr. Frac. | Switched # Ctrl. Steps | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point | Name | Space Function | Floor Area | Control Type | MinDayltg per 140.3c | Min. Dim. Ltg. Frac. | Min Dim. Pwr. Frac. | Switched # Ctrl. Steps | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point |  | Ref Pt Coord [1] | Ref Pt Coord [2] | Ref Pt Coord [3] | Daylit Area | Controlled Watts | Control Fraction | Illuminance Set Pt | Illum Set Pt Adj Factor | Adj Illum. Set Point
[37 empty] | (ft2) |  | (ft2) |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  | (ft2) |  | (ft2) |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux) |  |  |  |  | (ft2) | (Watts) | (Frac) | (lux) |  | (lux)
[35 empty] | Basement Spc | Office (Greater than 250 square feet in floor area) | 38353 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 1150 | Basement Spc | Office (Greater than 250 square feet in floor area) | 38353 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 1150
[35 empty] | Core_bottom | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 825 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 1100 | Core_bottom | Retail Merchandise Sales, Wholesale Showroom | 27257.6 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 825 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 550 | -99996 | 1100
[35 empty] | GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 | GroundFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0
[35 empty] | Perimeter_bot_ZN_1 | Lobby, Main Entry | 3373.61 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 125 | -99996 | 125 |  | 119.926 | 8.2021 | 2.5 | 1901.26 | 2851.88 | 0.56357 | 125 | -99996 | 187.5 |  | 119.93 | 14.75 | 2.5 | 1471.24 | 0 | 0 | 125 | -99996 | 250 | Perimeter_bot_ZN_1 | Lobby, Main Entry | 3373.61 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 125 | -99996 | 125 |  | 119.926 | 8.2021 | 2.5 | 1901.26 | 2851.88 | 0 | 125 | -99996 | 187.5 |  | 119.93 | 14.75 | 2.5 | 1471.24 | 2206.87 | 0 | 125 | -99996 | 250
[35 empty] | Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.651 | 79.951 | 2.5 | 1239.29 | 619.646 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 2.5 | 934.458 | 0 | 0 | 75 | -99996 | 150 | Perimeter_bot_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.651 | 79.951 | 2.5 | 1239.29 | 743.575 | 0 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 2.5 | 934.458 | 560.675 | 0 | 75 | -99996 | 150
[35 empty] | Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | 119.926 | 151.7 | 2.5 | 1901.26 | 1901.26 | 0.56356 | 550 | -99996 | 825 |  | 119.93 | 145.167 | 2.5 | 1471.24 | 0 | 0 | 550 | -99996 | 1100 | Perimeter_bot_ZN_3 | Retail Merchandise Sales, Wholesale Showroom | 3373.63 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | 119.926 | 151.7 | 2.5 | 1901.26 | 2281.51 | 0 | 550 | -99996 | 825 |  | 119.93 | 145.167 | 2.5 | 1471.24 | 1765.49 | 0 | 550 | -99996 | 1100
[35 empty] | Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | 8.2021 | 79.951 | 2.5 | 1245.27 | 1245.27 | 0.57279 | 550 | -99996 | 825 |  | 14.75 | 79.9535 | 2.5 | 928.477 | 0 | 0 | 550 | -99996 | 1100 | Perimeter_bot_ZN_4 | Retail Merchandise Sales, Wholesale Showroom | 2174.04 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 550 | -99996 | 550 |  | 8.2021 | 79.951 | 2.5 | 1245.27 | 1494.33 | 0 | 550 | -99996 | 825 |  | 14.75 | 79.9535 | 2.5 | 928.477 | 1114.17 | 0 | 550 | -99996 | 1100
[35 empty] | Core_mid | Medical and Clinical Care | 27257.6 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 2475 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 3300 | Core_mid | Medical and Clinical Care | 27257.6 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 2475 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 3300
[35 empty] | MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 | MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0
[35 empty] | Perimeter_mid_ZN_1 | Medical and Clinical Care | 3373.61 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 119.926 | 8.2014 | 67.5 | 1901.26 | 1901.26 | 0.56357 | 1650 | -99996 | 2475 |  | 119.93 | 14.75 | 67.5 | 1471.24 | 0 | 0 | 1650 | -99996 | 3300 | Perimeter_mid_ZN_1 | Medical and Clinical Care | 3373.61 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 119.926 | 8.2014 | 67.5 | 1901.26 | 2281.51 | 0 | 1650 | -99996 | 2475 |  | 119.93 | 14.75 | 67.5 | 1471.24 | 1765.49 | 0 | 1650 | -99996 | 3300
[35 empty] | Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.652 | 79.951 | 67.5 | 1239.29 | 619.646 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 67.5 | 934.458 | 0 | 0 | 75 | -99996 | 150 | Perimeter_mid_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.652 | 79.951 | 67.5 | 1239.29 | 743.575 | 0 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 67.5 | 934.458 | 560.675 | 0 | 75 | -99996 | 150
[35 empty] | Perimeter_mid_ZN_3 | Medical and Clinical Care | 3373.63 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 119.926 | 151.701 | 67.5 | 1901.26 | 1901.26 | 0.56356 | 1650 | -99996 | 2475 |  | 119.93 | 145.167 | 67.5 | 1471.24 | 0 | 0 | 1650 | -99996 | 3300 | Perimeter_mid_ZN_3 | Medical and Clinical Care | 3373.63 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 119.926 | 151.701 | 67.5 | 1901.26 | 2281.51 | 0 | 1650 | -99996 | 2475 |  | 119.93 | 145.167 | 67.5 | 1471.24 | 1765.49 | 0 | 1650 | -99996 | 3300
[35 empty] | Perimeter_mid_ZN_4 | Medical and Clinical Care | 2174.04 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 8.2014 | 79.951 | 67.5 | 1245.27 | 1245.27 | 0.57279 | 1650 | -99996 | 2475 |  | 14.75 | 79.9535 | 67.5 | 928.477 | 0 | 0 | 1650 | -99996 | 3300 | Perimeter_mid_ZN_4 | Medical and Clinical Care | 2174.04 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 1650 | -99996 | 1650 |  | 8.2014 | 79.951 | 67.5 | 1245.27 | 1494.33 | 0 | 1650 | -99996 | 2475 |  | 14.75 | 79.9535 | 67.5 | 928.477 | 1114.17 | 0 | 1650 | -99996 | 3300
[35 empty] | Core_hi | Office (Greater than 250 square feet in floor area) | 27257.6 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 1150 | Core_hi | Office (Greater than 250 square feet in floor area) | 27257.6 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 1150
[35 empty] | HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 | HiFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0
[35 empty] | Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) | 3373.61 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 119.926 | 8.202 | 132.5 | 1901.26 | 1425.94 | 0.56357 | 287.5 | -99996 | 287.5 |  | 119.93 | 14.75 | 132.5 | 1471.24 | 0 | 0 | 287.5 | -99996 | 1150 | Perimeter_hi_ZN_1 | Office (Greater than 250 square feet in floor area) | 3373.61 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 119.926 | 8.202 | 132.5 | 1901.26 | 1425.94 | 0 | 287.5 | -99996 | 287.5 |  | 119.93 | 14.75 | 132.5 | 1471.24 | 1103.43 | 0 | 287.5 | -99996 | 1150
[35 empty] | Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.651 | 79.951 | 132.5 | 1239.29 | 619.646 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 132.5 | 934.458 | 0 | 0 | 75 | -99996 | 150 | Perimeter_hi_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.651 | 79.951 | 132.5 | 1239.29 | 743.575 | 0 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 132.5 | 934.458 | 560.675 | 0 | 75 | -99996 | 150
[35 empty] | Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) | 3373.63 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 119.926 | 151.7 | 132.5 | 1901.26 | 1425.94 | 0.56356 | 287.5 | -99996 | 287.5 |  | 119.93 | 145.167 | 132.5 | 1471.24 | 0 | 0 | 287.5 | -99996 | 1150 | Perimeter_hi_ZN_3 | Office (Greater than 250 square feet in floor area) | 3373.63 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 119.926 | 151.7 | 132.5 | 1901.26 | 1425.94 | 0 | 287.5 | -99996 | 287.5 |  | 119.93 | 145.167 | 132.5 | 1471.24 | 1103.43 | 0 | 287.5 | -99996 | 1150
[35 empty] | Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) | 2174.04 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 8.202 | 79.951 | 132.5 | 1245.27 | 933.954 | 0.57279 | 287.5 | -99996 | 287.5 |  | 14.75 | 79.9535 | 132.5 | 928.477 | 0 | 0 | 287.5 | -99996 | 1150 | Perimeter_hi_ZN_4 | Office (Greater than 250 square feet in floor area) | 2174.04 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 287.5 | -99996 | 287.5 |  | 8.202 | 79.951 | 132.5 | 1245.27 | 933.954 | 0 | 287.5 | -99996 | 287.5 |  | 14.75 | 79.9535 | 132.5 | 928.477 | 696.358 | 0 | 287.5 | -99996 | 1150
[35 empty] | Core_top | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 247.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 330 | Core_top | Convention, Conference, Multipurpose and Meeting Center Areas | 27257.6 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 247.5 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 165 | -99996 | 330
[35 empty] | Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 119.926 | 8.201 | 145.5 | 1901.26 | 2281.51 | 0.56357 | 165 | -99996 | 247.5 |  | 119.93 | 14.75 | 145.5 | 1471.24 | 0 | 0 | 165 | -99996 | 330 | Perimeter_top_ZN_1 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.61 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 119.926 | 8.201 | 145.5 | 1901.26 | 2661.76 | 0 | 165 | -99996 | 247.5 |  | 119.93 | 14.75 | 145.5 | 1471.24 | 2059.74 | 0 | 165 | -99996 | 330
[35 empty] | Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.652 | 79.951 | 145.5 | 1239.29 | 619.646 | 0.57004 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 145.5 | 934.458 | 0 | 0 | 75 | -99996 | 150 | Perimeter_top_ZN_2 | Corridors, Restrooms, Stairs, and Support Areas | 2174.05 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 75 | -99996 | 75 |  | 231.652 | 79.951 | 145.5 | 1239.29 | 743.575 | 0 | 75 | -99996 | 112.5 |  | 225.083 | 79.9535 | 145.5 | 934.458 | 560.675 | 0 | 75 | -99996 | 150
[35 empty] | Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 119.926 | 151.701 | 145.5 | 1901.26 | 2281.51 | 0.56356 | 165 | -99996 | 247.5 |  | 119.93 | 145.167 | 145.5 | 1471.24 | 0 | 0 | 165 | -99996 | 330 | Perimeter_top_ZN_3 | Convention, Conference, Multipurpose and Meeting Center Areas | 3373.63 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 119.926 | 151.701 | 145.5 | 1901.26 | 2661.76 | 0 | 165 | -99996 | 247.5 |  | 119.93 | 145.167 | 145.5 | 1471.24 | 2059.74 | 0 | 165 | -99996 | 330
[35 empty] | Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | Continuous | 0 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 8.201 | 79.951 | 145.5 | 1245.27 | 1494.33 | 0.57279 | 165 | -99996 | 247.5 |  | 14.75 | 79.9535 | 145.5 | 928.477 | 0 | 0 | 165 | -99996 | 330 | Perimeter_top_ZN_4 | Convention, Conference, Multipurpose and Meeting Center Areas | 2174.04 | Continuous | -99996 | 0.2 | 0.2 | -99996 | 0 | 0 | 0 | 165 | -99996 | 165 |  | 8.201 | 79.951 | 145.5 | 1245.27 | 1743.38 | 0 | 165 | -99996 | 247.5 |  | 14.75 | 79.9535 | 145.5 | 928.477 | 1299.87 | 0 | 165 | -99996 | 330
[35 empty] | TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | 0 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 | TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | None | -99996 | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0 |  | -99996 | -99996 | -99996 | 0 | 0 | 0 | 0 | -99996 | 0
[35 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[35 empty] | BuildingStory | [33 empty] | BuildingStory
[37 empty] | Floor Area (including multipliers) |  |  |  |  | Ventilation (Design) |  |  | Ventilation (For Balance) | [5 empty] | General |  | Comm. Kitchen |  | Parking Garage |  | Laboratory | [13 empty] | Floor Area (including multipliers) |  |  |  |  | Ventilation (Design) |  |  | Ventilation (For Balance) | [5 empty] | General |  | Comm. Kitchen |  | Parking Garage |  | Laboratory
[35 empty] | Name | Multiplier | Total | Cond. NRes | Cond. Res | Total Cond. | Number | Total | Code Min. | Exhaust | Total | Code Min. | Tot:Min Ratio | Exhaust | Vent:Exh Ratio | Vent Mult. | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | [10 empty] | Name | Multiplier | Total | Cond. NRes | Cond. Res | Total Cond. | Number | Total | Code Min. | Exhaust | Total | Code Min. | Tot:Min Ratio | Exhaust | Vent:Exh Ratio | Vent Mult. | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust | Vent | Exhaust
[37 empty] | (ft2) | (ft2) | (ft2) | (ft2) | (people) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) |  | (cfm) |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | [12 empty] | (ft2) | (ft2) | (ft2) | (ft2) | (people) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) |  | (cfm) |  |  | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm) | (cfm)
[35 empty] | Basement | 1 | 38353 | 38353 | 0 | 38353 | 575.3 | 5753 | 5753 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Basement | 1 | 38353 | 38353 | 0 | 38353 | 575.3 | 5753 | 5753 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | GroundFloor | 1 | 38353 | 38353 | 0 | 38353 | 1330.3 | 10141 | 10141 | 0 | 7393 | 7393 | 1 | 0 | 1 | 1 | 10141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | GroundFloor | 1 | 38353 | 38353 | 0 | 38353 | 1330.3 | 10141 | 10141 | 0 | 7393 | 7393 | 1 | 0 | 1 | 1 | 10141 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | MidFloor | 5 | 191764.9 | 191764.9 | 0 | 191764.9 | 1917.6 | 7562 | 5753 | 0 | 7562 | 5753 | 0.761 | 0 | 1 | 1 | 7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | MidFloor | 5 | 191764.9 | 191764.9 | 0 | 191764.9 | 1917.6 | 5753 | 5753 | 0 | 5753 | 5753 | 0.761 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | HiFloor | 5 | 191764.9 | 191764.9 | 0 | 191764.9 | 2822.1 | 5753 | 5753 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | HiFloor | 5 | 191764.9 | 191764.9 | 0 | 191764.9 | 2822.1 | 5753 | 5753 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | TopFloor | 1 | 38353 | 38353 | 0 | 38353 | 2445.7 | 18506 | 18506 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 18506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | TopFloor | 1 | 38353 | 38353 | 0 | 38353 | 2445.7 | 18506 | 18506 | 0 | 5753 | 5753 | 1 | 0 | 1 | 1 | 18506 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[35 empty] | Space | [33 empty] | Space
[42 empty] | Occupancy |  |  | Ventilation |  | Design Input (By Component) |  |  |  |  | Minimum Req. (By Component) |  |  |  | Simulated |  | Exhaust |  |  | ForBalance | [14 empty] | Occupancy |  |  | Ventilation |  | Design Input (By Component) |  |  |  |  | Minimum Req. (By Component) |  |  |  | Simulated |  | Exhaust |  |  | ForBalance
[35 empty] | Name | Story Name | Condg Type | Space Function | Thermal Zone | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Per Space | Calculated Flow | Per Occupant | Per Area | Per Volume | Calculated Flow |  |  | Calculated Flow | Lab Exh Type | Max Kitchen | Ventilation | Exhaust | [6 empty] | Name | Story Name | Condg Type | Space Function | Thermal Zone | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume | Per Space | Calculated Flow | Per Occupant | Per Area | Per Volume | Calculated Flow |  |  | Calculated Flow | Lab Exh Type | Max Kitchen | Ventilation | Exhaust
[40 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm) | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) |  | (cfm) | (cfm) | (cfm) | [11 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm) | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) |  | (cfm) | (cfm) | (cfm)
[35 empty] | Basement Spc | Basement | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Basement Thermal Zone | 38353 | 1 | 15 | 10 | 575.3 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 5753 | 7.5 | 0.15 | 0 | 5753 | 0 | 0.15 | 0 | UNDEFINED | 0 | 5753 | 0 | [6 empty] | Basement Spc | Basement | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Basement Thermal Zone | 38353 | 1 | 15 | 10 | 575.3 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 5753 | 7.5 | 0.15 | 0 | 5753 | 0 | 0.15 | 0 | UNDEFINED | 0 | 5753 | 0
[35 empty] | Core_bottom | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Core_bottom Thermal Zone | 27257.6 | 1 | 33 | 33 | 899.5 | Maximum | CO2Sensors | 7.5 | 0.2 | 0 | 0 | 6746 | 7.5 | 0.2 | 0 | 6746 | 7.5 | 0.2 | 0 | UNDEFINED | 0 | 5452 | 0 | [6 empty] | Core_bottom | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Core_bottom Thermal Zone | 27257.6 | 1 | 33 | 33 | 899.5 | Maximum | CO2Sensors | 7.5 | 0.2 | 0 | 0 | 6746 | 7.5 | 0.2 | 0 | 6746 | 7.5 | 0.2 | 0 | UNDEFINED | 0 | 5452 | 0
[35 empty] | GroundFloor_Plenum | GroundFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | GroundFloor_Plenum Thermal Zone | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | GroundFloor_Plenum | GroundFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | GroundFloor_Plenum Thermal Zone | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[35 empty] | Perimeter_bot_ZN_1 | GroundFloor | DirectlyConditioned | Lobby, Main Entry | Perimeter_bot_ZN_1 Thermal Zone | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 1695 | 7.5 | 0.15 | 0 | 1695 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0 | [6 empty] | Perimeter_bot_ZN_1 | GroundFloor | DirectlyConditioned | Lobby, Main Entry | Perimeter_bot_ZN_1 Thermal Zone | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 1695 | 7.5 | 0.15 | 0 | 1695 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0
[35 empty] | Perimeter_bot_ZN_2 | GroundFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_bot_ZN_2 Thermal Zone | 2174.1 | 1 | 10 | 10 | 21.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 326 | 7.5 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_bot_ZN_2 | GroundFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_bot_ZN_2 Thermal Zone | 2174.1 | 1 | 10 | 10 | 21.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 326 | 7.5 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0
[35 empty] | Perimeter_bot_ZN_3 | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Perimeter_bot_ZN_3 Thermal Zone | 3373.6 | 1 | 33 | 33 | 111.3 | Maximum | CO2Sensors | 7.5 | 0.2 | 0 | 0 | 835 | 7.5 | 0.2 | 0 | 835 | 7.5 | 0.2 | 0 | UNDEFINED | 0 | 675 | 0 | [6 empty] | Perimeter_bot_ZN_3 | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Perimeter_bot_ZN_3 Thermal Zone | 3373.6 | 1 | 33 | 33 | 111.3 | Maximum | CO2Sensors | 7.5 | 0.2 | 0 | 0 | 835 | 7.5 | 0.2 | 0 | 835 | 7.5 | 0.2 | 0 | UNDEFINED | 0 | 675 | 0
[35 empty] | Perimeter_bot_ZN_4 | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Perimeter_bot_ZN_4 Thermal Zone | 2174 | 1 | 33 | 33 | 71.7 | Maximum | CO2Sensors | 7.5 | 0.2 | 0 | 0 | 538 | 7.5 | 0.2 | 0 | 538 | 7.5 | 0.2 | 0 | UNDEFINED | 0 | 435 | 0 | [6 empty] | Perimeter_bot_ZN_4 | GroundFloor | DirectlyConditioned | Retail Merchandise Sales, Wholesale Showroom | Perimeter_bot_ZN_4 Thermal Zone | 2174 | 1 | 33 | 33 | 71.7 | Maximum | CO2Sensors | 7.5 | 0.2 | 0 | 0 | 538 | 7.5 | 0.2 | 0 | 538 | 7.5 | 0.2 | 0 | UNDEFINED | 0 | 435 | 0
[35 empty] | Core_mid | MidFloor | DirectlyConditioned | Medical and Clinical Care | Core_mid Thermal Zone | 27257.6 | 5 | 10 | 10 | 272.6 | Maximum | Fixed | 7.5 | 0.2 | 0 | 0 | 5452 | 7.5 | 0.15 | 0 | 4089 | 0 | 0.2 | 0 | UNDEFINED | 0 | 5452 | 0 | [6 empty] | Core_mid | MidFloor | DirectlyConditioned | Medical and Clinical Care | Core_mid Thermal Zone | 27257.6 | 5 | 10 | 10 | 272.6 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 4147 | 7.5 | 0.15 | 0 | 4089 | 0 | 0.15216 | 0 | UNDEFINED | 0 | 4147 | 0
[35 empty] | MidFloor_Plenum | MidFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | MidFloor_Plenum Thermal Zone | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | MidFloor_Plenum | MidFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | MidFloor_Plenum Thermal Zone | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[35 empty] | Perimeter_mid_ZN_1 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_1 Thermal Zone | 3373.6 | 5 | 10 | 10 | 33.7 | Maximum | Fixed | 7.5 | 0.2 | 0 | 0 | 675 | 7.5 | 0.15 | 0 | 506 | 0 | 0.2 | 0 | UNDEFINED | 0 | 675 | 0 | [6 empty] | Perimeter_mid_ZN_1 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_1 Thermal Zone | 3373.6 | 5 | 10 | 10 | 33.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 513 | 7.5 | 0.15 | 0 | 506 | 0 | 0.15216 | 0 | UNDEFINED | 0 | 513 | 0
[35 empty] | Perimeter_mid_ZN_2 | MidFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_mid_ZN_2 Thermal Zone | 2174.1 | 5 | 10 | 10 | 21.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 326 | 7.5 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_mid_ZN_2 | MidFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_mid_ZN_2 Thermal Zone | 2174.1 | 5 | 10 | 10 | 21.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 248 | 7.5 | 0.15 | 0 | 326 | 0 | 0.11412 | 0 | UNDEFINED | 0 | 248 | 0
[35 empty] | Perimeter_mid_ZN_3 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_3 Thermal Zone | 3373.6 | 5 | 10 | 10 | 33.7 | Maximum | Fixed | 7.5 | 0.2 | 0 | 0 | 675 | 7.5 | 0.15 | 0 | 506 | 0 | 0.2 | 0 | UNDEFINED | 0 | 675 | 0 | [6 empty] | Perimeter_mid_ZN_3 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_3 Thermal Zone | 3373.6 | 5 | 10 | 10 | 33.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 513 | 7.5 | 0.15 | 0 | 506 | 0 | 0.15216 | 0 | UNDEFINED | 0 | 513 | 0
[35 empty] | Perimeter_mid_ZN_4 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_4 Thermal Zone | 2174 | 5 | 10 | 10 | 21.7 | Maximum | Fixed | 7.5 | 0.2 | 0 | 0 | 435 | 7.5 | 0.15 | 0 | 326 | 0 | 0.2 | 0 | UNDEFINED | 0 | 435 | 0 | [6 empty] | Perimeter_mid_ZN_4 | MidFloor | DirectlyConditioned | Medical and Clinical Care | Perimeter_mid_ZN_4 Thermal Zone | 2174 | 5 | 10 | 10 | 21.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 331 | 7.5 | 0.15 | 0 | 326 | 0 | 0.15216 | 0 | UNDEFINED | 0 | 331 | 0
[35 empty] | Core_hi | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Core_hi Thermal Zone | 27257.6 | 5 | 15 | 10 | 408.9 | Sum | Fixed | 0 | 0 | 0 | 4415 | 4415 | 7.5 | 0.15 | 0 | 4089 | 0 | 0.16197 | 0 | UNDEFINED | 0 | 4415 | 0 | [6 empty] | Core_hi | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Core_hi Thermal Zone | 27257.6 | 5 | 15 | 10 | 408.9 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 4415 | 7.5 | 0.15 | 0 | 4089 | 0 | 0.16197 | 0 | UNDEFINED | 0 | 4415 | 0
[35 empty] | HiFloor_Plenum | HiFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | HiFloor_Plenum Thermal Zone | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | HiFloor_Plenum | HiFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | HiFloor_Plenum Thermal Zone | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[35 empty] | Perimeter_hi_ZN_1 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_1 Thermal Zone | 3373.6 | 5 | 15 | 10 | 50.6 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 506 | 7.5 | 0.15 | 0 | 506 | 0 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0 | [6 empty] | Perimeter_hi_ZN_1 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_1 Thermal Zone | 3373.6 | 5 | 15 | 10 | 50.6 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 506 | 7.5 | 0.15 | 0 | 506 | 0 | 0.14999 | 0 | UNDEFINED | 0 | 506 | 0
[35 empty] | Perimeter_hi_ZN_2 | HiFloor | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_hi_ZN_2 Thermal Zone | 2174.1 | 5 | 10 | 10 | 21.7 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.15 | 0 | 326 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | Perimeter_hi_ZN_2 | HiFloor | IndirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_hi_ZN_2 Thermal Zone | 2174.1 | 5 | 10 | 10 | 21.7 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 7.5 | 0.15 | 0 | 326 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[35 empty] | Perimeter_hi_ZN_3 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_3 Thermal Zone | 3373.6 | 5 | 15 | 10 | 50.6 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 506 | 7.5 | 0.15 | 0 | 506 | 0 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0 | [6 empty] | Perimeter_hi_ZN_3 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_3 Thermal Zone | 3373.6 | 5 | 15 | 10 | 50.6 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 506 | 7.5 | 0.15 | 0 | 506 | 0 | 0.14999 | 0 | UNDEFINED | 0 | 506 | 0
[35 empty] | Perimeter_hi_ZN_4 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_4 Thermal Zone | 2174 | 5 | 15 | 10 | 32.6 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 326 | 7.5 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_hi_ZN_4 | HiFloor | DirectlyConditioned | Office (Greater than 250 square feet in floor area) | Perimeter_hi_ZN_4 Thermal Zone | 2174 | 5 | 15 | 10 | 32.6 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 326 | 7.5 | 0.15 | 0 | 326 | 0 | 0.14999 | 0 | UNDEFINED | 0 | 326 | 0
[35 empty] | Core_top | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Core_top Thermal Zone | 27257.6 | 1 | 67 | 67 | 1826.3 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 13697 | 7.5 | 0.15 | 0 | 13697 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 4089 | 0 | [6 empty] | Core_top | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Core_top Thermal Zone | 27257.6 | 1 | 67 | 67 | 1826.3 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 13697 | 7.5 | 0.15 | 0 | 13697 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 4089 | 0
[35 empty] | Perimeter_top_ZN_1 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_1 Thermal Zone | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 1695 | 7.5 | 0.15 | 0 | 1695 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0 | [6 empty] | Perimeter_top_ZN_1 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_1 Thermal Zone | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 1695 | 7.5 | 0.15 | 0 | 1695 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0
[35 empty] | Perimeter_top_ZN_2 | TopFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_top_ZN_2 Thermal Zone | 2174.1 | 1 | 10 | 10 | 21.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 326 | 7.5 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_top_ZN_2 | TopFloor | DirectlyConditioned | Corridors, Restrooms, Stairs, and Support Areas | Perimeter_top_ZN_2 Thermal Zone | 2174.1 | 1 | 10 | 10 | 21.7 | Maximum | Fixed | 7.5 | 0.15 | 0 | 0 | 326 | 7.5 | 0.15 | 0 | 326 | 0 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0
[35 empty] | Perimeter_top_ZN_3 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_3 Thermal Zone | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 1695 | 7.5 | 0.15 | 0 | 1695 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0 | [6 empty] | Perimeter_top_ZN_3 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_3 Thermal Zone | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 1695 | 7.5 | 0.15 | 0 | 1695 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 506 | 0
[35 empty] | Perimeter_top_ZN_4 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_4 Thermal Zone | 2174 | 1 | 67 | 67 | 145.7 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 1092 | 7.5 | 0.15 | 0 | 1092 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0 | [6 empty] | Perimeter_top_ZN_4 | TopFloor | DirectlyConditioned | Convention, Conference, Multipurpose and Meeting Center Areas | Perimeter_top_ZN_4 Thermal Zone | 2174 | 1 | 67 | 67 | 145.7 | Maximum | CO2Sensors | 7.5 | 0.15 | 0 | 0 | 1092 | 7.5 | 0.15 | 0 | 1092 | 7.5 | 0.15 | 0 | UNDEFINED | 0 | 326 | 0
[35 empty] | TopFloor_Plenum | TopFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | TopFloor_Plenum Thermal Zone | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0 | [6 empty] | TopFloor_Plenum | TopFloor | Plenum | Unoccupied-Exclude from Gross Floor Area | TopFloor_Plenum Thermal Zone | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNDEFINED | 0 | 0 | 0
[35 empty] | VentilationExhaust | [33 empty] | VentilationExhaust
[35 empty] | ThermalZone | [33 empty] | ThermalZone
[42 empty] | Occupancy |  |  | Ventilation |  | Design Value (Total) |  |  |  |  | Minimum Req. (Total) |  |  |  | Simulated |  | Exhaust | [17 empty] | Occupancy |  |  | Ventilation |  | Design Value (Total) |  |  |  |  | Minimum Req. (Total) |  |  |  | Simulated |  | Exhaust
[35 empty] | Name | Story Name | Type | Pri. HVAC System | Ventilation System | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume |  | Calculated Flow | Per Occupant | Per Area | Per Volume | Calculated Flow |  |  | Calculated Flow | ExhSysRef | ExhOperMode | ExhCtrlMthd | ExhBalancedSchRef | [6 empty] | Name | Story Name | Type | Pri. HVAC System | Ventilation System | Floor Area | Multiplier | Design | Minimum | Number | Spec. Method | Control | Per Occupant | Per Area | Per Volume |  | Calculated Flow | Per Occupant | Per Area | Per Volume | Calculated Flow |  |  | Calculated Flow | ExhSysRef | ExhOperMode | ExhCtrlMthd | ExhBalancedSchRef
[40 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  | (cfm/person) | (cfm/ft2) | (ACH) |  | (cfm) | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm) | [15 empty] | (ft2) |  | (ppl/1000ft2) | (ppl/1000ft2) | (people) |  |  | (cfm/person) | (cfm/ft2) | (ACH) |  | (cfm) | (cfm/person) | (cfm/ft2) | (ACH) | (cfm) | (cfm/person) | (cfm/ft2) | (cfm)
[35 empty] | Basement Thermal Zone | Basement | Conditioned | BaseAirSys6-Basement | BaseAirSys6-Basement | 38353 | 1 | 15 | 10 | 575.3 | Maximum | Fixed | 10 | 0.15 | 1.1247 |  | 5753 | 10 | 0.15 | 1.1247 | 5753 | 0 | 0.15 | [11 empty] | Basement Thermal Zone | Basement | Conditioned | BaseAirSys6 | BaseAirSys6 | 38353 | 1 | 15 | 10 | 575.3 | Maximum | Fixed | 10 | 0.15 | 1.1247 |  | 5753 | 10 | 0.15 | 1.1247 | 5753 | 0 | 0.15
[35 empty] | Core_bottom Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-Bot | BaseAirSys6-Bot | 27257.6 | 1 | 33 | 33 | 899.5 | Maximum | CO2Sensors | 7.5 | 0.2475 | 1.6495 |  | 6746 | 7.5 | 0.2475 | 1.6495 | 6746 | 7.5 | 0.2 | [11 empty] | Core_bottom Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-2 | BaseAirSys6-2 | 27257.6 | 1 | 33 | 33 | 899.5 | Maximum | CO2Sensors | 7.5 | 0.2475 | 1.6495 |  | 6746 | 7.5 | 0.2475 | 1.6495 | 6746 | 7.5 | 0.2
[35 empty] | GroundFloor_Plenum Thermal Zone | GroundFloor | Plenum | NONE | NONE | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | GroundFloor_Plenum Thermal Zone | GroundFloor | Plenum | NONE | NONE | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Perimeter_bot_ZN_1 Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-Bot | BaseAirSys6-Bot | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.349 |  | 1695 | 7.5 | 0.5025 | 3.349 | 1695 | 7.5 | 0.15 | [11 empty] | Perimeter_bot_ZN_1 Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-2 | BaseAirSys6-2 | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.349 |  | 1695 | 7.5 | 0.5025 | 3.349 | 1695 | 7.5 | 0.15
[35 empty] | Perimeter_bot_ZN_2 Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-Bot | BaseAirSys6-Bot | 2174.1 | 1 | 10 | 10 | 21.7 | Maximum | Fixed | 15 | 0.15 | 0.99971 |  | 326 | 15 | 0.15 | 0.99971 | 326 | 0 | 0.15 | [11 empty] | Perimeter_bot_ZN_2 Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-2 | BaseAirSys6-2 | 2174.1 | 1 | 10 | 10 | 21.7 | Maximum | Fixed | 15 | 0.15 | 0.99971 |  | 326 | 15 | 0.15 | 0.99971 | 326 | 0 | 0.15
[35 empty] | Perimeter_bot_ZN_3 Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-Bot | BaseAirSys6-Bot | 3373.6 | 1 | 33 | 33 | 111.3 | Maximum | CO2Sensors | 7.5 | 0.2475 | 1.6496 |  | 835 | 7.5 | 0.2475 | 1.6496 | 835 | 7.5 | 0.2 | [11 empty] | Perimeter_bot_ZN_3 Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-2 | BaseAirSys6-2 | 3373.6 | 1 | 33 | 33 | 111.3 | Maximum | CO2Sensors | 7.5 | 0.2475 | 1.6496 |  | 835 | 7.5 | 0.2475 | 1.6496 | 835 | 7.5 | 0.2
[35 empty] | Perimeter_bot_ZN_4 Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-Bot | BaseAirSys6-Bot | 2174 | 1 | 33 | 33 | 71.7 | Maximum | CO2Sensors | 7.5 | 0.2475 | 1.6495 |  | 538 | 7.5 | 0.2475 | 1.6495 | 538 | 7.5 | 0.2 | [11 empty] | Perimeter_bot_ZN_4 Thermal Zone | GroundFloor | Conditioned | BaseAirSys6-2 | BaseAirSys6-2 | 2174 | 1 | 33 | 33 | 71.7 | Maximum | CO2Sensors | 7.5 | 0.2475 | 1.6495 |  | 538 | 7.5 | 0.2475 | 1.6495 | 538 | 7.5 | 0.2
[35 empty] | Core_mid Thermal Zone | MidFloor | Conditioned | BaseAirSys6-Mid | BaseAirSys6-Mid | 27257.6 | 5 | 10 | 10 | 272.6 | Maximum | Fixed | 20 | 0.2 | 1.3329 |  | 5452 | 15 | 0.15 | 0.99971 | 4089 | 0 | 0.2 | [11 empty] | Core_mid Thermal Zone | MidFloor | Conditioned | BaseAirSys6-3 | BaseAirSys6-3 | 27257.6 | 5 | 10 | 10 | 272.6 | Maximum | Fixed | 15.2156 | 0.15216 | 1.0141 |  | 4147 | 15 | 0.15 | 0.99971 | 4089 | 0 | 0.15216
[35 empty] | MidFloor_Plenum Thermal Zone | MidFloor | Plenum | NONE | NONE | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | MidFloor_Plenum Thermal Zone | MidFloor | Plenum | NONE | NONE | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Perimeter_mid_ZN_1 Thermal Zone | MidFloor | Conditioned | BaseAirSys6-Mid | BaseAirSys6-Mid | 3373.6 | 5 | 10 | 10 | 33.7 | Maximum | Fixed | 20 | 0.2 | 1.3329 |  | 675 | 15 | 0.15 | 0.99971 | 506 | 0 | 0.2 | [11 empty] | Perimeter_mid_ZN_1 Thermal Zone | MidFloor | Conditioned | BaseAirSys6-3 | BaseAirSys6-3 | 3373.6 | 5 | 10 | 10 | 33.7 | Maximum | Fixed | 15.2156 | 0.15216 | 1.0141 |  | 513 | 15 | 0.15 | 0.99971 | 506 | 0 | 0.15216
[35 empty] | Perimeter_mid_ZN_2 Thermal Zone | MidFloor | Conditioned | BaseAirSys6-Mid | BaseAirSys6-Mid | 2174.1 | 5 | 10 | 10 | 21.7 | Maximum | Fixed | 15 | 0.15 | 0.99971 |  | 326 | 15 | 0.15 | 0.99971 | 326 | 0 | 0.15 | [11 empty] | Perimeter_mid_ZN_2 Thermal Zone | MidFloor | Conditioned | BaseAirSys6-3 | BaseAirSys6-3 | 2174.1 | 5 | 10 | 10 | 21.7 | Maximum | Fixed | 11.4117 | 0.11412 | 0.76056 |  | 248 | 15 | 0.15 | 0.99971 | 326 | 0 | 0.11412
[35 empty] | Perimeter_mid_ZN_3 Thermal Zone | MidFloor | Conditioned | BaseAirSys6-Mid | BaseAirSys6-Mid | 3373.6 | 5 | 10 | 10 | 33.7 | Maximum | Fixed | 20 | 0.2 | 1.333 |  | 675 | 15 | 0.15 | 0.99973 | 506 | 0 | 0.2 | [11 empty] | Perimeter_mid_ZN_3 Thermal Zone | MidFloor | Conditioned | BaseAirSys6-3 | BaseAirSys6-3 | 3373.6 | 5 | 10 | 10 | 33.7 | Maximum | Fixed | 15.2156 | 0.15216 | 1.0141 |  | 513 | 15 | 0.15 | 0.99973 | 506 | 0 | 0.15216
[35 empty] | Perimeter_mid_ZN_4 Thermal Zone | MidFloor | Conditioned | BaseAirSys6-Mid | BaseAirSys6-Mid | 2174 | 5 | 10 | 10 | 21.7 | Maximum | Fixed | 20 | 0.2 | 1.3329 |  | 435 | 15 | 0.15 | 0.9997 | 326 | 0 | 0.2 | [11 empty] | Perimeter_mid_ZN_4 Thermal Zone | MidFloor | Conditioned | BaseAirSys6-3 | BaseAirSys6-3 | 2174 | 5 | 10 | 10 | 21.7 | Maximum | Fixed | 15.2156 | 0.15216 | 1.0141 |  | 331 | 15 | 0.15 | 0.9997 | 326 | 0 | 0.15216
[35 empty] | Core_hi Thermal Zone | HiFloor | Conditioned | BaseAirSys6-Hi | BaseAirSys6-Hi | 27257.6 | 5 | 15 | 10 | 408.9 | Sum | Fixed | 10.7982 | 0.16197 | 1.0795 |  | 4415 | 10 | 0.15 | 0.99971 | 4089 | 0 | 0.16197 | [11 empty] | Core_hi Thermal Zone | HiFloor | Conditioned | BaseAirSys6-4 | BaseAirSys6-4 | 27257.6 | 5 | 15 | 10 | 408.9 | Maximum | Fixed | 10.7977 | 0.16197 | 1.0795 |  | 4415 | 10 | 0.15 | 0.99971 | 4089 | 0 | 0.16197
[35 empty] | HiFloor_Plenum Thermal Zone | HiFloor | Plenum | NONE | NONE | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | HiFloor_Plenum Thermal Zone | HiFloor | Plenum | NONE | NONE | 0 | 5 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[35 empty] | Perimeter_hi_ZN_1 Thermal Zone | HiFloor | Conditioned | BaseAirSys6-Hi | BaseAirSys6-Hi | 3373.6 | 5 | 15 | 10 | 50.6 | Maximum | Fixed | 10 | 0.15 | 0.99971 |  | 506 | 10 | 0.15 | 0.99971 | 506 | 0 | 0.15 | [11 empty] | Perimeter_hi_ZN_1 Thermal Zone | HiFloor | Conditioned | BaseAirSys6-4 | BaseAirSys6-4 | 3373.6 | 5 | 15 | 10 | 50.6 | Maximum | Fixed | 9.9996 | 0.14999 | 0.99967 |  | 506 | 10 | 0.15 | 0.99971 | 506 | 0 | 0.14999
[35 empty] | Perimeter_hi_ZN_2 Thermal Zone | HiFloor | Unconditioned | NONE | NONE | 2174.1 | 5 | 10 | 10 | 21.7 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 15 | 0.15 | 0.99971 | 326 | 0 | 0 | [11 empty] | Perimeter_hi_ZN_2 Thermal Zone | HiFloor | Unconditioned | NONE | NONE | 2174.1 | 5 | 10 | 10 | 21.7 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 15 | 0.15 | 0.99971 | 326 | 0 | 0
[35 empty] | Perimeter_hi_ZN_3 Thermal Zone | HiFloor | Conditioned | BaseAirSys6-Hi | BaseAirSys6-Hi | 3373.6 | 5 | 15 | 10 | 50.6 | Maximum | Fixed | 10 | 0.15 | 0.99973 |  | 506 | 10 | 0.15 | 0.99973 | 506 | 0 | 0.15 | [11 empty] | Perimeter_hi_ZN_3 Thermal Zone | HiFloor | Conditioned | BaseAirSys6-4 | BaseAirSys6-4 | 3373.6 | 5 | 15 | 10 | 50.6 | Maximum | Fixed | 9.9996 | 0.14999 | 0.99969 |  | 506 | 10 | 0.15 | 0.99973 | 506 | 0 | 0.14999
[35 empty] | Perimeter_hi_ZN_4 Thermal Zone | HiFloor | Conditioned | BaseAirSys6-Hi | BaseAirSys6-Hi | 2174 | 5 | 15 | 10 | 32.6 | Maximum | Fixed | 10 | 0.15 | 0.9997 |  | 326 | 10 | 0.15 | 0.9997 | 326 | 0 | 0.15 | [11 empty] | Perimeter_hi_ZN_4 Thermal Zone | HiFloor | Conditioned | BaseAirSys6-4 | BaseAirSys6-4 | 2174 | 5 | 15 | 10 | 32.6 | Maximum | Fixed | 9.9996 | 0.14999 | 0.99966 |  | 326 | 10 | 0.15 | 0.9997 | 326 | 0 | 0.14999
[35 empty] | Core_top Thermal Zone | TopFloor | Conditioned | BaseAirSys6-Top | BaseAirSys6-Top | 27257.6 | 1 | 67 | 67 | 1826.3 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.349 |  | 13697 | 7.5 | 0.5025 | 3.349 | 13697 | 7.5 | 0.15 | [11 empty] | Core_top Thermal Zone | TopFloor | Conditioned | BaseAirSys6-5 | BaseAirSys6-5 | 27257.6 | 1 | 67 | 67 | 1826.3 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.349 |  | 13697 | 7.5 | 0.5025 | 3.349 | 13697 | 7.5 | 0.15
[35 empty] | Perimeter_top_ZN_1 Thermal Zone | TopFloor | Conditioned | BaseAirSys6-Top | BaseAirSys6-Top | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.349 |  | 1695 | 7.5 | 0.5025 | 3.349 | 1695 | 7.5 | 0.15 | [11 empty] | Perimeter_top_ZN_1 Thermal Zone | TopFloor | Conditioned | BaseAirSys6-5 | BaseAirSys6-5 | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.349 |  | 1695 | 7.5 | 0.5025 | 3.349 | 1695 | 7.5 | 0.15
[35 empty] | Perimeter_top_ZN_2 Thermal Zone | TopFloor | Conditioned | BaseAirSys6-Top | BaseAirSys6-Top | 2174.1 | 1 | 10 | 10 | 21.7 | Maximum | Fixed | 15 | 0.15 | 0.99971 |  | 326 | 15 | 0.15 | 0.99971 | 326 | 0 | 0.15 | [11 empty] | Perimeter_top_ZN_2 Thermal Zone | TopFloor | Conditioned | BaseAirSys6-5 | BaseAirSys6-5 | 2174.1 | 1 | 10 | 10 | 21.7 | Maximum | Fixed | 15 | 0.15 | 0.99971 |  | 326 | 15 | 0.15 | 0.99971 | 326 | 0 | 0.15
[35 empty] | Perimeter_top_ZN_3 Thermal Zone | TopFloor | Conditioned | BaseAirSys6-Top | BaseAirSys6-Top | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.3491 |  | 1695 | 7.5 | 0.5025 | 3.3491 | 1695 | 7.5 | 0.15 | [11 empty] | Perimeter_top_ZN_3 Thermal Zone | TopFloor | Conditioned | BaseAirSys6-5 | BaseAirSys6-5 | 3373.6 | 1 | 67 | 67 | 226 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.3491 |  | 1695 | 7.5 | 0.5025 | 3.3491 | 1695 | 7.5 | 0.15
[35 empty] | Perimeter_top_ZN_4 Thermal Zone | TopFloor | Conditioned | BaseAirSys6-Top | BaseAirSys6-Top | 2174 | 1 | 67 | 67 | 145.7 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.349 |  | 1092 | 7.5 | 0.5025 | 3.349 | 1092 | 7.5 | 0.15 | [11 empty] | Perimeter_top_ZN_4 Thermal Zone | TopFloor | Conditioned | BaseAirSys6-5 | BaseAirSys6-5 | 2174 | 1 | 67 | 67 | 145.7 | Maximum | CO2Sensors | 7.5 | 0.5025 | 3.349 |  | 1092 | 7.5 | 0.5025 | 3.349 | 1092 | 7.5 | 0.15
[35 empty] | TopFloor_Plenum Thermal Zone | TopFloor | Plenum | NONE | NONE | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | TopFloor_Plenum Thermal Zone | TopFloor | Plenum | NONE | NONE | 0 | 1 | 0 | 0 | 0 | NoVentilation | UNDEFINED | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on G15: Sandeep: 150403: Updates to test by David to correct issues related to ventilation simulation
Note on G18: Sandeep: 150216: Lobby People Density increased from 10 to 67.
Note on G28: Sandeep: 150403: Updates to test by David to correct issues related to ventilation simulation
Note on G30: Sandeep: 150403: Updates to test by David to correct issues related to ventilation simulation
Note on AI31: Sandeep: 150403: Zone previously 'Conditioned' has been changed to 'IndirectlyConditioned'
Note on AK31: Sandeep: 150403: Zone previously 'Conditioned' has been changed to 'IndirectlyConditioned'
Note on G32: Sandeep: 150403: Updates to test by David to correct issues related to ventilation simulation
Note on G33: Sandeep: 150403: Updates to test by David to correct issues related to ventilation simulation
Note on G58: Sandeep: 150403: ACM prescribes the minimum occ dens, User defined occ dens if higher than the min, is carried over to the proposed and standard models.
Note on G61: Sandeep: 150216: Lobby People Density increased from 10 to 67.
Note on G71: Sandeep: 150403: ACM prescribes the minimum occ dens, User defined occ dens if higher than the min, is carried over to the proposed and standard models.
Note on G73: Sandeep: 150403: ACM prescribes the minimum occ dens, User defined occ dens if higher than the min, is carried over to the proposed and standard models.
Note on AI74: Sandeep: 150403: Zone previously 'Conditioned' has been changed to 'IndirectlyConditioned'
Note on AK74: Sandeep: 150403: Zone previously 'Conditioned' has been changed to 'IndirectlyConditioned'
Note on G75: Sandeep: 150403: ACM prescribes the minimum occ dens, User defined occ dens if higher than the min, is carried over to the proposed and standard models.
Note on G76: Sandeep: 150403: ACM prescribes the minimum occ dens, User defined occ dens if higher than the min, is carried over to the proposed and standard models.

## 030006S-OffMed-Run12 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006S-OffMed-Run12 |  | Model Revision no. |  | 3169 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006S-OffMed-Run12.cibd |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested |  | 2015-04-06 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed - ap
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Simulated Lighting Power Density (LPD) (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | Spc:IntLtgSpecMthd
Core_bottom | Waiting Area | X | 0.75 | X | 0.2 | X | 0.95 | X | OfficeLights | X | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_bot_ZN_2 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_bot_ZN_3 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_bot_ZN_4 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area | X | 0.75 | X | 0.2 | X | 0.95 | X | OfficeLights | X | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_mid_ZN_2 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_mid_ZN_3 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_mid_ZN_4 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area | X | 0.75 | X | 0.2 | X | 0.95 | X | OfficeLights | X | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_top_ZN_2 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_top_ZN_3 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
Perimeter_top_ZN_4 | Lobby, Main Entry | X | 0.5 | - | - | X | 0.5 | X | OfficeLights | - | -
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Baseline - ab
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Simulated Lighting Power Density (LPD) (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name |  | Spc:IntLtgSpecMthd
Core_bottom | Waiting Area | X | 0.8 | X | 0.2 | X | 1 | X | OfficeLights | X | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_bot_ZN_2 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_bot_ZN_3 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_bot_ZN_4 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area | X | 0.8 | X | 0.2 | X | 1 | X | OfficeLights | X | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_mid_ZN_2 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_mid_ZN_3 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_mid_ZN_4 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area | X | 0.8 | X | 0.2 | X | 1 | X | OfficeLights | X | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_top_ZN_2 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_top_ZN_3 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
Perimeter_top_ZN_4 | Lobby, Main Entry | X | 0.8 | - | - | X | 0.8 | X | OfficeLights | - | -
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | -

## 030006-OffMed-Run13 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run13 |  | Model Revision no. |  | 3169 |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run13.cibd |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested |  | 2015-04-06 |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name
Core_bottom | Waiting Area | X | 0.6 | - | - | X | 1.2 | X | 0.1 | X | 1.9 | X | OfficeLights | X | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_bot_ZN_2 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.91 | X | OfficeLights | - | -
Perimeter_bot_ZN_3 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_bot_ZN_4 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.91 | X | OfficeLights | - | -
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area | X | 0.6 | - | - | X | 1.2 | X | 0.1 | X | 1.9 | X | OfficeLights | X | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_mid_ZN_2 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.91 | X | OfficeLights | - | -
Perimeter_mid_ZN_3 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_mid_ZN_4 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.91 | X | OfficeLights | - | -
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area | X | 0.6 | - | - | X | 1.2 | X | 0.1 | X | 1.9 | X | OfficeLights | X | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_top_ZN_2 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.91 | X | OfficeLights | - | -
Perimeter_top_ZN_3 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_top_ZN_4 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.91 | X | OfficeLights | - | -
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function |  | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) |  | Lighting Power Density (TailoredOrnamentalAndSpecialEffectAllowance) (W/ft2) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method
Spc |  |  | Calculated |  | Calculated |  | Calculated |  | Calculated |  | IntLPDReg |  | IntLtgRegSchRef:Name
Core_bottom | Waiting Area | X | 0.8 | - | - | X | 0.5 | X | 0.1 | X | 1.4 | X | OfficeLights | X | Tailored Method
Perimeter_bot_ZN_1 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_bot_ZN_2 | Lobby, Main Entry | X | 0.8 | X | 0.09 | - | - | - | - | X | 0.89 | X | OfficeLights | - | -
Perimeter_bot_ZN_3 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_bot_ZN_4 | Lobby, Main Entry | X | 0.8 | X | 0.09 | - | - | - | - | X | 0.89 | X | OfficeLights | - | -
FirstFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_mid | Waiting Area | X | 0.8 | - | - | X | 0.5 | X | 0.1 | X | 1.4 | X | OfficeLights | X | Tailored Method
Perimeter_mid_ZN_1 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_mid_ZN_2 | Lobby, Main Entry | X | 0.8 | X | 0.09 | - | - | - | - | X | 0.89 | X | OfficeLights | - | -
Perimeter_mid_ZN_3 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_mid_ZN_4 | Lobby, Main Entry | X | 0.8 | X | 0.09 | - | - | - | - | X | 0.89 | X | OfficeLights | - | -
MidFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Core_top | Waiting Area | X | 0.8 | - | - | X | 0.5 | X | 0.1 | X | 1.4 | X | OfficeLights | X | Tailored Method
Perimeter_top_ZN_1 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_top_ZN_2 | Lobby, Main Entry | X | 0.8 | X | 0.09 | - | - | - | - | X | 0.89 | X | OfficeLights | - | -
Perimeter_top_ZN_3 | Lobby, Main Entry | X | 0.8 | X | 0.1 | - | - | - | - | X | 0.9 | X | OfficeLights | - | -
Perimeter_top_ZN_4 | Lobby, Main Entry | X | 0.8 | X | 0.09 | - | - | - | - | X | 0.89 | X | OfficeLights | - | -
TopFloor_Plenum |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## 020006S-OffSml-Run14 (hidden)
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020006S-OffSml-Run14 |  | Model Revision no. |  | 3169 |  |  | X | Use cell to check if values are verified
Model File Name | 020006S-OffSml-Run14.cibd |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | 2015-04-06 |  |  | 1 | Intermediate values, not directly evaluated
Test Category | Lighting |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Value in cell based on a calculation performed within the cell
[8 empty] | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Internal Load Components
Space
Space Name | Space Function |  | Installed Lighitng Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor |  | Lighting Power Density (Simulated) (W/ft2) |  | Lighting Schedule
Spc | SpcFunc |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF |  | Spc:IntLPDReg |  | IntLtgRegSchRef
Perimeter_ZN_1 | Office (Greater than 250 square feet in floor area) | X | 1152 | X | 1094.4 | X | DemandResponsiveControl | X | 0.05 | X | 0.9 | X | OfficeLights
Perimeter_ZN_2 | Office (Greater than 250 square feet in floor area) | X | 640 | X | 608 | X | DemandResponsiveControl | X | 0.05 | X | 0.84 | X | OfficeLights
Perimeter_ZN_3 | Office (Greater than 250 square feet in floor area) | X | 1152 | X | 1094.4 | X | DemandResponsiveControl | X | 0.05 | X | 0.9 | X | OfficeLights
Perimeter_ZN_4 | Office (Greater than 250 square feet in floor area) | X | 640 | X | 608 | X | DemandResponsiveControl | X | 0.05 | X | 0.84 | X | OfficeLights
Core_Zn | Office (Greater than 250 square feet in floor area) | X | 1408 | X | 1337.6 | X | DemandResponsiveControl | X | 0.05 | X | 0.83 | X | OfficeLights
Baseline
Internal Load Components
Space
Space Name | Space Function |  | Installed Lighitng Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor |  | Lighting Power Density (Simulated) (W/ft2) |  | Lighting Schedule
Spc | SpcFunc |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF |  | Spc:IntLPDReg |  | IntLtgRegSchRef
Perimeter_ZN_1 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | X | 0.75 | X | OfficeLights
Perimeter_ZN_2 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | X | 0.75 | X | OfficeLights
Perimeter_ZN_3 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | X | 0.75 | X | OfficeLights
Perimeter_ZN_4 | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | X | 0.75 | X | OfficeLights
Core_Zn | Office (Greater than 250 square feet in floor area) | - | - | - | - | - | - | - | - | X | 0.75 | X | OfficeLights
Note on K14: Sandeep: The Proposed Transform does not utilize the PAF, the evaluation for the same has already been made and only the final LPD is relevant

## 080006S-Whse-Run15 (hidden)
Note: Reference positions of the daylight control sensors are not being checked.
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 080006S-Whse-Run15 |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006S-Whse-Run15.cibd |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting Control |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Daylighting
Space
Space Name | Space Function |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | Continuous | - | - | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 10730.4 |  | 5000 |  | 250 |  | 250
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 34302 |  | 15000 |  | 250 |  | 250
Space Name | Space Function |  | Primary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint
Spc |  |  | Spc:PriSideDaylitArea |  | Spc:PriSideDayltgCtrlLtgPwr |  | Spc:PriSideDayltgIllumSetPt |  | Spc:PriSideDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 538.667 |  | 150 |  | 400 |  | 400
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Space Name | Space Function |  | Secondary Sidelit Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:SecSideDaylitArea |  | Spc:SecSideDayltgCtrlLtgPwr |  | Spc:SecSideDayltgIllumSetPt |  | Spc:SecSideDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 421.33 | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Baseline
Daylighting
Space
Space Name | Space Function |  | Daylight Control Type |  | Skylit Zone - Daylit Area (ft2) |  | Controlled General Lighting Power (W) |  | Illuminance Setpoint (lux) |  | Adjusted Illuminance Setpoint (lux)
Spc |  |  | Spc:DayltgCtrlType |  | Spc:SkylitDaylitArea |  | Spc:SkylitDayltgCtrlLtgPwr |  | Spc:SkylitDayltgIllumSetPt |  | Spc:SkylitDayltgAdjIllumSetPt
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | Continuous | - | - | - | - | - | - | - | -
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 10730.4 |  | 6438.25 |  | 250 |  | 250
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  | Continuous |  | 34387.5 |  | 20632.5 |  | 250 |  | 250
Space Name | Space Function |  | Primary Sidelit Daylit Area |  | Controlled General Lighting Power |  | Illuminance Setpoint |  | Adjusted Illuminance Setpoint
|  |  | (ft2) |  | (W) |  | (lux) |  | (lux)
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 538.667 |  | 404 |  | 400 |  | 400
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Space Name | Space Function |  | Secondary Sidelit Daylit Area |  | Controlled General Lighting Power |  | Illuminance Setpoint |  | Adjusted Illuminance Setpoint
|  |  | (ft2) |  | (W) |  | (lux) |  | (lux)
Zone1 Office | Office (Greater than 250 square feet in floor area) |  | 421.33 |  | 316 |  | 287.5 |  | 1150
Zone2 Fine Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -
Zone3 Bulk Storage | Commercial and Industrial Storage Areas (conditioned or unconditioned) | - | - | - | - | - | - | - | -

## 050006S-RetlMed-Run16 (hidden)
General Details |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 050006S-RetlMed-Run16 |  | Model Revision no. |  |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 050006S-RetlMed-Run16.cibd |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Retail |  | Date Tested |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Lighting Control |  | Testing Performed by |  | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Internal Load Components
Space
Space Name | Space Function | Space Floor Area (ft2) | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) | Lighting Power Density Simulated (W/ft2) |  | Allowance Area (ft2)
Spc |  |  | Calculated |  | Calculated | IntLPDReg |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | 0.6 | - | - | 0.6 | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | 1.2 | - | - | 1.2 | - | -
Front_Entry | Lobby, Main Entry | 129.167 | 1.5 | - | - | 1.5 | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 | 1.6 |  | 0.75 | 2.35 |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 | 1.2 | - | - | 1.2 | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function | Space Floor Area (ft2) | Lighting Power Density (General Lighting) (W/ft2) |  | Lighting Power Density (TailoredTaskAllowance) (W/ft2) | Lighting Power Density Simulated (W/ft2) |  | Allowance Area (ft2)
Spc |  |  | Calculated |  | Calculated | IntLPDReg |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) | 4089.12 | 0.6 | - | - | 0.6 | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom | 17227.4 | 1.2 | - | - | 1.2 | - | -
Front_Entry | Lobby, Main Entry | 129.167 | 1.5 | - | - | 1.5 | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom | 1623.3 | 1.5 |  | 0.65 | 2.15 |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom | 1623.3 | 1.2 | - | - | 1.2 | - | -

## 020006S-OffSml-Run18
General Details |  |  | Model/Software Details | [5 empty] | Key
Test Name | 020006S-OffSml-Run18 |  | Model Revision no. |  | 3169 |  |  | X | Cell used to check if values are verified
Model File Name | 020006S-OffSml-Run18.cibd |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Climate Zone | CZ-06 |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Small Office |  | Date Tested |  | 2015-04-06 |  |  | 1 | Intermediate values, not directly evaluated
Test Category | HVAC |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Value in cell based on a calculation performed within the cell
[8 empty] | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Core_ZN Thermal Zone | CoreZnPSZ AirSys | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
Perimeter_ZN_1 Thermal Zone | Perim1ZnPSZ AirSys | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnPSZ AirSys | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
AirSystem - Name | Cooling Coil - Name |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
CoreZnPSZ AirSys | CoreZnCoolingCoil | X | DirectExpansion | X | 13 | - | - | X | CoilClgDXSEER16EER13EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
Perim1ZnPSZ AirSys | Perim1ZnCoolingCoil | X | DirectExpansion | X | 13 | - | - | X | CoilClgDXSEER16EER13EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnPSZ AirSys | Perim2ZnCoolingCoil | X | DirectExpansion | X | 13 | - | - | X | CoilClgDXSEER16EER13EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil | X | DirectExpansion | X | 13 | - | - | X | CoilClgDXSEER16EER13EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil | X | DirectExpansion | X | 13 | - | - | X | CoilClgDXSEER16EER13EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name |  | Type |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
CoreZnPSZ AirSys | CoreZnHeatingCoil | X | Furnace (Natural Gas) | X | 0.80003 | - | - | X | CoilHtgFurnFIRRatio_fQRatio
Perim1ZnPSZ AirSys | Perim1ZnHeatingCoil | X | Furnace (Natural Gas) | X | 0.80003 | - | - | X | CoilHtgFurnFIRRatio_fQRatio
Perim2ZnPSZ AirSys | Perim2ZnHeatingCoil | X | Furnace (Natural Gas) | X | 0.80003 | - | - | X | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil | X | Furnace (Natural Gas) | X | 0.80003 | - | - | X | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil | X | Furnace (Natural Gas) | X | 0.80003 | - | - | X | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name |  | Control Method |  | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
CoreZnPSZ AirSys | CoreZnSupplyFan | X | Constant Volume | X | BrakeHorsePower | X | 1.6 | - | - | - | - | X | 2 | X | 0.865
Perim1ZnPSZ AirSys | Perim1ZnSupplyFan | X | Constant Volume | X | BrakeHorsePower | X | 1.12 | - | - | - | - | X | 1.5 | X | 0.855
Perim2ZnPSZ AirSys | Perim2ZnSupplyFan | X | Constant Volume | X | BrakeHorsePower | X | 0.8 | - | - | - | - | X | 1 | X | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan | X | Constant Volume | X | BrakeHorsePower | X | 1.2 | - | - | - | - | X | 1.5 | X | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan | X | Constant Volume | X | BrakeHorsePower | X | 0.8 | - | - | - | - | X | 1 | X | 0.855
Thermal Zone - Name | Conditioning Type |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint |  | Economizer Integration
ThrmlZn | ThrmlZn:Type |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef |  | OACtrl:EconoIntegration
Core_ZN Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Perimeter_ZN_1 Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Perimeter_ZN_2 Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Perimeter_ZN_3 Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Perimeter_ZN_4 Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Baseline
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Core_ZN Thermal Zone | BaseAirSys3 | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
Perimeter_ZN_1 Thermal Zone | BaseAirSys3-2 | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
Perimeter_ZN_2 Thermal Zone | BaseAirSys3-3 | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
Perimeter_ZN_3 Thermal Zone | BaseAirSys3-4 | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
Perimeter_ZN_4 Thermal Zone | BaseAirSys3-5 | X | SZAC | X | OfficeHVACAvail | X | 55 | X | 95 | X | NoSATControl
AirSystem - Name | Cooling Coil - Name |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg | X | DirectExpansion | X | 10.8446 | X | 1.15 | X | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-2 | BaseSys3 CoilClg-2 | X | DirectExpansion | X | 10.8446 | X | 1.15 | X | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-3 | BaseSys3 CoilClg-3 | X | DirectExpansion | X | 10.8446 | X | 1.15 | X | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-4 | BaseSys3 CoilClg-4 | X | DirectExpansion | X | 10.8446 | X | 1.15 | X | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3-5 | BaseSys3 CoilClg-5 | X | DirectExpansion | X | 10.8446 | X | 1.15 | X | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | X | CoilClgDXSEEREIRRatio_fQFrac | X | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name |  | Type |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg | X | Furnace (Natural Gas) | X | 0.80003 | X | 1.25 | X | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-2 | BaseSys3 CoilHtg-2 | X | Furnace (Natural Gas) | X | 0.80003 | X | 1.25 | X | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-3 | BaseSys3 CoilHtg-3 | X | Furnace (Natural Gas) | X | 0.80003 | X | 1.25 | X | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-4 | BaseSys3 CoilHtg-4 | X | Furnace (Natural Gas) | X | 0.80003 | X | 1.25 | X | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3-5 | BaseSys3 CoilHtg-5 | X | Furnace (Natural Gas) | X | 0.80003 | X | 1.25 | X | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan | X | Constant Volume | X | StaticPressure | X | 1227.95 | X | 0.96757 | X | 0.5 | X | 2.5 | X | 1 | X | 0.855
BaseAirSys3-2 | BaseSys3 Fan-2 | X | Constant Volume | X | StaticPressure | X | 1342.95 | X | 1.0582 | X | 0.5 | X | 2.5 | X | 1.5 | X | 0.865
BaseAirSys3-3 | BaseSys3 Fan-3 | X | Constant Volume | X | StaticPressure | X | 699.098 | X | 0.55086 | X | 0.5 | X | 2.5 | X | 0.75 | X | 0.855
BaseAirSys3-4 | BaseSys3 Fan-4 | X | Constant Volume | X | StaticPressure | X | 960.397 | X | 0.75675 | X | 0.5 | X | 2.5 | X | 1 | X | 0.855
BaseAirSys3-5 | BaseSys3 Fan-5 | X | Constant Volume | X | StaticPressure | X | 765.763 | X | 0.60339 | X | 0.5 | X | 2.5 | X | 0.75 | X | 0.855
Thermal Zone - Name | Conditioning Type |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint |  | Economizer Integration
ThrmlZn | ThrmlZn:Type |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef |  | OACtrl:EconoIntegration
Core_ZN Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Perimeter_ZN_1 Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Perimeter_ZN_2 Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Perimeter_ZN_3 Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -
Perimeter_ZN_4 Thermal Zone | Conditioned | X | OfficeClgSetPt | X | OfficeHtgSetPt | - | -

## 030006S-OffMed-Run19 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006S-OffMed-Run19 |  |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006S-OffMed-Run19.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Complete |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Internal Load Components
Space Name | Space Function | Space Floor Area (ft2) |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name
Spc |  |  |  | RecptPwrDens |  | RecptSchRef:Name
Core_bottom | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_mid | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_top | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor | BottomVAV | New |  | Bottom Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | Mid VAV | New |  | Mid Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | Top VAV | New |  | Top Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Core_bottom Thermal Zone | Core_bottomZnPSZ AirSys | New |  | Bottom Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Core_mid Thermal Zone | Core_midZnPSZ AirSys | New |  | Mid Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Core_top Thermal Zone | Core_topZnPSZ AirSys | New |  | Top Floor - Core Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | New |  | DirectExpansion |  | 12.96 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | New |  | DirectExpansion |  | 12.96 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | New |  | DirectExpansion |  | 12.96 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_bottomZnPSZ AirSys | Core_bottomZnCoolingCoil | New |  | DirectExpansion |  | 13.65 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_midZnPSZ AirSys | Core_midZnCoolingCoil | New |  | DirectExpansion |  | 13.65 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Core_topZnPSZ AirSys | Core_topZnCoolingCoil | New |  | DirectExpansion |  | 13.65 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating | New |  | HotWater
Mid VAV | Mid VAV CoilHeating | New |  | HotWater
Top VAV | Top VAV CoilHeating | New |  | HotWater
BottomVAV | (All ReheatCoils) | New |  | HotWater
Mid VAV | (All ReheatCoils) | New |  | HotWater
Top VAV | (All ReheatCoils) | New |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | (Pwr_fPLRCrvRef)
Bottom Floor | BottomVAV SupplyFan | New |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 6.21 | - | - | - | - |  | 7.5 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Mid Floor | MidVAV SupplyFan | New |  | VariableSpeedDrive |  | Static Pressure |  | 10850 |  | 7.8917 |  | 0.65 |  | 3 |  | 10 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Top Floor | TopVAV SupplyFan | New |  | VariableSpeedDrive |  | Static Pressure |  | 10200 |  | 9.3767 |  | 0.6 |  | 3.5 |  | 10 |  | 0.9 |  | FanVSDGoodSpResetPwrRatio_fCFMRatio
Core_bottom Thermal Zone | Core_bottomZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
Core_mid Thermal Zone | Core_midZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
Core_top Thermal Zone | Core_topZnSupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 9.5 | - | - | - | - |  | 10 |  | 0.917 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV |  | New |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV |  | New |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV |  | New |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Core_bottomZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Core_midZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Core_topZnPSZ AirSys |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Perimeter Zones) | Conditioned | New |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Core Zones) | Conditioned | New |  | DataClgSetpt |  | DataHtgSetpt
(All Plenum) | Plenum | New | - | - | - | -
Baseline
Internal Load Components
Space Name | Space Function | Space Floor Area (ft2) |  | Equipment Power Density (W/ft2) |  | EPD - Schedule Name
Spc |  |  |  | RecptPwrDens |  | RecptSchRef:Name
Core_bottom | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_bot_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_bot_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
FirstFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_mid | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_mid_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_mid_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
MidFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
Core_top | Computer Room | 10586.7 |  | 20 |  | DataReceptacle
Perimeter_top_ZN_1 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_2 | Office (Greater than 250 square feet in floor area) | 1412.9 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_3 | Office (Greater than 250 square feet in floor area) | 2231.76 |  | 1.5 |  | OfficeReceptacle
Perimeter_top_ZN_4 | Office (Greater than 250 square feet in floor area) | 1412.8 |  | 1.5 |  | OfficeReceptacle
TopFloor_Plenum | Unoccupied-Exclude from Gross Floor Area | 0 | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Perimeter Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Core_bottom Thermal Zone | BaseAirSys11 | New |  | Bottom Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
Core_mid Thermal Zone | BaseAirSys11-2 | New |  | Mid Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
Core_top Thermal Zone | BaseAirSys11-3 | New |  | Top Floor - Core Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11 | BaseSys11 CoilClg | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11-2 | BaseSys11 CoilClg-2 | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys11-3 | BaseSys11 CoilClg-3 | New |  | DirectExpansion |  | 9.5 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx | (Pwr_fPLRCrvRef)
Bottom Floor (Peripheral Zones) | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 8702.09 |  | 7.9997 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Mid Floor (Peripheral Zones) | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 10576.1 |  | 10.7529 |  | 0.62 |  | 4 |  | 15 |  | 0.924 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Top Floor (Peripheral Zones) | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 10662.8 |  | 10.8411 |  | 0.62 |  | 4 |  | 15 |  | 0.924 | - | - | FanVSDGoodSpResetPwrRatio_fCFMRatio
Core_bottom Thermal Zone | BaseSys11 Fan | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 38362.1 |  | 23.5976 |  | 0.62 |  | 2.4201 |  | 25 |  | 0.936 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Core_mid Thermal Zone | BaseSys11 Fan-2 | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 38213.5 |  | 23.3555 |  | 0.62 |  | 2.4045 |  | 20 |  | 0.93 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Core_top Thermal Zone | BaseSys11 Fan-3 | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 38805.2 |  | 23.8702 |  | 0.62 |  | 2.4201 |  | 25 |  | 0.936 |  | 0.49 | FanVSDPerfSpResetPwrRatio_fCFMRatio
Bottom Floor (Peripheral Zones) | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 8337.63 |  | 2.4636 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
Mid Floor (Peripheral Zones) | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 10211.7 |  | 3.2185 |  | 0.5 |  | 1 |  | 5 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
Top Floor (Peripheral Zones) | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 10298.3 |  | 3.2458 |  | 0.5 |  | 1 |  | 5 |  | 0.895 | - | - | FanVSDPwrRatio_fCFMRatio
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys11-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Peripheral Zones) | Conditioned | New |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Core Zones) | Conditioned | New |  | DataClgSetpt |  | DataHtgSetpt
(All Plenum) | Plenum | New | - | - | - | -
Note on F15: Sandeep: 150321: Changed from 0.5 to 1.5
Note on F21: Sandeep: 150321: Changed from 0.5 to 1.5
Note on F27: Sandeep: 150321: Changed from 0.5 to 1.5
Note on N39: Sandeep: 150217: The system has no Heating. Previously reported value - 95
Note on L67: Sandeep: 150219: changed from 7.62 to 7.89
Note on L68: Sandeep: 150219: changed from 7.78 to 10.37
Note on N68: Sandeep: 150219: changed from 0.60 to 0.62 150327: hardset to 0.60 asper appendix 3c
Note on P68: Sandeep: 150219: changed from 3.5 to 4 150327: hardset to 3.5 asper appendix 3c
Note on I74: Sandeep: 150331: Check Parameter added
Note on L74: Sandeep: 150331: Check Parameter added
Note on H127: Sandeep: 150217: DXEER changed from 10.8 to 9.8, because the capacity changed from 233134 to 410306
Note on H151: Sandeep: 150321: Changed to static pressure?

## 040006S-OffLrg-Run20 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 040006S-OffLrg-Run20 |  |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 040006S-OffLrg-Run20.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office |  |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Complete |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Basement Floor | BsmntZnPSZ AirSys | New |  | Basement Floor/Zone |  | SZAC |  | DataHVACAvail |  | 60 | - | - |  | NoSATControl | - | - | - | -
Bottom Floor | BaseAirSys6-Bot | New |  | Bottom Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys6-Mid | New |  | Mid Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Hi Floor | BaseAirSys6-Hi | New |  | Hi Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys6-Top | New |  | Top Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BsmntZnPSZ AirSys | BsmntZnCoolingCoil | New |  | DirectExpansion |  | 11.4 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys6-Bot | BaseSys6 CoilClg-Bot | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Mid | BaseSys6 CoilClg-Mid | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Hi | BaseSys6 CoilClg-Hi | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | -
BaseAirSys6-Top | BaseSys6 CoilClg-Top | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating |  |  | HotWater
Mid VAV | Mid VAV CoilHeating |  |  | HotWater
Hi VAV | Hi VAV CoilHeating |  |  | HotWater
Top VAV | Top VAV CoilHeating |  |  | HotWater
BottomVAV | (All ReheatCoils) |  |  | HotWater
Mid VAV | (All ReheatCoils) |  |  | HotWater
Hid VAV | (All ReheatCoils) |  |  | HotWater
Top VAV | (All ReheatCoils) |  |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Basement Floor | BsmntZnSupplyFan | New |  | ConstantVolume |  | StaticPressure |  | 190000 |  | 169.0293 |  | 0.62 |  | 3.5 |  | 200 |  | 0.962
Bottom Floor | BaseSys6 Fan-Bot | New |  | VariableSpeedDrive |  | StaticPressure |  | 38624.3 |  | 44.1787 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Mid Floor | BaseSys6 Fan-Mid | New |  | VariableSpeedDrive |  | StaticPressure |  | 40232.3 |  | 46.018 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Hi Floor | BaseSys6 Fan-Hi | New |  | VariableSpeedDrive |  | StaticPressure |  | 40232.3 |  | 46.018 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
Top Floor | BaseSys6 Fan-Top | New |  | VariableSpeedDrive |  | StaticPressure |  | 42188.3 |  | 48.2553 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BsmntZnPSZ AirSys |  |  |  | NoEconomizer |  | UNDEFINED
BaseAirSys6-Bot |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Mid |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Hi |  |  |  | DifferentialDryBulb |  | Integrated
BaseAirSys6-Top |  |  |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Basement Floor | Conditioned |  |  | DataClgSetpt |  | DataHtgSetpt
Bottom, Mid, Hi and Top Floors | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 2887230 |  | 0.82 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Condensor Type |  | Chiller Capacity |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Centrifugal |  | Fluid |  | 5268800 |  | 5.86 (0.6 kW/ton, 20 EER) |  | 0.4 |  | 0.1
Base Chlr-2 | BaseChWSystem | New |  | Centrifugal |  | Fluid |  | 5268800 |  | 5.86 (0.6 kW/ton, 20 EER) |  | 0.4 |  | 0.1
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Base Chlr-2 | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment |  |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 2.74 (19 W/gpm) |  | 5 |  | 63.2 |  | 0.895 | - | -
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 2.74 (19 W/gpm) |  | 5 |  | 63.2 |  | 0.895 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 16.00 (13 W/gpm) |  | 20 |  | 45 |  | 0.93 | - | -
Base CW Pump-2 | Base Tower-2 | New |  | OnDemand |  | ConstantSpeed |  | 16.00 (13 W/gpm) |  | 20 |  | 45 |  | 0.93 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 8.15 (15.5 W/gpm) |  | 15 |  | 53.172 |  | 0.924 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
Base ChW Pump-2 | Base Chlr-2 | New |  | OnDemand |  | VariableSpeed |  | 8.15 (15.5 W/gpm) |  | 15 |  | 53.172 |  | 0.924 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 1229.88 |  | 20.5 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Base Tower-2 | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 1229.88 |  | 20.5 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Baseline
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor | BaseAirSys6 | New |  | Bottom Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys6-2 | New |  | Mid Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Hi Floor | BaseAirSys6-3 | New |  | Hi Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys6-4 | New |  | Top Floor - All Zones |  | VAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Basement Floor | BaseAirSys10 | New |  | Basement Floor/Zone |  | SZVAVAC |  | DataHVACAvail |  | 60 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys6 | BaseSys6 CoilClg | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-2 | BaseSys6 CoilClg-2 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-3 | BaseSys6 CoilClg-3 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys6-4 | BaseSys6 CoilClg-4 | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
BaseAirSys10 | BaseSys10 CoilClg | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys6 | BaseSys6 CoilHtg |  |  | HotWater
BaseAirSys6-2 | BaseSys6 CoilHtg-2 |  |  | HotWater
BaseAirSys6-3 | BaseSys6 CoilHtg-3 |  |  | HotWater
BaseAirSys6-4 | BaseSys6 CoilHtg-4 |  |  | HotWater
BaseAirSys6/6-2/6-3/6-4 | (All BaseVAVReheatCoils) |  |  | HotWater
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx
Bottom Floor | BaseSys6 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 48182.6 |  | 55.1116 |  | 0.62 |  | 4.5 |  | 60 |  | 0.95 | - | -
Mid Floor | BaseSys6 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 41702 |  | 47.699 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945 | - | -
Hi Floor | BaseSys6 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 41610.1 |  | 47.5939 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945 | - | -
Top Floor | BaseSys6 Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 39384.9 |  | 45.0487 |  | 0.62 |  | 4.5 |  | 50 |  | 0.945 | - | -
Basement Floor | BaseSys10 Fan | New |  | VariableSpeedDrive |  | PowerPerUnitFlow |  | 143597 |  | 90.0293 |  | 0.62 |  | 2.4666 |  | 100 |  | 0.954 |  | 0.49
Bottom Floor | BaseRelief Fan |  | - | - |  | StaticPressure |  | 46264.9 |  | 14.5819 |  | 0.5 |  | 1 |  | 15 |  | 0.924 |  | 0.25433
Mid Floor | BaseRelief Fan-2 |  | - | - |  | Static Pressure |  | 32113.7 |  | 10.1217 |  | 0.5 |  | 1 |  | 15 |  | 0.924 |  | 0.25433
Hi Floor | BaseRelief Fan-3 |  | - | - |  | Static Pressure |  | 32021.9 |  | 10.0927 |  | 0.5 |  | 1 |  | 15 |  | 0.924 |  | 0.25433
Top Floor | BaseRelief Fan-4 |  | - | - |  | Static Pressure |  | 37467.2 |  | 11.809 |  | 0.5 |  | 1 |  | 15 |  | 0.924 |  | 0.25433
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseSys6 OACtrl |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-2 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-3 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys6 OACtrl-4 |  | New |  | DifferentialDryBulb |  | Integrated
BaseSys10 OACtrl |  | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Basement Floor | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
Bottom, Mid, Hi and Top Floors | Conditioned |  |  | DataClgSetpt |  | DataHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 2007160 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Condensor Type |  | Chiller Capacity |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Centrifugal |  | Fluid |  | 8146370 |  | 5.96 (0.59 kW/ton) | - | - |  | 0.1
Base Chlr-2 | BaseChWSystem | New |  | Centrifugal |  | Fluid |  | 8146370 |  | 5.96 (0.59 kW/ton) | - | - |  | 0.1
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Base Chlr-2 | BaseChWSystem | New |  | ChlrWtrCentPathBGtEql600tonQRatio_fTchwsTcwsSI |  | ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatio |  | ChlrWtrCentPathBGtEql600tonEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment |  |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 1.91 (19 W/gpm) |  | 3 |  | 63.2 |  | 0.895 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 24.46 (12.9 W/gpm) |  | 40 |  | 45 |  | 0.941 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 14.21 (17.4 W/gpm) |  | 20 |  | 60.3659 |  | 0.93 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 1.91 (19 W/gpm) |  | 3 |  | 63.2 |  | 0.895 | - | -
Base ChW Pump-2 | Base Chlr-2 | New |  | OnDemand |  | VariableSpeed |  | 14.22 (17.4 W/gpm) |  | 20 |  | 60.3659 |  | 0.93 |  | PumpVSDRstEPPwrRatio_fGPMRatio
Base CW Pump-2 | Base Tower-2 | New |  | OnDemand |  | ConstantSpeed |  | 24.46 (12.9 W/gpm) |  | 40 |  | 45 |  | 0.941 | - | -
Cells above need to be reviewed
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 1901.89 |  | 31.69 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Base Tower-2 | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 1901.89 |  | 31.69 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Note on N14: Sandeep: 150321: The system has no Heating. Previously reported value - 95
Note on N73: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on L75: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412
Note on L76: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412
Note on J79: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on H137: Sandeep: 150330: Previously 'undefined'.
Note on F162: Sandeep: 150330: PRIOR VALUE - 1992320
Note on N165: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on J167: Sandeep: 150330: PRIOR VALUE- 8122500
Note on L167: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412

## 080006S-Whse-Run21 (hidden)
General Details |  | Model/Software Details |  |  |  |  | Key
Test Name | 080006S-Whse-Run21 | Model Revision no. |  |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 080006S-Whse-Run21.cibd | Version of Ruleset (Trunk rev. No.) | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 | CBECC Software | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Warehouse | Date Tested |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | HVAC | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name | Type | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys | AirSys:Type | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Zone1 Office Thermal Zone | OfficeZnPSZAirSys | SZAC | WarehouseHVACAvail |  | 55 |  | 95 |  | NoSATControl
Zone2 Fine Storage Thermal Zone | FineSto_ZnPSZAirSys | SZAC | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
Zone3 Bulk Storage Thermal Zone | BulkSto_ZnPSZAirSys | SZAC | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg | CoilClg:Type | CoilClg:DXEER |  |  |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
OfficeZnPSZAirSys | OfficeZnCoolingCoil | DirectExpansion | 11.2 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Type | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
OfficeZnPSZAirSys | OfficeZnHeatingCoil | Furnace (Natural Gas) | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
FineSto_ZnPSZAirSys | FineSto_ZnHeatingCoil | Furnace (Natural Gas) | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
BulkSto_ZnPSZAirSys | BulkSto_ZnHeatingCoil | Furnace (Natural Gas) | 0.81 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Control Method | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: | Fan:CtrlMthd | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
OfficeZnPSZAirSys | OfficeZnSupplyFan | Constant Volume | BreakHorsePower |  | 2 | - | - | - | - | 5 | 0.89
FineSto_ZnPSZAirSys | FineSto_ZnSupplyFan | Constant Volume | BreakHorsePower |  | 5.5 | - | - | - | - | 10 | 0.92
BulkSto_ZnPSZAirSys | BulkSto_ZnSupplyFan | Constant Volume | BreakHorsePower |  | 20 | - | - | - | - | 30 | 0.92
Baseline
HVAC Systems
Thermal Zone - Control Zone Name | AirSystem - Name | Type | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys | AirSys:Type | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Zone1 Office Thermal Zone | BaseAirSys3 | SZAC | WarehouseHVACAvail |  | 55 |  | 95 |  | NoSATControl
Zone2 Fine Storage Thermal Zone | BaseAirSys9 | HV | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
Zone3 Bulk Storage Thermal Zone | BaseAirSys9-2 | HV | WarehouseHVACAvail | - | - |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg | CoilClg:Type | CoilClg:DXEER |  |  |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg | DirectExpansion | 11 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Type | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys9 | BaseSys9 CoilHtg | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys9-2 | BaseSys9 CoilHtg-2 | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan | Constant Volume | StaticPressure |  | 3041.71 |  | 2.3967 |  | 0.6 | 3 | 3 | 0.895
BaseAirSys9 | BaseSys9 Fan | Constant Volume | StaticPressure |  | 6407.47 |  | 5.0488 |  | 0.6 | 3 | 7.5 | 0.917
BaseAirSys9-2 | BaseSys9 Fan-2 | Constant Volume | StaticPressure |  | 25484.6 |  | 22.6718 |  | 0.62 | 3.5 | 25 | 0.936
BaseAirSys3 | BaseRelief Fan | VariableSpeedDrive | StaticPressure |  | 2914.22 |  | 0.8611 |  | 0.4 | 0.75 | 1 | 0.855
Note on G64: Sandeep: 150330: PREVIOUSLY 'UNDEFINED'

## 070015S-HotSml-Run22 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 070015S-HotSml-Run22 |  |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 070015S-HotSml-Run22.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Large Office |  |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Complete |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Common Areas: Floor 1 | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 2 | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 3 | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 4 | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Zone: KitchenFlr1 | KitchenMUA | New |  | Zone: KitchenFlr1 |  | SZAC |  | RestaurantHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Residential Units: All Floors | Residential Units: FPFC (All) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
Zone: KitchenFlr1 | KitchenExhaust | New |  | Zone: KitchenFlr1 |  | Exhaust |  | RestaurantHVACAvail | - | - | - | - |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 | - | - |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 | - | - |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 11 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Residential Units: FPFC (All) | Residential Units: FPFC CoilClg (All) | New |  | ChilledWater | - | - | - | - | - | - | - | - | - | -
KitchenMUA | Kitchen CoilClg | New |  | DirectExpansion |  | 10.8446 | - | - |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-2 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-3 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
BaseAirSys5-4 | (All ReheatCoils) | New |  | HotWater | - | - | - | - | - | -
Residential Units: FPFC (All) | Residential Units: FPFC CoilHtg (All) | New |  | HotWater | - | - | - | - | - | -
KitchenMUA | KitchenCoilHtg | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 12396.3 |  | 12.6035 |  | 0.62 |  | 4 |  | 15 |  | 0.924
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1646.78 |  | 1.5571 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1674.51 |  | 1.5833 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | StaticPressure |  | 1721.44 |  | 1.6277 |  | 0.5 |  | 3 |  | 2 |  | 0.865
Residential Units: Floor1 | GuestRoom101_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom102_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom103_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom104_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor1 | GuestRoom105_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom201_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom202_205_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom206_208_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom209_212_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom213_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom214_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom215_218_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom219_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom220_223_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor2 | GuestRoom224_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom301_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom302_305_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom306_308_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom309_312_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom313_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom314_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom315_318_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom319_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom320_323_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor3 | GuestRoom324_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom401_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.027 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom402_405_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom406_408_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 378.03 |  | 0.15172 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom409_412_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom413_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.026 |  | 0.14089 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom414_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom415_418_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom419_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351.006 |  | 0.14088 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom420_423_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Residential Units: Floor4 | GuestRoom424_FPFC Fan | New |  | ConstantVolume |  | StaticPressure |  | 351 |  | 0.14087 |  | 0.5 |  | 1.2734 |  | 0.25 |  | 0.855
Zone: KitchenFlr1 | Kitchen Fan | New |  | ConstantVolume |  | StaticPressure |  | 864.069 |  | 0.68085 |  | 0.5 |  | 2.5 |  | 0.75 |  | 0.855
Zone: KitchenFlr1 | KitchExh Fan | New |  | ConstantVolume |  | StaticPressure |  | 1050 |  | 0.49641 |  | 0.5 |  | 1.5 |  | 0.5 |  | 0.855
AirSystem - Name | OA - Control Name | Status |  | Economizer Control |  | Economizer Integration
AirSys |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New |  | DifferentialDryBulb |  | Integrated
KitchenMUA | Kitchen OAControl | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Common Areas: All Floors | Conditioned | New |  | OfficeClgSetpt |  | OfficeHtgSetpt
Residential Units: All Floors | Conditioned | New |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
Zone: KitchenFlr1 | Conditioned | New |  | RestaurantClgSetpt |  | RestaurantHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 363000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Condensor Type |  | Chiller Capacity |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Fluid |  | 348000 |  | 4.39 (0.8 kW/ton, 15 EER) |  | 0.6 |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 0.34 (19 W/gpm) |  | 0.5 |  | 60.39 |  | 0.855 | - | -
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 0.34 (19 W/gpm) |  | 0.5 |  | 60.39 |  | 0.855 | - | -
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 1.19 (14 W/gpm) |  | 1.5 |  | 45 |  | 0.865 | - | -
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 0.44 (13 W/gpm) |  | 0.75 |  | 40.87 |  | 0.855 |  | PumpVSDNoRstEPPwrRatio_fGPMRatio
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 85.4 |  | 1.42 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Baseline
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Common Areas: Floor 1 | BaseAirSys5 | New |  | Common Areas: Floor 1 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 2 | BaseAirSys5-2 | New |  | Common Areas: Floor 2 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 3 | BaseAirSys5-3 | New |  | Common Areas: Floor 3 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Common Areas: Floor 4 | BaseAirSys5-4 | New |  | Common Areas: Floor 4 |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Zone: KitchenFlr1 | BaseAirSys13 | New |  | Zone: KitchenFlr1 |  | SZAC |  | RestaurantHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
Thermal Zone - Floor/Zone | Zone System - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
ZnSys:CtrlZnRef | [5 empty] | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Residential Units: All Floors | Residential Units: FPFC (All) | New |  | Residential Units: All Floors |  | FPFC |  | ResidentialLivingHVACAvail |  | 58 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-4 | BaseSys5 CoilClg-4 | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys13 | BaseSys13 CoilClg | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys2 | Residential Units: BaseSys2 CoilClg (All) | New |  | ChilledWater | - | - |  | 1.15 | - | - | - | - | - | -
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency (Frac) |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 CoilHtg-4 | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-2 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-3 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys5-4 | BaseSys5 (All ReheatCoils) | New |  | HotWater | - | - |  | 1.25 | - | -
BaseAirSys13 | BaseSys13 CoilHtg | New |  | HotWater (Natural Gas) | - | - |  | 1.25 | - | -
BaseAirSys2 | Residential Units: BaseSys2 CoilHtg (All) | New |  | HotWater | - | - |  | 1.25 | - | -
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency |  | Fan Power Index
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff |  | Fan:PwrIdx
Common Areas: Floor 1 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 9800.18 |  | 9.0091 |  | 0.6 |  | 3.5 |  | 10 |  | 0.917 | - | -
Common Areas: Floor 2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1602.02 |  | 1.5148 |  | 0.5 |  | 3 |  | 2 |  | 0.865 | - | -
Common Areas: Floor 3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1597.97 |  | 1.511 |  | 0.5 |  | 3 |  | 2 |  | 0.865 | - | -
Common Areas: Floor 4 | BaseSys5 Fan-4 | New |  | VariableSpeedDrive |  | Static Pressure |  | 1689.14 |  | 1.5972 |  | 0.5 |  | 3 |  | 2 |  | 0.865 | - | -
Zone: KitchenFlr1 | BaseSys13 Fan | New |  | ConstantVolume |  | Static Pressure |  | 866.8 |  | 0.683 |  | 0.5 |  | 2.5 |  | 0.75 |  | 0.855 | - | -
Residential Units: All Floors | BaseSys2 Fan | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 265.167 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-2 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 268.617 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-3 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 261.958 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-4 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 254.771 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-5 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 255.576 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-6 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 324.484 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-7 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 253.02 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-8 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 250.738 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-9 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 227.74 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-10 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 230.092 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-11 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 224.63 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-12 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 220.886 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-13 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 224.48 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-14 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 220.265 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-15 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 223.169 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-16 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 301.128 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-17 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 232.97 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-18 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 251.179 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-19 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 228.979 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-20 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 230.333 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-21 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 225.147 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-22 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 223.468 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-23 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 223.18 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-24 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 221.964 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-25 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 221.456 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-26 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 338.491 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-27 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 261.079 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-28 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 285.691 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-29 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 259.587 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-30 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 261.061 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-31 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 253.483 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-32 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 251.318 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-33 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 251.401 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-34 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 249.234 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Residential Units: All Floors | BaseSys2 Fan-35 | New |  | ConstantVolume |  | PowerPerUnitFlow |  | 249.055 | - | - |  | 0.5 |  | 1.2734 | - | - |  | 0.855 |  | 0.35
Common Areas: Floor 1 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 9399.22 |  | 2.7773 |  | 0.4 |  | 0.75 |  | 3 |  | 0.895 | - | -
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New | - | - | - | -
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New | - | - | - | -
BaseAirSys5-4 | BaseSys5 OACtrl-4 | New | - | - | - | -
BaseAirSys13 | BaseSys13 OACtrl | New | - | - | - | -
BaseAirSys2 | - | New | - | - | - | -
Thermal Zone - Name | Conditioning Type | Status |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Common Areas: All Floors | Conditioned | New |  | OfficeClgSetpt |  | OfficeHtgSetpt
Residential Units: All Floors | Conditioned | New |  | ResidentialLivingClgSetpt |  | ResidentialLivingHtgSetpt
Zone: KitchenFlr1 | Conditioned | New |  | RestaurantClgSetpt |  | RestaurantHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 287675 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
HVAC Systems_Primary
Chiller - Name | Fluid System Name | Status |  | Chiller Type |  | Condensor Type |  | Chiller Capacity |  | Chiller Efficiency (COP) |  | Chiller Part-Load Efficiency (IPLV) |  | Chiller Min Unloading Ratio
|  |  |  | Chlr:Type |  | Chlr:CndsrType |  | Chlr:CapRtd |  | Chlr:COP |  | Chlr:IPLVkWPerTon |  | Chlr:UnldRatMin
Base Chlr | BaseChWSystem | New |  | Screw |  | Fluid |  | 436152 |  | 4.39 (0.8 kW/ton) | - | - |  | 0.15
Chiller - Name | Fluid System Name | Status |  | Chiller Cooling Capacity Adjustment Curve |  | Electric Chiller Cooling Efficiency fPLR Curves |  | Electric Chiller Cooling Efficiency fTemperature Curves |  | Chilled Water Supply Temperature |  | Chilled Water ReturnTemperature
|  |  |  | (Cap_fTempCrvRef) |  | (EIR_fPLRCrvRef) |  | (EIR_fTempCrvRef) |  | (LvgTempDsgn) |  | (EntTempDsgn)
Base Chlr | BaseChWSystem | New |  | ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI |  | ChlrWtrPosDispPathBAllEIRRatio_fQRatio |  | ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI |  | 44 F |  | 64 (20 F Delta temperature)
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP
Base HW Pump | Base Blr | New |  | OnDemand |  | ConstantSpeed |  | 0.27 (19 W/gpm) |  | 0.855
Base CW Pump | Base Tower | New |  | OnDemand |  | ConstantSpeed |  | 1.49 (14 W/gpm) |  | 0.865
Base ChW Pump | Base Chlr | New |  | OnDemand |  | VariableSpeed |  | 0.56 (13 W/gpm) |  | 0.855
Base HW Pump-2 | Base Blr-2 | New |  | OnDemand |  | ConstantSpeed |  | 0.27 (19 W/gpm) |  | 0.855
Cooling Tower - Name | Fluid System Name | Status |  | Cooling Tower -Type |  | Capacity Control |  | Condenser Water Flow Rate (gpm) |  | Total Fan (HP) |  | Cooling Tower Power Adjustment Curve
|  |  |  | HtRej:Type |  | HtRej:CapRtd |  | HtRej:WtrFlowCap |  | HtRej:TotFanHP |  | (Pwr_fPLRCrvRef)
Base Tower | BaseCWSystem | New |  | OpenTower |  | VariableSpeedDrive |  | 107.03 |  | 1.78 (60 gpm/HP) |  | HtRejVSDFanPwrRatio_fQRatio
Note on L18: Sandeep: 150330: PREVIOUS VALUE - 60,
Note on N118: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on L120: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412
Note on J123: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on R183: Sandeep: 150330: PREVIOUS VALUE 7.5
Note on F229: Sandeep: 150331: no economizer when the baseline cooling capacity < 54,000 Btu/h
Note on N249: Sandeep: 140820: Used only in proposed transforms (equal to user input values) to find the path 'A' or 'B' and adjustment curves
Note on J251: Sandeep: 150330: PREVIOUS VALUE 433925
Note on L251: Sandeep: EER = 12 / (kW/ton) COP = EER / 3.412

## 030006S-OffMed-Run23 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006S-OffMed-Run23 |  |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006S-OffMed-Run23.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Existing Alteration |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.065 |  | 0.8 |  | 0.8 |  | 0.1 |  | 0.9
Exterior Wall | NACM_Metal Framed Wall | New | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | Exisiting | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New |  | Top Floor-South Window |  | FixedWindow |  | 0.4 |  | 0.33 |  | 0.5
Window | FixedWindow_Unaltered | Exisiting |  | All Other |  | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3 |  | 0.33 |  | 0.33 |  | 0.33 |  | 0.22
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | NACM_Metal Framed Wall | Exisiting/New |  | 1.) Stucco - 7/8 in. |  | 2.) Building Paper - 1/16 in. |  | 3.) Expanded Polystyrene - EPS - 3 in. R13 |  | 4.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 5.) Gypsum Board - 1/2 in. | - | -
Roof | NACM_Roof | New |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Expanded Polystyrene - EPS - 3 1/2 in. R15 | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Flr / All Zone | BottomVAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Flr / All Zone | Mid VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / All Zone (Except Zone 4) | Top VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / Zone 4 | Perimeter_top_ZN_4 New AirSys | New |  | Top Floor - Zone 4 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perimeter_top_ZN_4 New AirSys | Perim_top_4Zn CoolingCoil | New |  | DirectExpansion |  | 13 | - | - |  | CoilClgDXSEER18EER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BottomVAV | Bottom VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | CoreBottomReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom4ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | Mid VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | CoreMidReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid4ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | Top VAV CoilHeating | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | CoreTopReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop1ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop2ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop3ReheatCoil | Exisiting |  | Hot Water | - | - | - | - | - | -
Perimeter_top_ZN_4 New AirSys | Perim_top_4Zn HeatingCoil | New |  | Furnace (Natural Gas) |  | 0.80517 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BottomVAV | BottomVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower |  | 20.45 | - | - | - | - |  | 25 |  | 0.936
Mid VAV | MidVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower |  | 20.8 | - | - | - | - |  | 25 |  | 0.936
Top VAV | TopVAV SupplyFan | Exisiting |  | VariableSpeedDrive |  | BrakeHorsePower |  | 18.76 | - | - | - | - |  | 20 |  | 0.93
Perimeter_top_ZN_4 New AirSys | Perim_top_4ZnSupplyFan | New |  | Constant Volume |  | BrakeHorsePower |  | 1.23 | - | - | - | - |  | 1.5 |  | 0.865
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV | BottomVAV Economizer | Exisiting |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV | MidVAV OACtrl | Exisiting |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV | Top VAV OACtrl | Exisiting |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Perimeter_top_ZN_4 New AirSys | Perime1OAControl | New | - | - | - | - | - | - | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 |  | Exisiting |  | 600000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 0.59 (19.68 W/gpm) |  | 0.8 |  | 65.86 |  | 0.9 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU098 | New | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | Exisiting | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting |  | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.3 |  | 0.33 |  | 0.33 |  | 0.33 |  | 0.22
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Exterior Wall | MetalFrameWallU098 | New |  | 1.) Stucco - 7/8 in. |  | 2.) Compliance Insulation R8.07 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | Exisiting |  | 1.) Stucco - 7/8 in. |  | 2.) Building Paper - 1/16 in. |  | 3.) Expanded Polystyrene - EPS - 3 in. R13 |  | 4.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 5.) Gypsum Board - 1/2 in. | - | -
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Compliance Insulation R12.55 | - | - | - | - | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  | AirSys:Type |  | AirSys:AvailSchRef |  |  |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Flr / All Zone | BottomVAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Flr / All Zone | Mid VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / All Zone (Except Zone 4) | Top VAV | Exisiting | - | - |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Flr / Zone 4 | BaseAirSys3 | New |  | Top Floor - Zone 4 |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion |  | 10.8446 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BottomVAV | Bottom VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | CoreBottomReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BottomVAV | PerimeterBottom4ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | Mid VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | CoreMidReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Mid VAV | PerimeterMid4ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | Top VAV CoilHeating | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | CoreTopReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop1ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop2ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
Top VAV | PerimeterTop3ReheatCoil | Existing |  | Hot Water | - | - | - | - | - | -
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) |  | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BottomVAV | BottomVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 20.45 | - | - | - | - |  | 25 |  | 0.936
Mid VAV | MidVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 20.8 | - | - | - | - |  | 25 |  | 0.936
Top VAV | TopVAV SupplyFan | Existing |  | VariableSpeedDrive |  | BrakeHorsePower | - | - |  | 18.76 | - | - | - | - |  | 20 |  | 0.93
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume |  | StaticPressure |  | 1176.54 |  | 0.92597 |  | 0.5 |  | 2.5 |  | 1 |  | 0.855
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt |  | OfficeHtgSetPt
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BottomVAV | BottomVAV Economizer | Existing |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV | MidVAV OACtrl | Existing |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV | Top VAV OACtrl | Existing |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
BaseAirSys3 | BaseSys3 OACtrl | New | - | - | - | - | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 |  | Exisiting |  | 600000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 0.59 (19.68 W/gpm) |  | 0.8 |  | 65.86 |  | 0.9 | - | -
Note on B17: Sandeep: 140811: underground wall not being tested, not documented
Note on L43: Sandeep: 150218: Design Suppy Air Temperature (Cooling) changed from 60 to 55 for Office space SZAC system
Note on H73: Sandeep: =0.0051427*(79)+0.3989
Note on I84: Sandeep: 150331: Check Parameter added
Note on L84: Sandeep: 150331: Check Parameter added
Note on L143: Sandeep: 150218: Design Suppy Air Temperature (Cooling) changed from 60 to 55 for Office space SZAC system
Note on H173: Sandeep: =0.0051427*(79)+0.3989
Note on J181: Sandeep: 150330: capacity reduced from 1596.99 to 1176.54
Note on R181: Sandeep: 150218: Motor HP changed from 1.5 to 1
Note on T181: Sandeep: 150218: MtrEff changed from 0.865 to 0.855
Note on I192: Sandeep: 150331: Check Parameter added
Note on L192: Sandeep: 150331: Check Parameter added

## 020006S-OffSml-Run24 (hidden)
General Details |  |  |  | Model/Software Details |  |  |  |  | Key
Test Name | 020006S-OffSml-Run24 |  |  | Model Revision no. |  |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006S-OffSml-Run24.cibd |  |  | Version of Ruleset (Trunk rev. No.) | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Existing Alteration |  |  | Testing Performed by | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered |  | Top Floor-South Window | FixedWindow |  | 0.4 |  | 0.33 |  | 0.5
Window | FixedWindow_Unaltered | Exisiting |  | All Other | FixedWindow |  | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.21 | 0.2 |  | 0.2 |  | 0.24 |  | 0.2
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Core_ZN Thermal Zone | CoreZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | Perim1ZnPSZ AirSys_New | New |  | Bottom Floor - Zone 1 | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
CoreZnPSZ AirSys | CoreZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnPSZ AirSys | Perim2ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 | - | - |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil | Existing |  | DirectExpansion | 10.8446 |  |  |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim1ZnPSZ AirSys_New | Perim1ZnCoolingCoil | New |  | DirectExpansion | 13 | - | - |  | CoilClgDXSEER18EER13EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
CoreZnPSZ AirSys | CoreZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim2ZnPSZ AirSys | Perim2ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil | Existing |  | Furnace (Natural Gas) | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Perim1ZnPSZ AirSys_New | Perim1ZnHeatingCoil | New |  | Furnace (Natural Gas) | 0.80414 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP | Fan:MtrEff
CoreZnPSZ AirSys | CoreZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower |  | 1.6 | - | - | - | - |  | 2 | 0.865
Perim2ZnPSZ AirSys | Perim2ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower |  | 0.8 | - | - | - | - |  | 1 | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower |  | 1.2 | - | - | - | - |  | 1.5 | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan | Existing |  | ConstantVolume | BrakeHorsePower |  | 0.8 | [5 empty] | 1 | 0.855
Perim1ZnPSZ AirSys_New | Perim1ZnSupplyFan | New |  | Constant Volume | BrakeHorsePower |  | 1.12 | - | - | - | - |  | 1.5 | 0.855
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
Fan:ZnServed | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_4 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered |  | FixedWindow | 0.47 |  | 0.31 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting |  | FixedWindow | 0.55 |  | 0.56 |  | 0.6
|  | Type |  | Overall WWR (Frac) | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.21 | 0.2 |  | 0.2 |  | 0.24 |  | 0.2
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Core_ZN Thermal Zone | CoreZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_2 Thermal Zone | Perim2ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_3 Thermal Zone | Perim3ZnPSZ AirSys | Exisiting | - | - | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_4 Thermal Zone | Perim4ZnPSZ AirSys | Exisiting |  |  | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
Perimeter_ZN_1 Thermal Zone | BaseAirSys3 | New |  | Bottom Floor - Zone 1 | SZAC |  | OfficeHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
CoreZnPSZ AirSys | CoreZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim2ZnPSZ AirSys | Perim2ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim3ZnPSZ AirSys | Perim3ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Perim4ZnPSZ AirSys | Perim4ZnCoolingCoil | Exisiting |  | DirectExpansion | 10.8 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion | 10.8446 |  | 1.15 |  | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI |  | CoilClgDXSEEREIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
CoreZnPSZ AirSys | CoreZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
Perim2ZnPSZ AirSys | Perim2ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
Perim3ZnPSZ AirSys | Perim3ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
Perim4ZnPSZ AirSys | Perim4ZnHeatingCoil | Exisiting |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) | 0.80003 |  | 1.25 |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
CoreZnPSZ AirSys | CoreZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower | - | - |  | 1.6 | - | - | - | - | 2 | 0.865
Perim2ZnPSZ AirSys | Perim2ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower | - | - |  | 0.8 | - | - | - | - | 1 | 0.855
Perim3ZnPSZ AirSys | Perim3ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower | - | - |  | 1.2 | - | - | - | - | 1.5 | 0.855
Perim4ZnPSZ AirSys | Perim4ZnSupplyFan | Exisiting |  | ConstantVolume | BrakeHorsePower | - | - |  | 0.8 | - | - | - | - | 1 | 0.855
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume | StaticPressure |  | 1529.06 |  | 1.2034 |  | 0.5 |  | 2.5 | 1.5 | 0.865
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef | ThrmlZn:HtgTstatSchRef
Core_ZN Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_2 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_3 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_4 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Perimeter_ZN_1 Thermal Zone | Conditioned |  |  | OfficeClgSetPt | OfficeHtgSetPt
Note on L26: Sandeep: 141223: Design Supply Air 150218: Temperature (Cooling) changed from 60 to 55 for SZAC system , office core zone
Note on H48: Sandeep: 140813: Value updated from 0.81 to .804 Issue: both AFUE and Thermal efficiency was being hard input (thermal efficiency not required for capacity below 225000) Thermal efficiency from AFUE formula changed to - 0.0051427*AFUE+0.3989
Note on L85: Sandeep: 150218: Design Supply Air Temperature (Cooling) changed from 60 to 55 for SZAC system , office core zone
Note on J116: Sandeep: 150330: Capacity changed from 1700.05 to 1529.06
Note on L116: Sandeep: 141223: BHP changed from 1.34 to 1.2

## 020006S-OffSml-Run25 (hidden)
General Details |  |  | Model/Software Details |  |  |  | Key
Test Name | 020006S-OffSml-Run25 |  | Model Revision no. |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006S-OffSml-Run25.cibd |  | Version of Ruleset (Trunk rev. No.) | v3b |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2013-3b (717) |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Existing Alteration |  | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Relevant Position | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC | FenConsRef:VT
Window | FixedWindow_Altered | Altered | South Window | FixedWindow | 0.4 |  | 0.33 | 0.5
Window | FixedWindow_Unaltered | Exisiting | All Other | FixedWindow | 0.55 |  | 0.56 | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | Altered | FixedWindow | 0.47 | 0.31 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting | FixedWindow | 0.55 | 0.56 |  | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2

## 020006S-OffSml-Run26 (hidden)
General Details |  |  | Model/Software Details |  |  |  | Key
Test Name | 020006S-OffSml-Run26 |  | Model Revision no. |  |  |  | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 020006S-OffSml-Run26.cibd |  | Version of Ruleset (Trunk rev. No.) | v3b |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  | CBECC Software | CBECC-Com 2013-3b (717) |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  | Date Tested |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Existing Alteration |  | Testing Performed by | Sandeep Doddaballapur |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Relevant Position | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) |  | SHGC | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType | FenConsRef:UFactor |  | FenConsRef:SHGC | FenConsRef:VT
Window | FixedWindow_Altered | New | South Window | FixedWindow | 0.35 |  | 0.32 | 0.53
Window | FixedWindow_Unaltered | Exisiting | All Other | FixedWindow | 0.55 |  | 0.56 | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.42 | 0.2 | 0.2 |  | 0.94 | 0.2
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status | Construction Assembly Type | Overall U value (Btu/h-°F-ft2) | SHGC |  | Visual Transmittance
| FenConsRef:Name |  | FenConsRef:FenProdType | FenConsRef:UFactor | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindow_Altered | New | FixedWindow | 0.36 | 0.25 |  | 0.42
Window | FixedWindow_Unaltered | Exisiting | FixedWindow | 0.55 | 0.56 |  | 0.6
|  | Type | Overall WWR (Frac) | North WWR (Frac) | East WWR (Frac) |  | South WWR (Frac) | West WWR (Frac)
|  |  | CondWWR | NorthCondWWR | EastCondWWR |  | SouthCondWWR | WestCondWWR
|  | Window | 0.4 | 0.19 | 0.19 |  | 0.89 | 0.19

## 050006S-RetlMed-Run27 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 050006S-RetlMed-Run27 |  |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 050006S-RetlMed-Run27.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Existing Addition |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Relevant Position |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 | New |  | South Windows (All Windows) |  | FixedWindow |  | 0.35 |  | 0.32 |  | 0.53
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.37 |  | 0 |  | 0 |  | 0.45 |  | 0
Internal Load Components
Space
Space Name | Space Function |  |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Front_Entry | Lobby, Main Entry |  |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.6 |  | 0.75 |  | 2.35 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.15 | - | - |  | 1.15 |  | RetailLights | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor / All Zones | SouthAddtn AirSys | New |  | All additions |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl | .cibd
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
SouthAddtn AirSys | SouthAddtn CoolingCoil | New |  | DirectExpansion |  | 11 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
SouthAddtn AirSys | SouthAddtn HeatingCoil | New |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP | Fan:MtrEff
SouthAddtn AirSys | SouthAddtn SupplyFan | New |  | Constant Volume |  | BrakeHorsePower |  | 3.2 | - | - | - | - |  | 3 | 0.895
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
SouthAddtn AirSys | SouthAddtn OAControl | New |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Baseline
Envelope Components
Fenestrations
Type | Construction Assembly Name | Status |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 | New |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.37 |  | 0 |  | 0 |  | 0.45 |  | 0
Internal Load Components
Space
Space Name | Space Function |  |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Front_Entry | Lobby, Main Entry |  |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.5 |  | 0.65 |  | 2.15 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor / All Zones | BaseAirSys3 | New |  | All additions |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys3 | BaseSys3 CoilClg | New |  | DirectExpansion |  | 10.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys3 | BaseSys3 CoilHtg | New |  | Furnace (Natural Gas) |  | 0.8 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP | Fan:MtrEff
BaseAirSys3 | BaseSys3 Fan | New |  | ConstantVolume |  | StaticPressure |  | 6983.94 |  | 5.4966 |  | 0.6 |  | 3 | 7.5 | 0.917
BaseAirSys3 | BaseRelief Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 6821.61 |  | 2.0133 |  | 0.4 |  | 0.75 | 3 | 0.895
AirSystem - Name | Outside Air Control - Name | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
SouthAddtn AirSys | BaseSys3 OACtrl | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Note on H102: Sandeep: 150330: PREVIOUSLY 'UNDEFINED'

## 050006S-RetlMed-Run28 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 050006-RetlMed-Run28 |  |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 050006-RetlMed-Run28.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | Existing Addition and Alteration |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | Altered metal bldg roof | Altered |  | Low |  | MetalBuildingRoof |  | 0.03 |  | 0.75 |  | 0.75 |  | 0.08 |  | 0.92
Roof | Other Altered Roof | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.021 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Low |  | WoodFramingAndOtherRoof |  | 1.282 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.039 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | Altered metal frame wall | Altered | - | - |  | MetalFrameWall |  | 0.053 | - | - | - | - | - | - | - | -
Exterior Wall | Altered metal building wall | Altered | - | - |  | MetalBuildingWall |  | 0.052 | - | - | - | - | - | - | - | -
Exterior Wall | New heavy mass wall | New | - | - |  | MassHeavyWall |  | 0.051 | - | - | - | - | - | - | - | -
Exterior Wall | Altered light mass wall | Altered | - | - |  | MassLightWall |  | 0.046 | - | - | - | - | - | - | - | -
Exterior Wall | Altered heavy mass wall | Altered | - | - |  | MassHeavyWall |  | 0.051 | - | - | - | - | - | - | - | -
Exterior Wall | Base_CZ12-NonresMetalFrameWallU062 | New | - | - |  | MetalFrameWall |  | 0.062 | - | - | - | - | - | - | - | -
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | Altered metal bldg roof | Altered |  | 1.) Insulation/Framing Layer - Metal, RoofMetalStandingSeam, cav. R-20 |  | 2.) Air - Cavity - Wall Roof Ceiling - 4 in. or more |  | 3.) Expanded Polystyrene - EPS - 4 1/16 in. R17 | - | - | - | - | - | -
Roof | Other Altered Roof | Altered |  | 1.) Built-up roofing - 3/8 in. |  | 2.) Expanded Polystyrene - EPS - 6 1/10 in. R25 |  | 3.) Insulation/Framing Layer - Wood, Roof24in OC, 2x6, cav. R-19 |  | 4.) Air - Cavity - Wall Roof Ceiling - 4 in. or more |  | 5.) Acoustic Tile - 3/4 in. | - | -
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | 1.) Metal Standing Seam - 1/16 in. | - | - | - | - | - | - | - | - | - | -
Roof | Base_CZ12-FlatNonresWoodFramingAndOtherRoofU039 | New |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Compliance Insulation R24.86 | - | - | - | - | - | - | - | -
Exterior Wall | Altered metal frame wall | Altered |  | 1.) Stucco - 7/8 in. |  | 2.) Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall | Altered metal building wall | Altered |  | 1.) Metal Siding - 1/16 in. |  | 2.) Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Plywood 3/4in | - | - | - | -
Exterior Wall | New heavy mass wall | New |  | 1.) Stucco - 7/8 in. |  | 2.) Concrete - 140 lb/ft3 - 6 in. |  | 3.) Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | 4.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 5.) Gypsum Board - 1/2 in. | - | -
Exterior Wall | Altered light mass wall | Altered |  | 1.) Stucco - 7/8 in. |  | 2.) Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. |  | 3.) Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. |  | 4.) Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | 5.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 5.) Gypsum Board - 1/2 in.
Exterior Wall | Altered heavy mass wall | Altered |  | 1.) Stucco - 7/8 in. |  | 2.) Concrete - 140 lb/ft3 - 6 in. |  | 3.) Expanded Polystyrene - EPS - 4 1/16 in. R17 |  | 4.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 5.) Gypsum Board - 1/2 in. | - | -
Exterior Wall | Base_CZ12-NonresMetalFrameWallU062 | New |  | 1.) Stucco - 7/8 in. |  | 2.) Compliance Insulation R13.99 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall (UnConditioned) | Base_CZ12-NonresMetalFrameWallU062 | New |  | 1.) Stucco - 7/8 in. |  | 2.) Compliance Insulation R13.99 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Fenestrations
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.07 |  | 0 |  | 0 |  | 0.25 |  | 0
Internal Load Components
Space
Space Name | Space Function |  |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  |  | 0.5 | - | - |  | 0.5 |  | RetailLights | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
Front_Entry | Lobby, Main Entry |  |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.6 |  | 0.75 |  | 2.35 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.15 | - | - |  | 1.15 |  | RetailLights | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor / Exisiting Zones | BaseAirSys5 | Exisiting |  | Exisiting Zones |  | PVAV |  | RetailHVACAvail |  | 60 |  | 60 |  | WarmestReset |  | 60 |  | 55
Bottom Floor / Addition Zones | SouthAddtn AirSys | Exisiting |  | All South Zones |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
SouthAddtn AirSys | SouthAddtn CoolingCoil | Exisiting |  | DirectExpansion |  | 11 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | Exisiting |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil | Exisiting |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil-2 | Exisiting |  | HotWater | - | - | - | - | - | -
SouthAddtn AirSys | SouthAddtn HeatingCoil | Exisiting |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
Thermal Zone - Floor/Zone | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
Fan:ZnServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
Bottom Floor / Exisiting Zones | BaseSys5 Fan | Exisiting |  | VariableSpeedDrive |  | Static Pressure |  | 21.67 |  | 0.62 |  | 4 |  | 25 |  | 0.936
Bottom Floor / Addition Zones | SouthAddtn SupplyFan | Exisiting |  | Constant Volume |  | BrakeHorsePower |  | 3.2 | - | - | - | - |  | 3.5 |  | 0.895
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | Exisiting |  | DifferentialDryBulb |  | Integrated
SouthAddtn AirSys |  | Exisiting |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Back_Space | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Core_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | Exisiting |  | 240681 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 0.23 (19.0 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresMetalBuildingRoofU065 | Altered |  | Low |  | MetalBuildingRoof |  | 0.065 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofU075 | Altered |  | Low |  | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | Low |  | WoodFramingAndOtherRoof |  | 1.282 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU098 | Altered | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Exterior Wall | MetalBldgWallU113 | Altered | - | - |  | MetalBuildingWall |  | 0.113 | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | New | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Exterior Wall | MassLightWallU440 | Altered | - | - |  | MassLightWall |  | 0.44 | - | - | - | - | - | - | - | -
Exterior Wall | MassHeavyWallU690 | Altered | - | - |  | MassHeavyWall |  | 0.69 | - | - | - | - | - | - | - | -
Exterior Wall (UnConditioned) | MetalFrameWallUnconditioned | New |  |  |  | MetalFrameWall |  | 0.971
Exterior Wall | MetalFrameWallU098 | New | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | FlatNonresMetalBuildingRoofU065 | Altered |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Compliance Insulation R14.60 | - | - | - | - | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofU075 | Altered |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Compliance Insulation R12.55 | - | - | - | - | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofUnconditioned | New |  | 1.) Metal Standing Seam - 1/16 in. | - | - | - | - | - | - | - | - | - | -
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Compliance Insulation R12.55 | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | Altered |  | 1.) Stucco - 7/8 in. |  | 2.) Compliance Insulation R8.07 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall | MetalBldgWallU113 | Altered |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Compliance Insulation R8.00 | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | New |  | 1.) Stucco - 7/8 in. |  | 2.) Compliance Insulation R8.07 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall | MassLightWallU440 | Altered |  | 1.) Concrete - 140 lb/ft3 - 4 in. |  | 2.) Compliance Insulation R0.02 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall | MassHeavyWallU690 | Altered |  | 1.) Concrete - 140 lb/ft3 - 8 in. |  | 2.) Compliance Insulation R0.01 | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | New |  | 1.) Stucco - 7/8 in. |  | 2.) Compliance Insulation R8.07 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Exterior Wall (UnConditioned) | MetalFrameWallUnconditioned | New |  | 1.) Stucco - 7/8 in. | - | - | - | - | - | - | - | - | - | -
Fenestrations
|  | Type |  | Overall WWR (Frac) |  | North WWR (Frac) |  | East WWR (Frac) |  | South WWR (Frac) |  | West WWR (Frac)
|  |  |  | CondWWR |  | NorthCondWWR |  | EastCondWWR |  | SouthCondWWR |  | WestCondWWR
|  | Window |  | 0.07 |  | 0 |  | 0 |  | 0.25 |  | 0
Internal Load Components
Space
Space Name | Space Function |  |  | Lighting Power Density (General Lighting) |  | Lighting Power Density (TailoredFloorDisplayAllowance) (W/ft2) |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name |  | Interior Lighting Specification Method |  | Allowance Area (ft2)
Spc |  |  |  | IntLPDReg |  | IntLPDReg |  | IntLPDReg |  | IntLtgRegSchRef:Name |  |  |  | IntLtgSys:AllowArea
Back_Space | Commercial and Industrial Storage Areas (conditioned or unconditioned) |  |  | 0.5 | - | - |  | 0.5 |  | RetailLights | - | - | - | -
Core_Retail | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
Front_Entry | Lobby, Main Entry |  |  | 1.5 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
Front_Retail | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.5 |  | 0.65 |  | 2.15 |  | RetailLights |  | Tailored Method |  | 810
Point_Of_Sale | Retail Merchandise Sales, Wholesale Showroom |  |  | 1.2 | - | - |  | 1.2 |  | RetailLights | - | - | - | -
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor / Exisiting Zones | BaseAirSys5 | Exisiting |  | Exisiting Zones |  | PVAV |  | RetailHVACAvail |  | 60 |  | 60 |  | WarmestReset |  | 60 |  | 55
Bottom Floor / Addition Zones | SouthAddtn AirSys | Exisiting |  | All South Zones |  | SZAC |  | RetailHVACAvail |  | 55 |  | 95 |  | NoSATControl | - | - | - | -
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | Exisiting |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
SouthAddtn AirSys | SouthAddtn CoolingCoil | Exisiting |  | DirectExpansion |  | 11 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source |  | Thermal Efficiency |  | System Oversizing factor |  | Furnace Fuel Heating Part Load Efficiency Curve
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type |  | CoilHtg:FurnThrmlEff |  |  |  | (FurnHIR_fPLRCrvRef)
BaseAirSys5 | BaseSys5 CoilHtg | Existing |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil | Existing |  | HotWater | - | - | - | - | - | -
BaseAirSys5 | BaseVAVReheatCoil-2 | Existing |  | HotWater | - | - | - | - | - | -
SouthAddtn AirSys | SouthAddtn HeatingCoil | Existing |  | Furnace (Natural Gas) |  | 0.80003 | - | - |  | CoilHtgFurnFIRRatio_fQRatio
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BaseAirSys5 | BaseSys5 Fan | Exisiting |  | VariableSpeedDrive |  | Static Pressure | - | - |  | 21.67 |  | 0.62 |  | 4 |  | 25 |  | 0.936
SouthAddtn AirSys | SouthAddtn SupplyFan | Exisiting |  | Constant Volume |  | BrakeHorsePower | - | - |  | 3.2 | - | - | - | - |  | 3.5 |  | 0.895
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | Exisiting |  | DifferentialDryBulb |  | Integrated
SouthAddtn AirSys |  | Exisiting |  | NoEconomizer | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
Back_Space | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Core_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Front_Entry | Unconditioned |  | - | - | - | -
Front_Retail | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Point_Of_Sale | Conditioned |  |  | RetailClgSetpt |  | RetailHtgSetpt
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | Exisiting |  | 240681 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
|  |  |  | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | Exisiting |  | OnDemand |  | ConstantSpeed |  | 0.23 (19.0 W/gpm) |  | 0.5 |  | 60.4 |  | 0.855 | - | -
Note on L62: Sandeep: 150218: Design Suppy Air Temperature (Cooling) changed from 55 to 60 for PVAV system
Note on J154: Sandeep: 150321: Same as proposed as the space in unconditioned, unconditioned spaces cannot have an LPD less than the Baseline value
Note on L162: Sandeep: 150218: Design Suppy Air Temperature (Cooling) changed from 55 to 60 for PVAV system

## 030006S-OffMed-Run29 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run29 |  |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run29.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Envelope |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | NACM_Roof | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.065 |  | 0.78 |  | 0.78 |  | 0.75 |  | 0.25
Exterior Wall | NACM_Metal Framed Wall | New | - | - |  | MetalFrameWall |  | 0.068 | - | - | - | - | - | - | - | -
Exterior Floor | NACM_Conc Raised Flr | New | - | - |  | MassFloor |  | 0.039 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 |  |  | FixedWindow |  | 0.35 |  | 0.32 |  | 0.53
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | NACM_Roof | New |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Expanded Polystyrene - EPS - 3 1/2 in. R15 | - | - | - | - | - | - | - | -
Exterior Wall | NACM_Metal Framed Wall | New |  | 1.) Stucco - 7/8 in. |  | 2.) Building Paper - 1/16 in. |  | 3.) Expanded Polystyrene - EPS - 3 in. R13 |  | 4.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 5.) Gypsum Board - 1/2 in. | - | -
Exterior Floor | NACM_Conc Raised Flr | New |  | 1.) Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 |  | 2.) Concrete - 80 lb/ft3 - 4 in. |  | 3.) Metal Deck - 1/16 in. |  | 4.) OSB - Oriented Strand Board - 5/8 in. |  | 5.) Carpet - 3/4 in. | - | -
Internal Load Components
Space
Space Name | Space Function |  |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Spaces) | Office (Greater than 250 square feet in floor area) |  |  | 0.75 |  | OfficeLights
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 18831.5 |  | 19.1238 |  | 0.62 |  | 4 |  | 20 |  | 0.93
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 18144 |  | 18.4256 |  | 0.62 |  | 4 |  | 20 |  | 0.93
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 18256.9 |  | 18.5403 |  | 0.62 |  | 4 |  | 20 |  | 0.93
BaseRelief Fan | BaseAirSys5 | New |  | VariableSpeedDrive |  | Static Pressure |  | 17937.7 |  | 5.647 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917
BaseRelief Fan-2 | BaseAirSys5-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 17250.2 |  | 5.4306 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917
BaseRelief Fan-3 | BaseAirSys5-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 17363.1 |  | 5.4661 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 293409 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 0.28 (19 W/gpm) |  | 0.5 |  | 60.39 |  | 0.855 | - | -
Baseline
Envelope Components
Opaque
Type | Construction Assembly Name | Status |  | Slope Category |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | Construction Assembly Thermal emittance (frac.) |  | Construction Assembly Exterior Thermal Absorptance (frac.) |  | Construction Assembly Aged Solar Reflectance (frac.) |  | Construction Assembly Exterior Solar Absorptance (frac.)
| ConsAssmRef:Name |  |  | SlopeType |  | ConsType |  | ConsAssmRef:Ufactor |  | ConsAssmRef:CRRCAgedEmittance |  | ConsAssmRef:ExtThrmlAbs |  | ConsAssmRef:CRRCAgedRefl |  | ConsAssmRef:ExtSolAbs
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | Low |  | WoodFramingAndOtherRoof |  | 0.075 |  | 0.85 |  | 0.85 |  | 0.63 |  | 0.37
Exterior Wall | MetalFrameWallU098 | New | - | - |  | MetalFrameWall |  | 0.098 | - | - | - | - | - | - | - | -
Exterior Floor | OtherFloorU071 | New | - | - |  | OtherFloor |  | 0.071 | - | - | - | - | - | - | - | -
Fenestrations
Type | Construction Assembly Name |  |  | Construction Assembly Type |  | Overall U value (Btu/h-°F-ft2) |  | SHGC |  | Visual Transmittance
| FenConsRef:Name |  |  | FenConsRef:FenProdType |  | FenConsRef:UFactor |  | FenConsRef:SHGC |  | FenConsRef:VT
Window | FixedWindowU35 |  |  | FixedWindow |  | 0.36 |  | 0.25 |  | 0.42
Constructions/Layers
Opaque
Type | Construction Assembly Name | Status |  | Layers -1 |  | Layers -2 |  | Layers -3 |  | Layers -4 |  | Layers -5 |  | Layers -6
| ConsAssmRef:Name |  |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem |  | CodeItem
Roof | FlatNonresWoodFramingAndOtherRoofU075 | New |  | 1.) Metal Standing Seam - 1/16 in. |  | 2.) Compliance Insulation R12.55 | - | - | - | - | - | - | - | -
Exterior Wall | MetalFrameWallU098 | New |  | 1.) Stucco - 7/8 in. |  | 2.) Compliance Insulation R8.07 |  | 3.) Air - Metal Wall Framing - 16 or 24 in. OC |  | 4.) Gypsum Board - 1/2 in. | - | - | - | -
Exterior Floor | OtherFloorU071 | New |  | 1.) Compliance Insulation R9.83 |  | 2.) Plywood - 5/8 in. |  | 3.) Carpet - 3/4 in. | - | - | - | - | - | -
Internal Load Components
Space
Space Name | Space Function |  |  | Lighting Power Density Simulated (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Spaces) | Office (Greater than 250 square feet in floor area) |  |  | 0.75 |  | OfficeLights
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type |  | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset |  | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseAirSys5 | BaseSys5 CoilHtg | New |  | HotWater
BaseAirSys5-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseAirSys5-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) |  | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress |  | Fan:MtrHP |  | Fan:MtrEff
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 18629.1 |  | 18.9183 |  | 0.62 |  | 4 |  | 20 |  | 0.93
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 17661.3 |  | 17.9354 |  | 0.62 |  | 4 |  | 20 |  | 0.93
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 18184.4 |  | 18.4667 |  | 0.62 |  | 4 |  | 20 |  | 0.93
BaseAirSys5 | BaseRelief Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 17735.3 |  | 5.5833 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917
BaseAirSys5-2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 16767.5 |  | 5.2786 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917
BaseAirSys5-3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 17290.6 |  | 5.4433 |  | 0.5 |  | 1 |  | 7.5 |  | 0.917
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration
BaseAirSys5 | BaseSys5 OACtrl | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-2 | BaseSys5 OACtrl-2 | New |  | DifferentialDryBulb |  | Integrated
BaseAirSys5-3 | BaseSys5 OACtrl-3 | New |  | DifferentialDryBulb |  | Integrated
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers |  | Status |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 |  | New |  | 323935 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) |  | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd |  | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 0.31 (19 W/gpm) |  | 0.5 |  | 60.39 |  | 0.855 | - | -
Note on J64: Sandeep: 150320: Capacities changes slightly for all fans but not enough to affect other dependent properties. Eg: BaseSys5 Fan changed from 18837.9 cfm to 18831.5 cfm.
Note on H67: Sandeep: 150330: PREVIOUSLY REPORTED AS 'UNDEFINED'
Note on F87: Sandeep: 150320: Slight change in capacity from 293502 to 293409
Note on J148: Sandeep: 150320: Capacities changes slightly for all fans but not enough to affect other dependent properties. Eg: BaseSys5 Fan changed from 18631.1 cfm to 18629.1 cfm.
Note on B151: Sandeep: 140821: System Relief fan first accounted for in rev. 2432,
Note on H151: Sandeep: 150330: PREVIOUSLY REPORTED AS 'UNDEFINED'
Note on F172: Sandeep: 150320: Capacity decreased slightly from 323981 to 323935

## 030006S-OffMed-Run30 (hidden)
General Details |  |  |  | Model/Software Details | [5 empty] | Key
Test Name | 030006-OffMed-Run30 |  |  | Model Revision no. | [5 empty] | EnergyPlus calculates the Overall U-value of the assemblies using the materials and layers definitions, hence not evaluated.
Model File Name | 030006-OffMed-Run30.cibd |  |  | Version of Ruleset (Trunk rev. No.) |  | v3b |  |  | 1 | Intermediate values, not directly evaluated
Climate Zone | CZ-06 |  |  | CBECC Software |  | CBECC-Com 2013-3b (717) |  |  | 1 | Intermediate values, not directly evaluated
Building Type | Medium Office |  |  | Date Tested |  |  |  |  | 1 | Value in cell based on a calculation performed within the cell
Test Category | New Mechanical and Partial Lighting |  |  | Testing Performed by |  | Sandeep Doddaballapur |  |  | 1 | Intermediate values, not directly evaluated, based on a calculation performed within the cell
Proposed
Internal Load Components
Space
Space Name | Space Function | Status |  | Installed Power (Watts) |  | Simulated Lighting Power |  | Control Credit Type |  | Power adjustment factor |  | Lighting Power Density (Simulated) (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | Spc:RegInstPwr |  | Spc:RegPwr |  | IntLtgSys:PAFCredType |  | IntLtgSys:PAF |  | Spc:IntLPDReg |  | IntLtgRegSchRef:Name
(All Levels - Core Zones) | Office (Greater than 250 square feet in floor area) | New |  | 8448 |  | 5068.8 |  | OccupantSensingControls-1to125SF |  | 0.4 |  | 0.48 |  | OfficeLights
(All Levels - South Zones - Zone 1) | Office (Greater than 250 square feet in floor area) | New | - | - | - | - | - | - | - | - |  | 0.8 |  | OfficeLights
(All Levels - All other Zones) | Office (Greater than 250 square feet in floor area) | Existing | - | - | - | - | - | - | - | - |  | 1.2 |  | OfficeLights
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor | BottomVAV | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset | 60 |  | 55
Mid Floor | Mid VAV | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset | 60 |  | 55
Top Floor | Top VAV | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BottomVAV | Bottom VAV CoilCooling | New |  | DirectExpansion |  | 13.1 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Mid VAV | Mid VAV CoilCooling | New |  | DirectExpansion |  | 13.1 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
Top VAV | Top VAV CoilCooling | New |  | DirectExpansion |  | 13.1 | - | - |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXSnglEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BottomVAV | Bottom VAV CoilHeating | New |  | HotWater
Mid VAV | Mid VAV CoilHeating | New |  | HotWater
Top VAV | Top VAV CoilHeating | New |  | HotWater
BottomVAV | (All ReheatCoils) | New |  | HotWater
Mid VAV | (All ReheatCoils) | New |  | HotWater
Top VAV | (All ReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP |  | Fan:MtrEff
BottomVAV | BottomVAV SupplyFan | New |  | ConstantVolume |  | BrakeHorsePower | - | - |  | 14.085 | - | - | - | - | 15 |  | 0.9
Mid VAV | MidVAV SupplyFan | New |  | ConstantVolume |  | Static Pressure |  | 17875.9 |  | 12.9866 |  | 0.65 |  | 3 | 15 |  | 0.9
Top VAV | TopVAV SupplyFan | New |  | ConstantVolume |  | Static Pressure |  | 17875.9 |  | 18.1534 |  | 0.62 |  | 4 | 20 |  | 0.9
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl: |  | OACtrl:
BottomVAV |  | New |  | DifferentialEnthalpy |  | Integrated | - | - |  | 30
Mid VAV |  | New |  | FixedDryBulb |  | NonIntegrated |  | 75 | - | -
Top VAV |  | New |  | DifferentialDryBulbAndEnthalpy |  | Integrated |  | 80 |  | 30
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
1 | New |  |  | 700000 |  | 0.8 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
HotWater Pump | Boiler 1 | New |  | 1 |  | OnDemand |  | ConstantSpeed |  | 1.18 kW (33.74 W/gpm) |  | 2 |  | 112.903 | 0.9 | - | -
Baseline
Internal Load Components
Space
Space Name | Space Function | Status |  | Lighting Power Density (Simulated) (W/ft2) |  | LPD - Schedule Name
Spc |  |  |  | IntLPDReg |  | IntLtgRegSchRef:Name
(All Levels - Core Zones) | Office (Greater than 250 square feet in floor area) | New |  | 0.75 |  | OfficeLights
(All Levels - South Zones - Zone 1) | Office (Greater than 250 square feet in floor area) | New |  | 0.75 |  | OfficeLights
(All Levels - All other Zones) | Office (Greater than 250 square feet in floor area) | Existing |  | 1.2 |  | OfficeLights
HVAC Systems
Thermal Zone - Floor/Zone | AirSystem - Name | Status |  | Relevant Position |  | Type |  | Availability Schedule |  | Design Suppy Air Temperature (Cooling) (DegF) |  | Design Suppy Air Temperature (Heating) (DegF) |  | Outside Air Control - Control Type | SAT Reset Control (High) |  | SAT Reset Control (Low)
AirSys:CtrlZnRef | AirSys |  |  |  |  | AirSys:Type |  | AirSys:AvailSchRef |  | AirSys:ClgDsgnSupAirTemp |  | AirSys:HtgDsgnSupAirTemp |  | OACtrl:EconoCtrlMthd
Bottom Floor | BaseAirSys5 | New |  | Bottom Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset | 60 |  | 55
Mid Floor | BaseAirSys5-2 | New |  | Mid Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset | 60 |  | 55
Top Floor | BaseAirSys5-3 | New |  | Top Floor - All Zones |  | PVAV |  | OfficeHVACAvail |  | 55 |  | 60 |  | WarmestReset | 60 |  | 55
AirSystem - Name | Cooling Coil - Name | Status |  | Type |  | Cooling Efficiency (EER) |  | System Oversizing factor |  | Direct Expansion Cooling Efficiency Temperature Adjustment Curve |  | Direct Expansion Part-Load Efficiency Adjustment Curve |  | Cooling efficiency as a function of indoor coil coil flow
CoilClg:SysServed | CoilClg |  |  | CoilClg:Type |  | CoilClg:DXEER |  | CoilClg: |  | (DXEIR_fTempCrvRef) |  | (DXEIR_fPLFCrvRef) |  | (DXEIR_fFlowCrvRef)
BaseAirSys5 | BaseSys5 CoilClg | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-2 | BaseSys5 CoilClg-2 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
BaseAirSys5-3 | BaseSys5 CoilClg-3 | New |  | DirectExpansion |  | 9.8 |  | 1.15 |  | CoilClgDXEIRRatio_fTwbToadbSI |  | CoilClgDXEIRRatio_fQFrac |  | CoilClgDXDblEIRRatio_fCFMRatio
AirSystem - Name | Heating Coil - Name | Status |  | Type / Fuel Source
CoilHtg:SysServed | CoilHtg: |  |  | CoilHtg:Type
BaseSys5 CoilHtg | BaseSys5 CoilHtg | New |  | HotWater
BaseSys5 CoilHtg-2 | BaseSys5 CoilHtg-2 | New |  | HotWater
BaseSys5 CoilHtg-3 | BaseSys5 CoilHtg-3 | New |  | HotWater
BaseAirSys5/5-2/5-3 | (All BaseVAVReheatCoils) | New |  | HotWater
AirSystem - Name | Fans - Name | Status |  | Control Method |  | Modeling Method |  | Capacity (Maximum) (Cfm) |  | Brake Horse Power |  | Overall Fan Efficiency |  | Total Static (in H2O) | Name Plate Horse Power |  | Motor Efficiency
CoilHtg:SysServed | Fan: |  |  | Fan:CtrlMthd |  | Fan:ModelingMthd |  |  |  | Fan:MtrBHP |  | Fan:OverallEff |  | Fan:TotStaticPress | Fan:MtrHP |  | Fan:MtrEff
BaseAirSys5 | BaseSys5 Fan | New |  | VariableSpeedDrive |  | Static Pressure |  | 16216.5 |  | 16.4682 |  | 0.62 |  | 4 | 20 |  | 0.93
BaseAirSys5-2 | BaseSys5 Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 18085 |  | 18.3657 |  | 0.62 |  | 4 | 20 |  | 0.93
BaseAirSys5-3 | BaseSys5 Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 20819.8 |  | 21.143 |  | 0.62 |  | 4 | 25 |  | 0.936
BaseAirSys5 | BaseRelief Fan | New |  | VariableSpeedDrive |  | StaticPressure |  | 15322.7 |  | 4.8238 |  | 0.5 |  | 1 | 5 |  | 0.895
BaseAirSys5-2 | BaseRelief Fan-2 | New |  | VariableSpeedDrive |  | Static Pressure |  | 17191.2 |  | 5.412 |  | 0.5 |  | 1 | 7.5 |  | 0.917
BaseAirSys5-3 | BaseRelief Fan-3 | New |  | VariableSpeedDrive |  | Static Pressure |  | 19926 |  | 6.2729 |  | 0.5 |  | 1 | 7.5 |  | 0.917
AirSystem - Name |  | Status |  | Economizer Control |  | Economizer Integration |  | HI DB Lockout |  | High Enthalpy Lockout
CoilHtg:SysServed |  |  |  | OACtrl:EconoCtrlMthd |  | OACtrl:EconoIntegration |  | OACtrl:EconoHiTempLockout |  | OACtrl:EconoHiEnthLockout
BaseAirSys5 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-2 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
BaseAirSys5-3 |  | New |  | DifferentialDryBulb |  | Integrated | - | - | - | -
Thermal Zone - Name | Conditioning Type |  |  | Cooling Thermostat Setpoint |  | Heating Thermostat Setpoint
ThrmlZn | ThrmlZn:Type |  |  | ThrmlZn:ClgTstatSchRef |  | ThrmlZn:HtgTstatSchRef
(All Zones) | Conditioned |  |  | OfficeClgSetpt |  | OfficeHtgSetpt
(All Plenum) | Plenum |  | - | - | - | -
Boiler Components
Number of boilers | Status |  |  | Boiler Capacity (Btu/h) |  | Boiler Efficiency |  | Boiler Type |  | Boiler performance curve |  | Boiler Min Unloading Ratio
|  |  |  | Blr:CapRtd |  | Blr:ThrmlEff |  | Blr:Type |  | (HIR_fPLRCrvRef) |  | Blr:UnldRatMin
2 | New |  |  | 240522 |  | 0.8225 |  | Hot Water |  | BlrHWBlrFIRRatio_fQRatioSI |  | 0.25
Pump - Name | Serving Equipment | Status |  | Number of Pumps |  | Operation Control Type |  | Speed Control Type |  | Pump Power kW (W/gpm) |  | Total Pump HP |  | Head (ft. H20) | Pump Motor Efficiency |  | Pump Power Part-load Curve
[6 empty] | Pump:OperCtrl |  | Pump:SpdCtrl |  | Pump:Pwr |  | Pump:MtrHP |  | Pump:TotHd | Pump:MtrEff |  | (Pwr_fPLRCrvRef)
Base HW Pump/ Base HW Pump-2 | Base Blr/ Base Blr-2 | New |  | 2 |  | OnDemand |  | ConstantSpeed |  | 0.23 (19 W/gpm) |  | 0.5 |  | 60.39 | 0.855 | - | -
Note on I52: Sandeep: 150331: Check Parameter added
Note on L52: Sandeep: 150331: Check Parameter added
Note on H112: Sandeep: 150330: PREVIOUSLY 'UNDEFINED'
Note on I117: Sandeep: 150331: Check Parameter added
Note on L117: Sandeep: 150331: Check Parameter added
Note on F133: Sandeep: 150330: REDUCED SLIGHTLY FROM 240607 TO 240522