## Prototype Model
Prototype Name | I | II | III | IV | IV |  |  | VIII
Prototype Description | Small Office Building (02000CZ-OffSml) | Medium Office Building ((0300CZ-OffMed)) | Large Office Building (0400CZ-OffLrg) | Stand-alone Retail (0500CZ-RetlMed) | Stand-alone Retail DuctLoss Baseline | Strip Mall-PSZ System (1000CZ-RetlStrp) | Strip Mall-PTAC System (1000CZ-RetlStrp) | Strip Mall- Fan Coil System (1000CZ-RetlStrp)
Vintage | New Construction | New Construction | New Construction | New Construction | Same as Stand-alone Retail | New Construction | New Construction | New Construction
Location | CZ-6/15/16 | CZ-6/15/16 | CZ-1/7/6/15/16 | CZ-1/6/7/15/16 |  | CZ-6/15/16 | CZ-6/15/16 | CZ-6/15/16
Fuel Type | gas, electricity | gas, electricity | gas, electricity | gas, electricity |  | gas, electricity | Same as Strip Mall- PSZ System | Same as Strip Mall- PSZ System
Total Floor Area (sq feet) | 5500 (90.8 ft x 60.5ft) | 53600 (163.8 ft x 109.2 ft) | 498,600 (240 ft x 160 ft) | 24695 (178 ft x 139 ft) |  | 22,500 ft² (300 ft x 75 ft)
Building shape
Aspect Ratio | 1.5 | 1.5 | 1.5 | 1.28 |  | 4
Number of Floors | 1 | 3 | 13 (Including basement) | 1 |  | 1
Window Fraction (Window-to-Wall Ratio) | 24.4% for South and 19.8% for the other three orientations (Window Dimensions: 6.0 ft x 5.0 ft punch windows for all façades) | 33% (Window Dimensions: 163.8 ft x 4.29 ft on the long side of facade 109.2 ft x 4.29 ft on the short side of the façade) | 40% of above-grade gross walls 37.5% of gross walls (including the below-grade walls) | 7.1% (Window Dimensions: 82.136 ft x 5 ft, 9.843 ft x 8.563 ft and 82.136 ft x 5 on the street facing facade) |  | 10.5% (Window Dimensions: 24 windows, 7 ft x 5 ft each and 12 doors, 6 ft x 7 ft each, on the street facing façade with south WWR 26%)
Window Locations | evenly distributed along four façades | evenly distributed along four façades | evenly distributed along four façades | Windows only on the street facing façade (25.4% WWR) |  | Windows only on the street facing façade
Shading Geometry | none | none | none | none |  | none
Azimuth | non-directional | non-directional | non-directional | non-directional |  | non-directional
Thermal Zoning | Perimeter zone depth: 16.4 ft. Four perimeter zones, one core zone and an attic zone. Percentages of floor area: Perimeter 70%, Core 30% | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 40%, Core 60% | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 33%, Core 67% | Five thermal zones Refer StandAloneRetailArea for details |  | 10 thermal zones (from left to right): LGStore1 (Type 1), SMStore1 (Type 1), SMStore2 (Type 2), SMStore3 (Type 3), SMStore4 (Type 2), LGStore2 (Type 3), SMStore5 (Type 3), SMStore6 (Type 3), SMStore7 (Type 3), and SMStore8 (Type 3). Refer StripMallArea for details
Floor to floor height (feet) | 10 | 13 | 13, Basement - 8 | 20 |  | 17
Floor to ceiling height (feet) | 10 | 9 (4 ft above-ceiling plenum) | 9 | 20 (Core retail, Front Entry) 15 (Point of Sale, Front Retail, Back Space) |  | 17
Glazing sill height (feet) | 3 (top of the window is 8 ft high with 5 ft high glass) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass) | 3 ft | 3.74 ft (top of the window is 8.73 ft high with 5 ft high glass) |  | 3.0 ft (top of the window is 8 ft high)
Exterior walls
Construction | Wood-Frame Walls | NACM Metal Framed Wall | NACM Metal Framed Wall | NACM Metal Framed Wall |  | NACM Metal Framed Wall
Construction Assembly Layers | Refer T24NRWallWood | Refer NACM MetalFrameWall | Refer NACM MetalFrameWall | Refer NACM MetalFrameWall |  | Refer NACM MetalFrameWall
Refer NACMBasementWall
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Refer T24NRWallWood for respective CZ U value | 0.053 | 0.053 | 0.053 |  | 0.053
Dimensions | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio
Tilts and orientations | Vertical | Vertical | Vertical | Vertical | Vertical
Roof
Construction | Attic Roof with wood joist | NACM Roof | NACM Roof | NACM Roof | NACM Roof. Note: For duct loss baseline, the insulation layer is modelled at the drop ceiling. See details below | NACM Roof
Construction Assembly Layers | Refer NACM_AtticRfWood | Refer NACM Roof | Refer NACM Roof | Refer NACM Roof (In addition to layer described above Roof has 1/2 in Gypboard on the interior) | Refer T24NRRoofInsAboveDeck | Refer NACM Roof
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Refer NACM_AtticRfWood for respective CZ U value | 0.065 | 0.065 | 0.063 | Refer T24NRRoofInsAboveDeck | 0.065
Aged Solar Reflectance Aged Thermal Emittance | 0.2 0.85 | 0.40 0.75 | 0.40 0.75 | 0.40 0.75 |  | 0.40 0.75
Dimensions | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio | Based on floor area and aspect ratio
Tilts and orientations | Hipped roof: 10.76 ft attic ridge height, 2 ft overhang-soffit | Horizontal | Horizontal | Horizontal | Horizontal | Horizontal
Window |  |  |  |  | Same as Stand-alone Retail
Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio | based on window fraction, location, glazing sill height, floor area and aspect ratio | based on window fraction, location, glazing sill height, floor area and aspect ratio | based on window fraction, location, glazing sill height, floor area and aspect ratio |  | based on window fraction, location, glazing sill height, floor area and aspect ratio
Glass-Type and frame | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. | Fixed vertical window with U-value and SHGC as specified. |  | Fixed vertical window with U-value and SHGC as specified.
U-factor (Btu / h * ft2 * °F) | 0.36 | 0.36 | 0.36 | 0.36 |  | 0.36
SHGC | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.25
Visible transmittance | 0.42 | 0.42 | 0.42 | 0.42 |  | 0.42
Operable area | 0 | 0 | 0 | 0 |  | 0
Skylight | NA | NA | NA
Dimensions |  |  |  | Skylight to Roof Ratio- 2.07 % Core Retail, Refer Skylight Layout for details |  | Skylight to Roof Ratio- 0.85 %
Glass-Type and frame |  |  |  | Glass, curb mounted skylight with U-value and SHGC as specified. |  | Glass, curb mounted skylight with U-value and SHGC as specified.
U-factor (Btu / h * ft2 * °F) |  |  |  | 0.58 |  | 0.58
SHGC |  |  |  | 0.25 |  | 0.25
Visible transmittance |  |  |  | 0.49 |  | 0.49
Foundation
Foundation Type | NACM Slab Floor F-factor method | NACM Slab Floor F-factor method | NACM Slab Floor F-factor method | NACM Slab Floor F-factor method |  | NACM Slab Floor F-factor method
Construction | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation | Unheated Slab on Grade | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation |  | Unheated Slab on Grade with 12 in Horizontal R-5 Insulation
Construction Assembly Layers | NACM Floor Slab | NACM Floor Slab | NACM Floor Slab | NACM Floor Slab |  | NACM Floor Slab
Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | F factor= 0.72 | F factor= 0.72 | F factor= 0.730 | F factor= 0.72 |  | F factor= 0.72
Thermal properties for basement walls | NA | NA | Refer NACMBasementWall for detailed description | NA |  | NA
Dimensions | Based on floor area and aspect ratio. | Based on floor area and aspect ratio. | Based on floor area and aspect ratio. | Based on floor area and aspect ratio. |  | Based on floor area and aspect ratio.
Interior Surfaces
Construction | 2x4 uninsulated Stud Wall | 2x4 uninsulated Stud Wall for Interior Walls, 100mm NW Concrete floor with carpet for interior floor slabs & 3/4 in Acoustic celing tile for Drop ceiling | 2x4 uninsulated Stud Wall for Interior Walls, 100mm NW Concrete floor with carpet for interior floor slabs & 3/4 in Acoustic celing tile for Drop ceiling | 2x4 uninsulated Stud Wall for Interior Walls & 3/4 in Acoustic celing tile for Drop ceiling | 2x4 uninsulated Stud Wall for Interior Walls & 3/4 in Acoustic celing tile for Drop ceiling. Note: For duct loss baseline the drop ceiling is modelled with a layer of insulation. See details below | 2x4 uninsulated Stud Wall for Interior Walls
Construction Assembly Layers | NACM Interior wall Drop Ceiling | NACM Interior wall NACM Interior Floor slab Drop Ceiling | NACM Interior wall NACM Interior Floor slab Drop Ceiling | NACM Interior wall Drop Ceiling | NACM Interior wall Drop Ceiling2 | NACM Interior wall
Dimensions | Based on floor area and floor to floor height | Based on floor area and floor to floor height | Based on floor area and floor to floor height | Based on floor area and floor to floor height | Based on floor area and floor to floor height | Based on floor area and floor to floor height
Internal Mass | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²) | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Peak: 0.2318 cfm/sf of exterior wall surface area for BackSpace Plenum, Point of Sale Plenum and Front Retail Plenum (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) | Peak: 0.0448 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on)
HVAC System Type |  |  |  |  | Same as Stand-alone Retail
System Type | Packaged single zone air conditioning unit | Packaged VAV with hot-water reheat with one system per floor serving all zones in the floor | VAV with hot-water reheat with one system per floor serving all zones in the floor | Idirectly Conditioned Front_entry, Packaged single zone air conditioning unit for other zones. |  | Packaged single zone (One PSZ per zone) | Packaged Terminal Air Conditioner (One PTAC per zone) | 4 pipe fan coil system (One FPFC per zone with central boiler and chiller)
Heating type | Gas furnace inside the packaged air conditioning unit | Gas furnace inside the packaged air conditioning unit | Gas condensing boiler | Gas furnace inside the packaged air conditioning unit for back_space, core_retail, point_of_sale, and front_retail. Unconditioned for front_entry. |  | Gas furnace | Electric heating | Heating hot water
Cooling type | Packaged air conditioning unit | Packaged air conditioning unit | Water cooled Centrifugal chillers (2) | Packaged air conditioning unit for back_space, core_retail, point_of_sale, and front_retail. No cooling for front_entry. |  | Single speed DX cooling | Single speed DX cooling | Chilled water system
Distribution and terminal units | Single zone constant air volume distribution. | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. Zone control type: minimum supply air at 25% of the zone maximum air flow rate. | VAV terminal box with damper and hot-water reheating coil with Dual maximum control logic. Zone control type: minimum supply air at 30% of the zone maximum air flow rate. | Constant air volume air distribution 4 single-zone roof top units serving thermal zones back_space, point_of_sale, core_retail, and front_retail. |  | Single zone Constant air volume distribution | Constant Air Volume distribution | 4 pipe fan coil unit
HVAC Sizing
Cooling | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues |  | Refer SizingValues | Refer SizingValues | Refer SizingValues
Heating | Refer SizingValues | Refer SizingValues | Refer SizingValues | Refer SizingValues |  | Refer SizingValues | Refer SizingValues | Refer SizingValues
HVAC Efficiency
Cooling | EER-11 (COP- 3.8445) | EER-11.00 / COP-3.23 (Bottom VAV, Mid and Top VAV). Note: EER, COP includes fan heat | COP: 5.96 (0.590 kw/ton, 0.4 IPLV) | EER-11.20 / COP-3.28 (back_space, point_of_sale, core_retail, and front_retail). Indirect Heating and Cooling for front_entry) Note: EER, COP includes fan heat |  | EER-11.20 / COP-3.28 Note: EER, COP includes fan heat | EER-11.20 / COP-3.28 Note: EER, COP includes fan heat | Chiller COP-6.1
Heating | 82% | 80% | 80% | 82% |  | 82% | 80% | 80%
HVAC Control
Thermostat Setpoint | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating |  | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating | 75°F Cooling/70°F Heating
Thermostat Setback | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating |  | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating | 85°F Cooling/60°F Heating
| Small Office Building Schedule for Heating/Cooling setpoint Schedule | Medium Office Building Schedule for Heating/Cooling setpoint Schedule | Large Office Building Schedule for Heating/Cooling setpoint Schedule | Stand-alone Retail Schedule for Heating/Cooling setpoint Schedule AssemblySchedule for Back Space, Front Entry Retail Schedule for Front Retail, Core Retail & Point of Sale |  | Strip mall Schedule for Heating/Cooling setpoint Schedule | Strip mall Schedule for Heating/Cooling setpoint Schedule | Strip mall Schedule for Heating/Cooling setpoint Schedule
Design Supply air temperature | Maximum 95F, Minimum 55F | Maximum 95F, Minimum 55F Reheat coil max reheat temp 95F | Maximum 95F, Minimum 55F Reheat coil max reheat temp 95F | Minimum 55F Reheat coil max reheat temp 95F |  | Maximum 104°F, Minimum 57.2°F | Maximum 104°F, Minimum 57.2°F | Maximum 122°F, Minimum 55°F
Supply air temperature reset | NA | SAT reset by warmest zone airflow first (Reset Supply high: 60 F, reset supply low: 55F) | SAT reset by warmest zone airflow first (Reset Supply high: 60 F, reset supply low: 55F) | No SAT Control |  | No SAT Control | No SAT Control | No SAT Control
Chilled water supply temperatures | NA | NA | 44°F | NA |  | NA | NA | 44°F
Chilled water return temperatures | NA | NA | 64°F | NA |  | NA | NA
Chilled water supply temperature reset | NA | NA | Fixed | NA |  | NA | NA | Reset (44°F-54°F ) based on outdoor air temperature
Condenser Type | NA | NA | Water-cooled, no reset | NA |  | NA | NA | Water cooled, no reset
Hot water supply temperatures | NA | 180°F | 180°F | NA |  | NA | NA | 180°F
Hot water supply temperature reset | NA | None | Fixed | NA |  | NA | NA | Reset (150°F-180°F ) based on outdoor air temperature
Economizers | No economizer | Differential Dry bulb economizer (Integrated), 80 F High DB lockout | Differential Dry bulb economizer (Integrated), 80 F High DB lockout | Differential Dry bulb economizer (Integrated) |  | Differential Dry bulb economizer (Integrated) | No economizer | No economizer
Ventilation | 0.15 cfm/ft2 | 0.15 cfm/ft2 | 0.15 cfm/ft2 | Point of Sale & Core and Front Retail -0.2 cfm/ft2; Backspace, Front Entry-0.15 cfm/ft2 |  | Max of 15 cfm/person or 0.20 cfm/ft2 | Max of 15 cfm/person or 0.20 cfm/ft2 | Max of 15 cfm/person or 0.20 cfm/ft2
Supply Fan
Fan type | CAV | Variable Volume | Constant volume for Basement, Variable Volume for all others | Constant Volume for all Conditioned zones |  | OnOff | OnOff | OnOff
Fan schedules | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule AssemblySchedule for Back Space, Front Entry Retail Schedule for Front Retail, Core Retail & Point of Sale |  | Strip mall Schedule | Strip mall Schedule | Strip mall Schedule
Supply Fan Total Efficiency (%) | 55% | 60% Bottom VAV, 62% -Mid and Top VAV | 65% (for all VAV fans) | 56.25% (all fans) |  | 60% | 60% | 60%
Fan Motor Efficiency | 85.5% | 92.4% | 94% (for VAV fans), Nameplate HP: 30 | 86.5% (all fans) |  | 86.5% | 86.5% | 86.5%
Supply Fan Pressure Rise | 2.5 ftinH2O | 4.08 in H20 | 5inH2O | 2.5in H2O (all fans) |  | 2.50 inH2O | 2.50 inH2O | 2.50 inH2O
Pump
Pump Type | NA | HW: Constant Speed variable flow | HW: Constant Speed variable flow, Cooling Tower:Constant Speed, CHW: Constant PrimaryVariable Secondary (constant flow to chillers with bypass, variable flow to coils) | NA |  | NA | NA | Variable speed pumps for condenser water, chilled water and heating hot water systems
Rated Pump Head | NA | HW: 50 ft H20 | HW: 50 ft H20 Cooling Tower: 60 ft H20 CHW Primary: 60 ft H20 CHW Secondary: 75 ft H20 | NA |  | NA | NA | HW- 63.5 ftH2O CHW- 30.0 ftH2O CW- 20.0 ftH2O
Pump Motor Power per Unit Flow |  | HW: 19 W/gpm | HW: 15 W/gpm, CW: 17.4 W/gpm, ChW Primary: 17.5 W/gpm, ChW Secondary: 21.8 | NA |  |  |  | Hw: 19 W/gpm
Pump Efficiency | NA | Motor efficiency- HW: 0.9 Total efficiency- HW:63% | Motor efficiency-HW: 0.9, Cooling Tower:0.930, CHW Primary, Secondary:0.924 | NA |  | NA | NA | Motor efficiency: 0.9
Cooling Tower
Cooling Tower Type | NA | NA | open cooling tower with variable speed fan | NA |  | NA | NA | open cooling tower with two speed fan
Tower range | NA | NA | 10F (Design CW supply temp. 85F, CW return temp 95F) | NA |  | NA | NA | 10F (Design CW supply temp. 85F, CW return temp 95F)
Tower Approach | NA | NA | 7F (Tower leaving temp 85F and wet-bulb 78F) |  |  | NA | NA | 7F (Tower leaving temp 85F and wet-bulb 78F)
Design Flow rate |  | NA | 3 gpm/Nominal Capacity |  |  |  |  | 3 gpm/Nominal Capacity
Cooling Tower Efficiency | NA | NA | 60 gpm/hp | NA |  | NA | NA | 48.5 gpm/hp (high speed) 303 gpm/hp (low speed)
Service Water Heating
SWH type | Storage Tank | Storage Tank | Storage Tank | Tank |  | Tank | Same as Strip Mall- PSZ System | Same as Strip Mall- PSZ System
Fuel type | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | Natural Gas
Thermal efficiency (%) | 80% | 80% | 80% | 80% |  | 80%
Peak Use Flow rate Schedule | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | Stand-alone Retail Schedule
Water temperature setpoint | 120°F | 120°F | 180°F | 135°F |  | 135°F
Water temperature setpoint Schedule | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | Stand-alone Retail Schedule
Water Heater Max Capacity (Btuh) | 6655 Btuh | 64355.46 Btuh | 250,000 Btuh | 40000 Btuh |  | 40000 Btuh
Water consumption | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | Stand-alone Retail Schedule
Lighting Load
Lighting power density (W/ft2) | 0.75 W/ft2 | 0.75 W/ft2 | 0.75 W/ft2 | Point of sale, Retail-1.2 W/ft2,, Lobby-1.5 W/ft2, Backspace-0.6 W/ft2 |  | 1.2 W/ft2
Schedule | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | Strip mall Schedule
Daylighting Controls | NA | Continuous dimming in Primary Daylit zone in Perimeter zones | Continuous dimming in Primary and Secondary Daylit zone in Perimeter zones | Continuous Dimming in Skylit area in Core Retail and in Primary Daylit in Front Entry, Front Retail, Point of Sale |  | Continuous Dimming in Skylit and Primary Daylit area in all zones.
Plug load
Electric power density (W/ft2) | 1.34 W/ft2 | 1.5 W/ft2 | 1.5 W/ft2 | Point of sale, Retail-1.0 W/ft2, Backspace-0.2 W/ft2 |  | 0.5 W/ft2
Schedule | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | Strip mall Schedule
Occupancy
Average people | 100- ft2/person | 100 ft2/person | 100 ft2/person | Point of sale, Retail - 30 ft2/person, Back Space- 333 ft2/person, Front Entry - 100 ft2/person |  | 30 ft2/person
Schedule | Small Office Building Schedule | Medium Office Building Schedule | Large Office Building Schedule | Stand-alone Retail Schedule |  | Strip mall Schedule
Elevator
Quantity | NA | NA | NA | NA |  | NA
Motor type
Peak Motor Power (W/elevator)
Heat Gain to Building
Peak Fan/lights Power (W/elevator)
Motor and fan/lights Schedules
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail
Note on F28: Nambiar, Chitra AEC: Not been updated

## Results (hidden)
| TEST RESULTS |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  |  | 16
| Test Case |  | Annual TDV EUI |  | Annual TDV EUI- Electricity |  | Annual TDV EUI- Natural Gas |  | Annual Total End Use Site Energy EUI |  | Annual End Use Site Energy EUI | [17 empty] | Variation from Baseline |  |  |  |  | Reference Model Occupied Unmet Load Hrs | Applicant Model Occupied Unmet Load Hrs
|  |  | (kBtu/sqft) |  | (kwh/sqft) |  | (therm/sqft) |  | (kBtu/sqft) |  | Heating (kBtu/sqft) |  | Cooling (kBtu/sqft) |  | Interior Lighting (kBtu/sqft) |  | Interior Equipment (kBtu/sqft) |  | Exterior Lighting (kBtu/sqft) |  | Fans (kBtu/sqft) |  | Pumps (kBtu/sqft) |  | Refrigeration (kBtu/sqft) |  | Water Heating (kBtu/sqft) |  | TDV % variation |  | Total End Use Site Energy % Variation
|  |  | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Pass/Fail
3 |  | Medium Office CZ-15 Baseline | 294.5639 |  | 10.3283 |  | 0.15484 |  | 50.722 |  | 0.35207 |  | 14.9552 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1483 |  | 0.12814 |  | 0 |  | 15.1282 | [6 empty] | 677.25
4 | 1 | Envelope Test Medium OfficeCZ-15 Roof Insulation | 293.7428 |  | 10.3019 |  | 0.15472 |  | 50.6193 |  | 0.33952 |  | 14.8696 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1449 |  | 0.12708 |  | 0 |  | 15.1282 |  | 0.2788% |  | 0.2024% |  | PASS | 674.5
5 | 2 | Envelope Test Medium OfficeCZ-15 Wall Insulation | 293.4568 |  | 10.2961 |  | 0.15467 |  | 50.5944 |  | 0.33475 |  | 14.8596 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.137 |  | 0.12513 |  | 0 |  | 15.1282 |  | 0.3758% |  | 0.2516% |  | PASS | 676.75
6 | 3 | Envelope Test Medium OfficeCZ-15 Floor Slab Insulation | 295.5473 |  | 10.364 |  | 0.15471 |  | 50.8303 |  | 0.33899 |  | 15.0632 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1674 |  | 0.12266 |  | 0 |  | 15.1282 |  | -0.3338% |  | -0.2136% |  | PASS | 673.5
7 | 4 | Envelope Test Medium OfficeCZ-15 Infiltration | 295.0579 |  | 10.3399 |  | 0.15499 |  | 50.7763 |  | 0.36673 |  | 14.9888 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1511 |  | 0.13132 |  | 0 |  | 15.1282 |  | -0.1677% |  | -0.107% |  | PASS | 676
8 |  | Medium Office CZ-16 Baseline | 207.5921 |  | 6.8524 |  | 0.2365 |  | 47.0258 |  | 8.5162 |  | 3.307 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4761 |  | 0.58519 |  | 0 |  | 15.1282 | [6 empty] | 822.5
9 | 5 | Envelope Test Medium OfficeCZ-16 Roof Insulation | 206.9981 |  | 6.8445 |  | 0.23479 |  | 46.8277 |  | 8.3451 |  | 3.2893 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4728 |  | 0.57918 |  | 0 |  | 15.1282 |  | 0.2861% |  | 0.4213% |  | PASS | 822.25
10 | 6 | Envelope Test Medium OfficeCZ-16 Wall Insulation | 206.9608 |  | 6.8463 |  | 0.23417 |  | 46.7715 |  | 8.2827 |  | 3.2974 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4735 |  | 0.57635 |  | 0 |  | 15.1282 |  | 0.3041% |  | 0.5408% |  | PASS | 821
11 | 7 | Envelope Test Medium OfficeCZ-16 Floor Slab Insulation | 207.7464 |  | 6.8598 |  | 0.23577 |  | 46.9781 |  | 8.4432 |  | 3.3305 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4873 |  | 0.57582 |  | 0 |  | 15.1282 |  | -0.07433% |  | 0.1015% |  | PASS | 816.75
12 | 8 | Envelope Test Medium OfficeCZ-16 Infiltration | 208.1379 |  | 6.8567 |  | 0.23908 |  | 47.2984 |  | 8.7742 |  | 3.3052 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4772 |  | 0.60038 |  | 0 |  | 15.1282 |  | -0.2629% |  | -0.5795% |  | PASS | 817
13 |  | Medium Office CZ-6 Baseline | 209.3173 |  | 7.505 |  | 0.15807 |  | 41.4112 |  | 0.67479 |  | 6.1474 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2533 |  | 0.19441 |  | 0 |  | 15.1282 | [6 empty] | 245.75
14 | 9 | Envelope Test Medium OfficeCZ-6 Roof Insulation | 208.827 |  | 7.4944 |  | 0.15765 |  | 41.3331 |  | 0.6329 |  | 6.1148 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2522 |  | 0.19176 |  | 0 |  | 15.1282 |  | 0.2342% |  | 0.1886% |  | PASS | 246.75
15 | 10 | Envelope Test Medium OfficeCZ-6 Wall Insulation | 209.0477 |  | 7.5014 |  | 0.15761 |  | 41.3534 |  | 0.62919 |  | 6.1396 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2552 |  | 0.18787 |  | 0 |  | 15.1282 |  | 0.1288% |  | 0.1396% |  | PASS | 246.5
16 | 11 | Envelope Test Medium OfficeCZ-6 Floor Slab Insulation | 209.6939 |  | 7.5167 |  | 0.15792 |  | 41.4356 |  | 0.65959 |  | 6.1887 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.263 |  | 0.1831 |  | 0 |  | 15.1282 |  | -0.1799% |  | -0.0589% |  | PASS | 231.25
17 | 12 | Envelope Test Medium OfficeCZ-6 Infiltration | 209.3185 |  | 7.5029 |  | 0.15831 |  | 41.428 |  | 0.69883 |  | 6.1383 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2506 |  | 0.19866 |  | 0 |  | 15.1282 |  | -0.0005911% |  | -0.04055% |  | PASS | 250.75
18 |  | Small Office CZ-15 SolarReflectance-Low Slope Baseline | 224.9749 |  | 8.7755 |  | 0.037977 |  | 33.7399 |  | 0.82687 |  | 8.9009 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9466 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 146.33
19 | 13 | Envelope Test Small OfficeCZ-15 SolarReflectance-Low Slope | 223.4125 |  | 8.7204 |  | 0.038097 |  | 33.5642 |  | 0.83893 |  | 8.7511 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9104 |  | 0 |  | 0 |  | 2.9699 |  | 0.6945% |  | 0.5208% |  | PASS | 147.33
20 |  | Small Office CZ-16 SolarReflectance-Low Slope Baseline | 227.8293 |  | 8.8658 |  | 0.038321 |  | 34.0827 |  | 0.86133 |  | 9.1456 |  | 6.1447 |  | 12.9509 |  | 0 |  | 2.0086 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 152.67
21 | 14 | Envelope Test Small OfficeCZ-16 SolarReflectance-Low Slope | 225.5537 |  | 8.7856 |  | 0.038511 |  | 33.8277 |  | 0.88028 |  | 8.9268 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9535 |  | 0 |  | 0 |  | 2.9699 |  | 0.9988% |  | 0.748% |  | PASS | 146.83
22 |  | Small Office CZ-6 SolarReflectance-Low Slope Baseline | 185.13 |  | 7.3356 |  | 0.051434 |  | 30.1722 |  | 2.1723 |  | 4.534 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.3936 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 78.83
23 | 15 | Envelope Test Small OfficeCZ-6 SolarReflectance-Low Slope | 183.2247 |  | 7.269 |  | 0.051951 |  | 29.9965 |  | 2.2222 |  | 4.36 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.3419 |  | 0 |  | 0 |  | 2.9699 |  | 1.029% |  | 0.5824% |  | FAIL | 80.67
24 |  | Small Office CZ-15 SolarReflectance-Steep Slope Baseline | 189.5434 |  | 7.4684 |  | 0.052589 |  | 30.7407 |  | 2.286 |  | 4.8699 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.5108 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 82.16
25 | 16 | Envelope Test Small OfficeCZ-15 SolarReflectance-Steep Slope | 186.6769 |  | 7.3669 |  | 0.053329 |  | 30.4685 |  | 2.3618 |  | 4.6064 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.4298 |  | 0 |  | 0 |  | 2.9699 |  | 1.512% |  | 0.8854% |  | FAIL | 82.17
26 |  | Small Office CZ-16 SolarReflectance-Steep Slope Baseline | 181.6485 |  | 6.8787 |  | 0.10673 |  | 34.1412 |  | 7.7003 |  | 3.0405 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3385 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 163.16
27 | 17 | Envelope Test Small OfficeCZ-16 SolarReflectance-Steep Slope | 180.8061 |  | 6.8444 |  | 0.1078 |  | 34.1309 |  | 7.8071 |  | 2.9526 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3092 |  | 0 |  | 0 |  | 2.9699 |  | 0.4637% |  | 0.03027% |  | PASS | 160.5
28 |  | Small Office CZ-6 SolarReflectance-Steep Slope Baseline | 183.8604 |  | 6.9448 |  | 0.1075 |  | 34.4444 |  | 7.7778 |  | 3.2007 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.4057 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 161.34
29 | 18 | Envelope Test Small OfficeCZ-6 SolarReflectance-Steep Slope | 182.6063 |  | 6.8934 |  | 0.109 |  | 34.4186 |  | 7.9276 |  | 3.0698 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3609 |  | 0 |  | 0 |  | 2.9699 |  | 0.6821% |  | 0.07502% |  | PASS | 158.33
30 |  | Envelope Test Primary SchoolCZ-15 Light | 223.6777 |  | 8.725 |  | 0.03827 |  | 33.5969 |  | 0.85616 |  | 8.7631 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9121 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 148
31 | 19 | Envelope Test Primary SchoolCZ-15 Heavy | 223.2729 |  | 8.7179 |  | 0.038063 |  | 33.5521 |  | 0.83549 |  | 8.7338 |  | 6.1447 |  | 12.9509 |  | 0 |  | 1.9156 |  | 0 |  | 0 |  | 2.9699 |  | 0.181% |  | 0.08101% |  | PASS | 150.67
32 |  | Envelope Test Primary SchoolCZ-16 Light | 181.2833 |  | 6.8631 |  | 0.10742 |  | 34.1567 |  | 7.7692 |  | 2.9991 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3264 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 160.17
33 | 20 | Envelope Test Primary SchoolCZ-16 Heavy | 180.9009 |  | 6.8545 |  | 0.10678 |  | 34.0637 |  | 7.7054 |  | 2.9819 |  | 6.1395 |  | 12.9509 |  | 0 |  | 1.3161 |  | 0 |  | 0 |  | 2.9699 |  | 0.211% |  | 0.1251% |  | PASS | 159.34
34 |  | Envelope Test Primary SchoolCZ-6 Light | 184.4065 |  | 7.3104 |  | 0.052123 |  | 30.155 |  | 2.2412 |  | 4.4668 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.3764 |  | 0 |  | 0 |  | 2.9699 | [6 empty] | 79.84
35 | 21 | Envelope Test Primary SchoolCZ-6 Heavy | 183.8862 |  | 7.2993 |  | 0.051279 |  | 30.0327 |  | 2.1568 |  | 4.4376 |  | 6.1516 |  | 12.9509 |  | 0 |  | 1.3661 |  | 0 |  | 0 |  | 2.9699 |  | 0.2821% |  | 0.1519% |  | PASS | 79.34
36
37 |  | Medium Office CZ-15 Baseline | 294.5639 |  | 10.3283 |  | 0.15484 |  | 50.722 |  | 0.35207 |  | 14.9552 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1483 |  | 0.12814 |  | 0 |  | 15.1282 | [6 empty] | 677.25
38 | 22 | Envelope Glazing Test Medium OfficeCZ-15 Window U | 292.5652 |  | 10.2822 |  | 0.15409 |  | 50.4899 |  | 0.2773 |  | 14.812 |  | 5.059 |  | 12.9515 |  | 0 |  | 2.1493 |  | 0.11258 |  | 0 |  | 15.1282 |  | 0.6785% |  | 0.4575% |  | PASS | 684.75
39 | 23 | Envelope Glazing Test Medium OfficeCZ-15 Window SHGC | 288.5239 |  | 10.1094 |  | 0.15528 |  | 50.0184 |  | 0.39554 |  | 14.3202 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.0337 |  | 0.13061 |  | 0 |  | 15.1282 |  | 2.051% |  | 1.387% |  | FAIL | 636.25
40 | 24 | Envelope Glazing Test Medium OfficeCZ-15 Window U&SHGC | 286.4189 |  | 10.0607 |  | 0.15437 |  | 49.7614 |  | 0.30488 |  | 14.1682 |  | 5.059 |  | 12.9515 |  | 0 |  | 2.0339 |  | 0.11594 |  | 0 |  | 15.1282 |  | 2.765% |  | 1.894% |  | FAIL | 633.25
41 |  | Medium Office CZ-16 Baseline | 207.5921 |  | 6.8524 |  | 0.2365 |  | 47.0258 |  | 8.5162 |  | 3.307 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4761 |  | 0.58519 |  | 0 |  | 15.1282 | [6 empty] | 822.5
42 | 25 | Envelope Glazing Test Medium OfficeCZ-16 Window U | 206.3141 |  | 6.8619 |  | 0.22775 |  | 46.1828 |  | 7.6408 |  | 3.3457 |  | 5.0624 |  | 12.9515 |  | 0 |  | 1.4996 |  | 0.55479 |  | 0 |  | 15.1282 |  | 0.6156% |  | 1.793% |  | PASS | 813
43 | 26 | Envelope Glazing Test Medium OfficeCZ-16 Window SHGC | 204.8334 |  | 6.7642 |  | 0.23781 |  | 46.8551 |  | 8.6465 |  | 3.1028 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.3823 |  | 0.58218 |  | 0 |  | 15.1282 |  | 1.329% |  | 0.3631% |  | FAIL | 842.5
44 | 27 | Envelope Glazing Test Medium OfficeCZ-16 Window U&SHGC | 203.441 |  | 6.7717 |  | 0.22884 |  | 45.9843 |  | 7.7502 |  | 3.1396 |  | 5.0624 |  | 12.9515 |  | 0 |  | 1.4028 |  | 0.54984 |  | 0 |  | 15.1282 |  | 2% |  | 2.215% |  | FAIL | 815.5
45 |  | Medium Office CZ-6 Baseline | 209.3173 |  | 7.505 |  | 0.15807 |  | 41.4112 |  | 0.67479 |  | 6.1474 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2533 |  | 0.19441 |  | 0 |  | 15.1282 | [6 empty] | 245.75
46 | 28 | Envelope Glazing Test Medium OfficeCZ-6 Window U | 209.7913 |  | 7.5337 |  | 0.15686 |  | 41.3884 |  | 0.55408 |  | 6.2366 |  | 5.0624 |  | 12.9515 |  | 0 |  | 1.2835 |  | 0.17232 |  | 0 |  | 15.1282 |  | -0.2265% |  | 0.05506% |  | PASS | 231
47 | 29 | Envelope Glazing Test Medium OfficeCZ-6 Window SHGC | 205.8698 |  | 7.388 |  | 0.15848 |  | 41.0529 |  | 0.7158 |  | 5.8174 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.1785 |  | 0.19989 |  | 0 |  | 15.1282 |  | 1.647% |  | 0.8651% |  | FAIL | 269.5
48 | 30 | Envelope Glazing Test Medium OfficeCZ-6 Window U&SHGC | 206.2687 |  | 7.4151 |  | 0.15715 |  | 41.0124 |  | 0.58271 |  | 5.9047 |  | 5.0624 |  | 12.9515 |  | 0 |  | 1.2062 |  | 0.17692 |  | 0 |  | 15.1282 |  | 1.456% |  | 0.9628% |  | FAIL | 258.5
49 |  | Large Office CZ-7 Baseline | 209.1751 |  | 8.5106 |  | 0.051375 |  | 34.1755 |  | 0.51816 |  | 3.3156 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.5473 |  | 1.686 |  | 0 |  | 4.6184 | [6 empty] | 325.75
50 | 31 | Envelope Glazing Test Large OfficeCZ-7 WWR 20% | 206.2328 |  | 8.4296 |  | 0.050922 |  | 33.8539 |  | 0.47285 |  | 3.1662 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.5186 |  | 1.6002 |  | 0 |  | 4.6183 |  | 1.407% |  | 0.9409% |  | FAIL | 194
51 | 32 | Envelope Glazing Test Large OfficeCZ-7 WWR 60% | 211.547 |  | 8.577 |  | 0.051869 |  | 34.4516 |  | 0.56752 |  | 3.4414 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.576 |  | 1.7474 |  | 0 |  | 4.6184 |  | -1.134% |  | -0.8081% |  | FAIL | 477
52 | 33 | Envelope Glazing Test Large OfficeCZ-7 WWR 60% with South overhang | 209.8252 |  | 8.5192 |  | 0.051884 |  | 34.2558 |  | 0.56903 |  | 3.356 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.502 |  | 1.7155 |  | 0 |  | 4.6184 |  | -0.3108% |  | -0.2352% |  | PASS | 480.75
53 |  | Large Office CZ-1 Baseline | 180.2285 |  | 7.2061 |  | 0.099686 |  | 34.5543 |  | 5.3506 |  | 0.27201 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8179 |  | 0.28964 |  | 0 |  | 4.6184 | [6 empty] | 347
54 | 34 | Envelope Glazing Test Large OfficeCZ-1 WWR 20% | 179.3501 |  | 7.2122 |  | 0.095753 |  | 34.182 |  | 4.9573 |  | 0.26046 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8625 |  | 0.27777 |  | 0 |  | 4.6184 |  | 0.4874% |  | 1.077% |  | PASS | 280.75
55 | 35 | Envelope Glazing Test Large OfficeCZ-1 WWR 60% | 181.0399 |  | 7.2182 |  | 0.10192 |  | 34.8191 |  | 5.5742 |  | 0.2761 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8471 |  | 0.29753 |  | 0 |  | 4.6184 |  | -0.4502% |  | -0.7665% |  | PASS | 391
56
57 |  | Medium Office CZ-15 Baseline | 294.5639 |  | 10.3283 |  | 0.15484 |  | 50.722 |  | 0.35207 |  | 14.9552 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1483 |  | 0.12814 |  | 0 |  | 15.1282 | [6 empty] | 677.25
58 | 36 | Lighting Tests Medium OfficeCZ-15 low LPD | 285.803 |  | 9.9491 |  | 0.155 |  | 49.4433 |  | 0.36744 |  | 14.683 |  | 4.0468 |  | 12.9515 |  | 0 |  | 2.1384 |  | 0.12796 |  | 0 |  | 15.1282 |  | 2.974% |  | 2.521% |  | FAIL | 709.5
59 | 37 | Lighting Tests Medium OfficeCZ-15 high LPD | 303.4138 |  | 10.7097 |  | 0.15469 |  | 52.008 |  | 0.33687 |  | 15.232 |  | 6.0703 |  | 12.9515 |  | 0 |  | 2.1603 |  | 0.12902 |  | 0 |  | 15.1282 |  | -3.004% |  | -2.535% |  | FAIL | 646.5
60 |  | Medium Office CZ-16 Baseline | 207.5921 |  | 6.8524 |  | 0.2365 |  | 47.0258 |  | 8.5162 |  | 3.307 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4761 |  | 0.58519 |  | 0 |  | 15.1282 | [6 empty] | 822.5
61 | 38 | Lighting Tests Medium OfficeCZ-16 low LPD | 199.9267 |  | 6.5151 |  | 0.23732 |  | 45.9567 |  | 8.5982 |  | 3.2149 |  | 4.0495 |  | 12.9515 |  | 0 |  | 1.439 |  | 0.57564 |  | 0 |  | 15.1282 |  | 3.693% |  | 2.273% |  | FAIL | 845.75
62 | 39 | Lighting Tests Medium OfficeCZ-16 high LPD | 215.0636 |  | 7.1902 |  | 0.23453 |  | 47.9811 |  | 8.3186 |  | 3.3998 |  | 6.0742 |  | 12.9515 |  | 0 |  | 1.514 |  | 0.59473 |  | 0 |  | 15.1282 |  | -3.599% |  | -2.031% |  | FAIL | 806.25
63 |  | Medium Office CZ-6 Baseline | 209.3173 |  | 7.505 |  | 0.15807 |  | 41.4112 |  | 0.67479 |  | 6.1474 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2533 |  | 0.19441 |  | 0 |  | 15.1282 | [6 empty] | 245.75
64 | 40 | Lighting Tests Medium OfficeCZ-6 low LPD | 201.1365 |  | 7.1446 |  | 0.15837 |  | 40.2116 |  | 0.70519 |  | 5.9671 |  | 4.0495 |  | 12.9515 |  | 0 |  | 1.2172 |  | 0.19318 |  | 0 |  | 15.1282 |  | 3.908% |  | 2.897% |  | FAIL | 258.75
65 | 41 | Lighting Tests Medium OfficeCZ-6 high LPD | 217.58 |  | 7.8659 |  | 0.15777 |  | 42.6125 |  | 0.64492 |  | 6.3292 |  | 6.0742 |  | 12.9515 |  | 0 |  | 1.2897 |  | 0.19494 |  | 0 |  | 15.1282 |  | -3.947% |  | -2.901% |  | FAIL | 235
66
67 |  | Large Office CZ-7 Baseline | 209.1751 |  | 8.5106 |  | 0.051375 |  | 34.1755 |  | 0.51816 |  | 3.3156 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.5473 |  | 1.686 |  | 0 |  | 4.6184 | [6 empty] | 325.75
68 | 42 | Daylighting Tests Large OfficeCZ-7 Continuous Dimming | 201.666 |  | 8.1953 |  | 0.05177 |  | 33.1393 |  | 0.55762 |  | 3.2328 |  | 5.2785 |  | 15.0362 |  | 0 |  | 2.4954 |  | 1.6388 |  | 0 |  | 4.6184 |  | 3.59% |  | 3.032% |  | FAIL | 366.5
69 | 43 | Daylighting Tests Large OfficeCZ-7 Continuous Dimming and high VT | 201.7138 |  | 8.1941 |  | 0.05178 |  | 33.136 |  | 0.55861 |  | 3.2358 |  | 5.2722 |  | 15.0362 |  | 0 |  | 2.4945 |  | 1.6386 |  | 0 |  | 4.6184 |  | 3.567% |  | 3.042% |  | FAIL | 366.5
70 | 44 | Daylighting Tests Large OfficeCZ-7 Stepped Dimming | 198.9275 |  | 8.0748 |  | 0.051913 |  | 32.7425 |  | 0.57195 |  | 3.1994 |  | 4.9398 |  | 15.0362 |  | 0 |  | 2.4796 |  | 1.6186 |  | 0 |  | 4.6184 |  | 4.899% |  | 4.193% |  | FAIL | 383.75
71 | 45 | Daylighting Tests Large OfficeCZ-7 Stepped Dimming and high VT | 198.7724 |  | 8.0661 |  | 0.051941 |  | 32.7153 |  | 0.57473 |  | 3.1921 |  | 4.9209 |  | 15.0362 |  | 0 |  | 2.4766 |  | 1.6181 |  | 0 |  | 4.6184 |  | 4.973% |  | 4.273% |  | FAIL | 384.25
72 |  | Large Office CZ-7 WWR 20% Baseline | 206.2328 |  | 8.4296 |  | 0.050922 |  | 33.8539 |  | 0.47285 |  | 3.1662 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.5186 |  | 1.6002 |  | 0 |  | 4.6183 | [6 empty] | 194
73 | 46 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Continuous Dimming | 199.0772 |  | 8.1291 |  | 0.051192 |  | 32.8555 |  | 0.49983 |  | 3.0648 |  | 5.3345 |  | 15.0362 |  | 0 |  | 2.478 |  | 1.5549 |  | 0 |  | 4.6184 |  | 3.47% |  | 2.949% |  | FAIL | 215.5
74 | 47 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Continuous Dimming and high VT | 198.7609 |  | 8.1217 |  | 0.051224 |  | 32.8335 |  | 0.5031 |  | 3.0641 |  | 5.3137 |  | 15.0362 |  | 0 |  | 2.4752 |  | 1.5541 |  | 0 |  | 4.6184 |  | 3.623% |  | 3.014% |  | FAIL | 215.25
75 | 48 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Stepped Dimming | 197.1025 |  | 8.0496 |  | 0.051198 |  | 32.585 |  | 0.50044 |  | 3.0418 |  | 5.111 |  | 15.0362 |  | 0 |  | 2.4691 |  | 1.5414 |  | 0 |  | 4.6183 |  | 4.427% |  | 3.748% |  | FAIL | 225
76 | 49 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Stepped Dimming and high VT | 196.6667 |  | 8.0293 |  | 0.051252 |  | 32.521 |  | 0.50586 |  | 3.0429 |  | 5.0468 |  | 15.0362 |  | 0 |  | 2.4673 |  | 1.5373 |  | 0 |  | 4.6184 |  | 4.638% |  | 3.937% |  | FAIL | 225.25
77 |  | Large Office CZ-7 WWR 60% Baseline | 211.547 |  | 8.577 |  | 0.051869 |  | 34.4516 |  | 0.56752 |  | 3.4414 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.576 |  | 1.7474 |  | 0 |  | 4.6184 | [6 empty] | 477
78 | 50 | Daylighting Tests Large OfficeCZ-7WWR-60%,Continuous Dimming | 204.1573 |  | 8.2628 |  | 0.052228 |  | 33.4153 |  | 0.60342 |  | 3.3572 |  | 5.2811 |  | 15.0362 |  | 0 |  | 2.527 |  | 1.6997 |  | 0 |  | 4.6184 |  | 3.493% |  | 3.008% |  | FAIL | 522.5
79 | 51 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Continuous Dimming and high VT | 204.0337 |  | 8.2577 |  | 0.052237 |  | 33.3987 |  | 0.60433 |  | 3.3478 |  | 5.2742 |  | 15.0362 |  | 0 |  | 2.5259 |  | 1.6997 |  | 0 |  | 4.6184 |  | 3.552% |  | 3.056% |  | FAIL | 522.25
80 | 52 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Stepped Dimming | 201.2606 |  | 8.1389 |  | 0.052351 |  | 33.0048 |  | 0.61573 |  | 3.3061 |  | 4.9465 |  | 15.0362 |  | 0 |  | 2.5125 |  | 1.6804 |  | 0 |  | 4.6184 |  | 4.862% |  | 4.2% |  | FAIL | 536.25
81 | 53 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Stepped Dimming and high VT | 201.0881 |  | 8.1297 |  | 0.05238 |  | 32.9763 |  | 0.61866 |  | 3.2978 |  | 4.9263 |  | 15.0362 |  | 0 |  | 2.5097 |  | 1.6807 |  | 0 |  | 4.6184 |  | 4.944% |  | 4.282% |  | FAIL | 536.25
82 |  | Large Office CZ-1 Baseline | 180.2285 |  | 7.2061 |  | 0.099686 |  | 34.5543 |  | 5.3506 |  | 0.27201 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8179 |  | 0.28964 |  | 0 |  | 4.6184 | [6 empty] | 347
83 | 54 | Daylighting Tests Large OfficeCZ-1 Continuous Dimming | 174.4021 |  | 6.9223 |  | 0.10453 |  | 34.0703 |  | 5.8353 |  | 0.26158 |  | 5.2946 |  | 15.0362 |  | 0 |  | 2.7385 |  | 0.28108 |  | 0 |  | 4.6184 |  | 3.233% |  | 1.401% |  | FAIL | 354.75
84 | 55 | Daylighting Tests Large OfficeCZ-1 Continuous Dimming and high VT | 174.3376 |  | 6.9184 |  | 0.10462 |  | 34.0661 |  | 5.8443 |  | 0.26158 |  | 5.2835 |  | 15.0362 |  | 0 |  | 2.7363 |  | 0.2811 |  | 0 |  | 4.6184 |  | 3.269% |  | 1.413% |  | FAIL | 354.5
85 | 56 | Daylighting Tests Large OfficeCZ-1 Stepped Dimming | 172.3111 |  | 6.8257 |  | 0.10615 |  | 33.9026 |  | 5.9975 |  | 0.25778 |  | 4.9898 |  | 15.0362 |  | 0 |  | 2.7213 |  | 0.27711 |  | 0 |  | 4.6184 |  | 4.393% |  | 1.886% |  | FAIL | 359.25
86 | 57 | Daylighting Tests Large OfficeCZ-1 Stepped Dimming and high VT | 172.1336 |  | 6.814 |  | 0.10644 |  | 33.892 |  | 6.0267 |  | 0.25764 |  | 4.9585 |  | 15.0362 |  | 0 |  | 2.7131 |  | 0.27682 |  | 0 |  | 4.6184 |  | 4.492% |  | 1.917% |  | FAIL | 359.25
87 |  | Large Office CZ-1 WWR-20% Baseline | 179.3501 |  | 7.2122 |  | 0.095753 |  | 34.182 |  | 4.9573 |  | 0.26046 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8625 |  | 0.27777 |  | 0 |  | 4.6184 | [6 empty] | 280.75
88 | 58 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Continuous Dimming | 174.0325 |  | 6.9534 |  | 0.10063 |  | 33.7861 |  | 5.445 |  | 0.2534 |  | 5.3818 |  | 15.0362 |  | 0 |  | 2.7772 |  | 0.26969 |  | 0 |  | 4.6183 |  | 2.965% |  | 1.158% |  | FAIL | 295.25
89 | 59 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Continuous Dimming and high VT | 173.874 |  | 6.9427 |  | 0.10095 |  | 33.7825 |  | 5.4777 |  | 0.25325 |  | 5.3519 |  | 15.0362 |  | 0 |  | 2.771 |  | 0.26954 |  | 0 |  | 4.6184 |  | 3.053% |  | 1.169% |  | FAIL | 296
90 | 60 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Stepped Dimming | 172.6837 |  | 6.9004 |  | 0.10093 |  | 33.6354 |  | 5.4751 |  | 0.25044 |  | 5.2178 |  | 15.0362 |  | 0 |  | 2.7666 |  | 0.2665 |  | 0 |  | 4.6183 |  | 3.717% |  | 1.599% |  | FAIL | 302
91 | 61 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Stepped Dimming and high VT | 172.273 |  | 6.8753 |  | 0.10176 |  | 33.6327 |  | 5.5582 |  | 0.24985 |  | 5.1423 |  | 15.0362 |  | 0 |  | 2.7577 |  | 0.26572 |  | 0 |  | 4.6183 |  | 3.946% |  | 1.607% |  | FAIL | 301.75
92 |  | Large Office CZ-1 WWR-60% Baseline | 181.0399 |  | 7.2182 |  | 0.10192 |  | 34.8191 |  | 5.5742 |  | 0.2761 |  | 6.1648 |  | 15.0362 |  | 0 |  | 2.8471 |  | 0.29753 |  | 0 |  | 4.6184 | [6 empty] | 391
93 | 62 | Daylighting Tests Large OfficeCZ-1WWR-60%,Continuous Dimming | 175.1306 |  | 6.9383 |  | 0.10588 |  | 34.2599 |  | 5.9701 |  | 0.26614 |  | 5.2989 |  | 15.0362 |  | 0 |  | 2.7779 |  | 0.28749 |  | 0 |  | 4.6184 |  | 3.264% |  | 1.606% |  | FAIL | 404.5
94 | 63 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Continuous Dimming and high VT | 175.0594 |  | 6.9339 |  | 0.10597 |  | 34.2538 |  | 5.979 |  | 0.2661 |  | 5.287 |  | 15.0362 |  | 0 |  | 2.7748 |  | 0.28747 |  | 0 |  | 4.6184 |  | 3.303% |  | 1.624% |  | FAIL | 404.75
95 | 64 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Stepped Dimming | 173.0459 |  | 6.8456 |  | 0.10712 |  | 34.0674 |  | 6.0942 |  | 0.26487 |  | 4.9997 |  | 15.0362 |  | 0 |  | 2.7656 |  | 0.28371 |  | 0 |  | 4.6184 |  | 4.416% |  | 2.159% |  | FAIL | 409.75
96 | 65 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Stepped Dimming and high VT | 172.8574 |  | 6.8339 |  | 0.10737 |  | 34.0528 |  | 6.1195 |  | 0.26471 |  | 4.9677 |  | 15.0362 |  | 0 |  | 2.7576 |  | 0.28388 |  | 0 |  | 4.6184 |  | 4.52% |  | 2.201% |  | FAIL | 408.25
97 |  | Stand Alone Retail CZ-7 Baseline | 279.3036 |  | 9.9747 |  | 0.11062 |  | 45.0945 |  | 2.6474 |  | 5.904 |  | 7.8851 |  | 10.726 |  | 0 |  | 9.5203 |  | 0 |  | 0 |  | 8.4121 | [6 empty] | 0
98 | 66 | Daylighting Tests Stand Alone Retail CZ-7 Skylight VT | 275.8255 |  | 9.8464 |  | 0.11076 |  | 44.6707 |  | 2.6612 |  | 5.8652 |  | 7.5081 |  | 10.726 |  | 0 |  | 9.4976 |  | 0 |  | 0 |  | 8.4121 |  | 1.245% |  | 0.9397% |  | FAIL | 0
99 | 67 | Daylighting Tests Stand Alone Retail CZ-7 SRR-5% | 273.9776 |  | 9.7463 |  | 0.11191 |  | 44.4434 |  | 2.7749 |  | 6.038 |  | 6.74 |  | 10.726 |  | 0 |  | 9.7514 |  | 0 |  | 0 |  | 8.4129 |  | 1.907% |  | 1.444% |  | FAIL | 0
100 | 68 | Daylighting Tests Stand Alone Retail CZ-7 SRR-5% and high VT | 273.1831 |  | 9.7129 |  | 0.11202 |  | 44.3406 |  | 2.786 |  | 6.028 |  | 6.6794 |  | 10.726 |  | 0 |  | 9.7087 |  | 0 |  | 0 |  | 8.4129 |  | 2.191% |  | 1.672% |  | FAIL | 0
101 |  | Stand Alone Retail CZ-1 Baseline | 247.4263 |  | 8.9523 |  | 0.19445 |  | 49.9863 |  | 11.0192 |  | 0.77768 |  | 8.1722 |  | 10.726 |  | 0 |  | 10.8703 |  | 0 |  | 0 |  | 8.4205 | [6 empty] | 0
102 | 69 | Daylighting Tests Stand Alone Retail CZ-1 Skylight VT | 244.2487 |  | 8.8212 |  | 0.19501 |  | 49.5959 |  | 11.0756 |  | 0.77116 |  | 7.7584 |  | 10.726 |  | 0 |  | 10.8442 |  | 0 |  | 0 |  | 8.4209 |  | 1.284% |  | 0.781% |  | FAIL | 0
103 | 70 | Daylighting Tests Stand Alone Retail CZ-1 SRR-5% | 237.9628 |  | 8.4889 |  | 0.20061 |  | 49.0209 |  | 11.633 |  | 0.80801 |  | 6.7558 |  | 10.726 |  | 0 |  | 10.6753 |  | 0 |  | 0 |  | 8.4221 |  | 3.825% |  | 1.931% |  | FAIL | 0
104 | 71 | Daylighting Tests Stand Alone Retail CZ-1 SRR-5% and high VT | 237.111 |  | 8.4456 |  | 0.20102 |  | 48.9145 |  | 11.6745 |  | 0.80993 |  | 6.6491 |  | 10.726 |  | 0 |  | 10.6327 |  | 0 |  | 0 |  | 8.4225 |  | 4.169% |  | 2.144% |  | FAIL | 0
105
106 |  | Medium Office CZ-15 Baseline | 294.5639 |  | 10.3283 |  | 0.15484 |  | 50.722 |  | 0.35207 |  | 14.9552 |  | 5.0586 |  | 12.9515 |  | 0 |  | 2.1483 |  | 0.12814 |  | 0 |  | 15.1282 | [6 empty] | 677.25
107 | 72 | Equipment test Medium OfficeCZ-15 low EPD | 270.6055 |  | 9.3035 |  | 0.15517 |  | 47.2584 |  | 0.38529 |  | 14.1784 |  | 5.0586 |  | 10.3612 |  | 0 |  | 2.0171 |  | 0.12973 |  | 0 |  | 15.1282 |  | 8.134% |  | 6.829% |  | FAIL | 740.25
108 | 73 | Equipment test Medium OfficeCZ-15 high EPD | 318.5544 |  | 11.3561 |  | 0.15451 |  | 54.1958 |  | 0.31884 |  | 15.7381 |  | 5.0586 |  | 15.5416 |  | 0 |  | 2.2831 |  | 0.12725 |  | 0 |  | 15.1282 |  | -8.144% |  | -6.849% |  | FAIL | 623
109 |  | Medium Office CZ-16 Baseline | 207.5921 |  | 6.8524 |  | 0.2365 |  | 47.0258 |  | 8.5162 |  | 3.307 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.4761 |  | 0.58519 |  | 0 |  | 15.1282 | [6 empty] | 822.5
110 | 74 | Equipment test Medium OfficeCZ-16 low EPD | 187.5602 |  | 5.9698 |  | 0.24029 |  | 44.3924 |  | 8.8941 |  | 3.0362 |  | 5.0618 |  | 10.3612 |  | 0 |  | 1.339 |  | 0.57193 |  | 0 |  | 15.1284 |  | 9.65% |  | 5.6% |  | FAIL | 873.75
111 | 75 | Equipment test Medium OfficeCZ-16 high EPD | 227.2777 |  | 7.7363 |  | 0.23071 |  | 49.4624 |  | 7.9367 |  | 3.5792 |  | 5.0618 |  | 15.5416 |  | 0 |  | 1.6195 |  | 0.59544 |  | 0 |  | 15.1282 |  | -9.483% |  | -5.181% |  | FAIL | 786.75
112 |  | Medium Office CZ-6 Baseline | 209.3173 |  | 7.505 |  | 0.15807 |  | 41.4112 |  | 0.67479 |  | 6.1474 |  | 5.0618 |  | 12.9515 |  | 0 |  | 1.2533 |  | 0.19441 |  | 0 |  | 15.1282 | [6 empty] | 245.75
113 | 76 | Equipment test Medium OfficeCZ-6 low EPD | 187.3558 |  | 6.5496 |  | 0.15872 |  | 38.2166 |  | 0.74019 |  | 5.6035 |  | 5.0618 |  | 10.3612 |  | 0 |  | 1.1227 |  | 0.19883 |  | 0 |  | 15.1282 |  | 10.49% |  | 7.714% |  | FAIL | 277
114 | 77 | Equipment test Medium OfficeCZ-6 high EPD | 231.4286 |  | 8.4622 |  | 0.15755 |  | 44.6248 |  | 0.62265 |  | 6.6928 |  | 5.0618 |  | 15.5416 |  | 0 |  | 1.3883 |  | 0.18964 |  | 0 |  | 15.1282 |  | -10.56% |  | -7.76% |  | FAIL | 216.5
115 |  | Fast food Restaurant CZ-6 Baseline | 2590.0943 |  | 104.3119 |  | 0.80693 |  | 436.5992 |  | 20.2761 |  | 48.3405 |  | 20.7081 |  | 245.6894 |  | 0 |  | 40.5332 |  | 0 |  | 25.0362 |  | 36.0194 | [6 empty] | 97.66
116 | 78 | Equipment test Fast food RestaurantCZ-6 high Process load | 2678.0432 |  | 108.1705 |  | 0.80298 |  | 449.3712 |  | 19.8781 |  | 50.0952 |  | 20.7081 |  | 256.5361 |  | 0 |  | 41.0866 |  | 0 |  | 25.0514 |  | 36.0194 |  | -3.396% |  | -2.925% |  | FAIL | 94.17

## HVAC Results (hidden)
| TEST RESULTS |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  |  |  | 8 |  | 9 | [7 empty] | 10 |  | 11 |  | 12 |  | 13 |  |  | 14
| Test Case |  | Annual TDV |  | Annual Total End Use Site Energy |  | Annual End Use TDV Energy | [25 empty] | Variation from Baseline |  |  |  |  | Reference Model Occupied Unmet Load Hrs | Applicant Model Occupied Unmet Load Hrs | Area/CoolingCapcity (ft2/Ton) | Area/HeatingCapacity (ft2/kBtu/hr) | Source Energy-Electricity/Area (kBtu/ft2) | Source Energy-Gas/Area (kBtu/ft2)
|  |  | TDV (kBtu/sq.ft) |  | Total End Use (kBtu/sq.ft) |  | Heating (kBtu/sq.ft) |  | Cooling (kBtu/sq.ft) |  | Interior Lighting (kBtu/sq.ft) |  | Interior Equipment (kBtu/sq.ft) |  | Exterior Lighting (kBtu/sq.ft) |  | Exterior Equipment (kBtu/sq.ft) |  | Fans (kBtu/sq.ft) |  | Pumps (kBtu/sq.ft) |  | Heat Rejection (kBtu/sq.ft) |  | Humidification (kBtu/sq.ft) |  | Heat Recovery (kBtu/sq.ft) |  | Refrigeration (kBtu/sq.ft) |  | Water Heating (kBtu/sq.ft) |  | TDV % variation |  | Total End Use Site Energy % Variation
|  |  | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Reference Model | Applicant Model | Pass/Fail
3 |  | PTAC Stripmall CZ-6 Baseline | 228.4444 |  | 31.0667 |  | 0.2341 |  | 65.1568 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 4.3674 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 1 | 0 | 396.6151 | 49.9263 | 228.4354 | 0
4 | 79 | PTAC Test Stripmall CZ-6 Low Eff | 316.4 |  | 44.1778 |  | 3.8605 |  | 80.4185 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 73.4601 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 38.5% |  | 42.2% |  |  | 35 | 0 | 396.6151 | 45.5672 | 316.4166 | 0
5 | 80 | PTAC Test Stripmall CZ-6 High Eff | 216.8444 |  | 29.7778 |  | 0.22525 |  | 55.3438 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 2.607 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -5.078% |  | -4.149% |  |  | 1 | 0 | 396.6151 | 55.2076 | 216.8532 | 0
3 |  | PTAC Stripmall CZ-15 Baseline | 280 |  | 36.5333 |  | 0.10694 |  | 113.0794 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 6.686 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 34 | 387.3439 | 50.1489 | 280.0177 | 0
4 | 81 | PTAC Test Stripmall CZ-15 Low Eff | 404.1778 |  | 54.0889 |  | 2.1304 |  | 166.7004 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 75.2183 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 44.35% |  | 48.05% |  |  | 19 | 155 | 387.3439 | 45.8085 | 404.1943 | 0
5 | 82 | PTAC Test Stripmall CZ-15 High Eff | 257.6 |  | 34.1333 |  | 0.10315 |  | 93.4293 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 3.9051 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -8% |  | -6.569% |  |  | 0 | 28 | 387.3439 | 55.3979 | 257.5824 | 0
3 |  | PTAC Stripmall CZ-16 Baseline | 225.4667 |  | 30.4889 |  | 3.7241 |  | 57.8296 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 4.2314 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 45 | 1 | 320.3664 | 54.149 | 225.4474 | 0
4 | 83 | PTAC Test Stripmall CZ-16 Low Eff | 343.9111 |  | 49.2889 |  | 28.2679 |  | 65.0486 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 90.944 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 52.53% |  | 61.66% |  |  | 85 | 2 | 320.3664 | 49.8745 | 343.9232 | 0
5 | 84 | PTAC Test Stripmall CZ-16 High Eff | 215.7333 |  | 29.4222 |  | 3.4912 |  | 50.0177 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 2.5578 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -4.317% |  | -3.499% |  |  | 48 | 1 | 320.3664 | 59.2248 | 215.7294 | 0
3 |  | PTHP Stripmall CZ-6 Baseline | 228.3111 |  | 31.0667 |  | 0.10231 |  | 65.1594 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 4.3657 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 0 | 396.6151 | 19.8859 | 228.3049 | 0
4 | 85 | PTHP Test Stripmall CZ-6 Low Eff | 314.3111 |  | 43.7778 |  | 1.7742 |  | 80.4215 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 73.4601 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 37.67% |  | 40.92% |  |  | 2 | 0 | 396.6151 | 19.156 | 314.3333 | 0
5 | 86 | PTHP Test Stripmall CZ-6 High Eff | 216.7111 |  | 29.7333 |  | 0.083786 |  | 55.3463 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 2.6058 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -5.081% |  | -4.292% |  |  | 0 | 0 | 396.6151 | 20.6736 | 216.713 | 0
|  | PTHP Stripmall CZ-15 Baseline | 279.9556 |  | 36.5333 |  | 0.047577 |  | 113.082 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 6.6856 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 34 | 387.3439 | 19.6378 | 279.9596 | 0
| 87 | PTHP Test Stripmall CZ-15 Low Eff | 403.0222 |  | 53.9111 |  | 0.9768 |  | 166.7016 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 75.2183 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 43.96% |  | 47.57% |  |  | 1 | 155 | 387.3439 | 18.9353 | 403.042 | 0
| 88 | PTHP Test Stripmall CZ-15 High Eff | 257.5111 |  | 34.1333 |  | 0.038735 |  | 93.4314 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 3.9047 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -8.017% |  | -6.569% |  |  | 0 | 28 | 387.3439 | 20.3945 | 257.5197 | 0
|  | PTHP Stripmall CZ-16 Baseline | 223.9556 |  | 30.1778 |  | 2.2109 |  | 57.8607 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 4.2175 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 10 | 1 | 320.3664 | 17.8807 | 223.9518 | 0
| 89 | PTHP Test Stripmall CZ-16 Low Eff | 330.4889 |  | 46.7556 |  | 14.8331 |  | 65.0507 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 90.944 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 47.57% |  | 54.93% |  |  | 27 | 2 | 320.3664 | 17.3886 | 330.4905 | 0
| 90 | PTHP Test Stripmall CZ-16 High Eff | 214.0889 |  | 29.1556 |  | 1.8399 |  | 50.0434 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 2.5447 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -4.406% |  | -3.387% |  |  | 10 | 1 | 320.3664 | 18.4015 | 214.0908 | 0
|  | PSZ Stripmall CZ-6 Baseline | 286.5778 |  | 40.7111 |  | 1.794 |  | 63.7569 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 59.2741 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0693 | [6 empty] | 31 | 9 | 461.1302 | 35.4294 | 281.7081 | 4.8638
| 91 | PSZ Test Stripmall CZ-6 Low Eff | 401.4222 |  | 56.5333 |  | 2.7317 |  | 119.4358 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 117.4961 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0988 |  | 40.07% |  | 38.86% |  |  | 36 | 19 | 372.1276 | 30.7175 | 395.609 | 5.8305
| 92 | PSZ Test Stripmall CZ-6 High Eff | 238.0889 |  | 34.0889 |  | 0.86649 |  | 38.3672 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 37.1403 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0475 |  | -16.92% |  | -16.27% |  |  | 2 | 10 | 570.0161 | 39.1198 | 234.1847 | 3.9144
|  | PSZ Stripmall CZ-15 Baseline | 360.5333 |  | 49.4222 |  | 1.1663 |  | 135.0747 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 61.1789 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 2.9822 | [6 empty] | 19 | 1155 | 450.8372 | 35.6132 | 356.3985 | 4.1485
| 93 | PSZ Test Stripmall CZ-15 Low Eff | 505.7778 |  | 68.6222 |  | 1.7646 |  | 220.0354 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 120.8307 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0243 |  | 40.29% |  | 38.85% |  |  | 21 | 1046 | 363.1311 | 30.8605 | 501.0105 | 4.7889
| 94 | PSZ Test Stripmall CZ-15 High Eff | 294.4889 |  | 40.8 |  | 0.54735 |  | 92.4311 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 38.4055 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 2.9418 |  | -18.32% |  | -17.45% |  |  | 2 | 1304 | 559.1744 | 39.3341 | 290.9818 | 3.4891
|  | PSZ Stripmall CZ-16 Baseline | 314.2667 |  | 54.1778 |  | 24.9594 |  | 52.5165 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 73.9704 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.1674 | [6 empty] | 76 | 3 | 376.3795 | 40.2861 | 286.1492 | 28.1272
| 95 | PSZ Test Stripmall CZ-16 Low Eff | 431.2444 |  | 70.8444 |  | 28.2809 |  | 93.3771 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 146.758 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.1616 |  | 37.22% |  | 30.76% |  |  | 88 | 18 | 302.176 | 36.1837 | 399.7979 | 31.4429
| 96 | PSZ Test Stripmall CZ-16 High Eff | 262.4444 |  | 44.8 |  | 18.4443 |  | 34.159 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 47.0191 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.1733 |  | -16.49% |  | -17.31% |  |  | 50 | 0 | 461.9885 | 45.09 | 240.8408 | 21.6176
|  | PVAV MediumOffice CZ-6 Baseline (No DataCenter) | 237.8422 |  | 38.2077 |  | 3.775 |  | 37.664 |  | 57.3965 |  | 104.6103 |  | 8.0991 |  | 0 |  | 20.2365 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 | [6 empty] | 120 | 186 | 473.9563 | 13.6307 | 231.7812 | 6.0597
| 97 | PVAV Test MediumOffice CZ-6 Low Eff | 382.3562 |  | 61.5537 |  | 57.6239 |  | 83.5766 |  | 57.3965 |  | 104.6103 |  | 8.0991 |  | 0 |  | 64.9814 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0596 |  | 60.76% |  | 61.1% |  |  | 41 | 6 | 465.2846 | 13.5888 | 376.2879 | 6.0596
| 98 | PVAV Test MediumOffice CZ-6 High Eff | 219.102 |  | 35.4852 |  | 2.0449 |  | 29.7608 |  | 57.3965 |  | 104.6103 |  | 8.0991 |  | 0 |  | 11.1394 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 |  | -7.879% |  | -7.125% |  |  | 192 | 267 | 480.6215 | 13.6307 | 213.0509 | 6.0597
|  | PVAV MediumOffice CZ-15 Baseline (No DataCenter) | 278.4926 |  | 43.5593 |  | 1.6522 |  | 83.5021 |  | 55.544 |  | 102.236 |  | 8.2157 |  | 0 |  | 21.2755 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 | [6 empty] | 90 | 358 | 427.696 | 14.4471 | 272.4253 | 6.0597
| 99 | PVAV Test MediumOffice CZ-15 Low Eff | 412.2287 |  | 63.1573 |  | 31.3298 |  | 144.5665 |  | 55.544 |  | 102.236 |  | 8.2157 |  | 0 |  | 64.2771 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 |  | 48.02% |  | 44.99% |  |  | 42 | 179 | 411.1942 | 14.4259 | 406.169 | 6.0597
| 100 | PVAV Test MediumOffice CZ-15 High Eff | 252.6852 |  | 40.3707 |  | 0.7315 |  | 67.5048 |  | 55.544 |  | 102.236 |  | 8.2157 |  | 0 |  | 12.4018 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0596 |  | -9.267% |  | -7.32% |  |  | 129 | 496 | 446.0173 | 14.4471 | 246.6336 | 6.0596
|  | PVAV MediumOffice CZ-16 Baseline (No DataCenter) | 248.6947 |  | 41.6387 |  | 23.5537 |  | 26.2752 |  | 56.24 |  | 102.9484 |  | 7.905 |  | 0 |  | 25.7041 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 | [6 empty] | 483 | 784 | 438.5266 | 14.7122 | 242.0803 | 6.6056
| 101 | PVAV Test MediumOffice CZ-16 Low Eff | 361.6394 |  | 60.006 |  | 63.9272 |  | 52.0388 |  | 56.24 |  | 102.9484 |  | 7.905 |  | 0 |  | 72.5156 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 |  | 45.42% |  | 44.11% |  |  | 319 | 41 | 438.5266 | 14.3014 | 355.5667 | 6.0677
| 102 | PVAV Test MediumOffice CZ-16 High Eff | 224.7893 |  | 37.5177 |  | 14.662 |  | 22.0761 |  | 56.24 |  | 102.9484 |  | 7.905 |  | 0 |  | 14.8989 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 6.0597 |  | -9.612% |  | -9.897% |  |  | 806 | 905 | 438.5266 | 14.9555 | 218.7303 | 6.0597
|  | VAV LargeOffice CZ-6 Baseline | 221.4494 |  | 34.2327 |  | 2.8214 |  | 36.8729 |  | 55.9814 |  | 63.9083 |  | 5.8817 |  | 23.1495 |  | 13.4951 |  | 14.1879 |  | 4.036 |  | 0 |  | 0 |  | 0 |  | 1.1146 | [6 empty] | 0 | 195 | 620.2401 | 28.6892 | 217.5129 | 3.9361
| 103 | VAV Test LargeOffice CZ-6 Low Eff | 279.2285 |  | 45.679 |  | 9.534 |  | 53.9787 |  | 55.9814 |  | 63.9083 |  | 5.8817 |  | 23.1495 |  | 44.1035 |  | 16.4726 |  | 5.1051 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | 26.09% |  | 33.44% |  |  | 0 | 71 | 620.2401 | 28.6892 | 268.5808 | 10.6486
| 104 | VAV Test LargeOffice CZ-6 Low Eff | 212.3457 |  | 32.0625 |  | 0.86415 |  | 32.8345 |  | 55.9814 |  | 63.9083 |  | 5.8817 |  | 23.1495 |  | 10.5281 |  | 14.2966 |  | 3.7859 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | -4.111% |  | -6.339% |  |  | 2 | 310 | 620.2401 | 28.6892 | 210.366 | 1.9788
|  | VAV LargeOffice CZ-15 Baseline | 253.905 |  | 38.2661 |  | 1.1512 |  | 60.2573 |  | 54.175 |  | 62.7314 |  | 5.9708 |  | 23.4992 |  | 16.9821 |  | 19.1593 |  | 8.8637 |  | 0 |  | 0 |  | 0 |  | 1.1146 | [6 empty] | 0 | 324 | 567.2307 | 30.0576 | 251.6388 | 2.2658
| 105 | VAV Test LargeOffice CZ-15 Low Eff | 307.5325 |  | 47.1792 |  | 4.3985 |  | 76.1737 |  | 54.175 |  | 62.7314 |  | 5.9708 |  | 23.4992 |  | 49.6021 |  | 20.6993 |  | 9.168 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | 21.12% |  | 23.29% |  |  | 0 | 203 | 567.2307 | 30.0576 | 302.0194 | 5.5131
| 106 | VAV Test LargeOffice CZ-15 Low Eff | 243.5077 |  | 36.7016 |  | 0.42424 |  | 53.9208 |  | 54.175 |  | 62.7314 |  | 5.9708 |  | 23.4992 |  | 13.5943 |  | 19.4116 |  | 8.6655 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | -4.095% |  | -4.088% |  |  | 0 | 458 | 567.2307 | 30.0576 | 241.9686 | 1.5388
|  | VAV LargeOffice CZ-16 Baseline | 210.5887 |  | 38.6211 |  | 16.7317 |  | 20.6354 |  | 54.8529 |  | 63.0282 |  | 5.7388 |  | 23.4067 |  | 16.4024 |  | 7.9443 |  | 0.73476 |  | 0 |  | 0 |  | 0 |  | 1.1146 | [6 empty] | 28 | 572 | 571.6977 | 28.7398 | 192.7434 | 17.8463
| 107 | VAV Test LargeOffice CZ-16 Low Eff | 264.9282 |  | 47.2996 |  | 17.0744 |  | 33.9963 |  | 54.8529 |  | 63.0282 |  | 5.7388 |  | 23.4067 |  | 52.3573 |  | 12.3519 |  | 1.0062 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | 25.8% |  | 22.47% |  |  | 24 | 409 | 571.6977 | 28.7398 | 246.7383 | 18.189
| 108 | VAV Test LargeOffice CZ-16 Low Eff | 197.3573 |  | 34.1926 |  | 10.3486 |  | 17.8544 |  | 54.8529 |  | 63.0282 |  | 5.7388 |  | 23.4067 |  | 12.3661 |  | 7.9798 |  | 0.66729 |  | 0 |  | 0 |  | 0 |  | 1.1146 |  | -6.283% |  | -11.47% |  |  | 98 | 646 | 571.6977 | 28.7398 | 185.8939 | 11.4632
|  | FanCoil Stripmall CZ-6 Baseline | 335.9111 |  | 46.7556 |  | 0.092628 |  | 149.0426 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 2.0239 |  | 25.2671 |  | 0.81176 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 0 | 311.9674 | 43.9524 | 335.8225 | 0.092628
| 109 | FanCoil Test Stripmall CZ-6 Low Eff | 338.7111 |  | 47.0222 |  | 0.091786 |  | 150.8248 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 2.962 |  | 25.356 |  | 0.79912 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0.8336% |  | 0.5703% |  |  | 0 | 0 | 311.9674 | 43.9524 | 338.6186 | 0.091786
| 110 | FanCoil Test Stripmall CZ-6 High Eff | 335.5111 |  | 46.7111 |  | 0.092628 |  | 148.9676 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 1.6858 |  | 25.2671 |  | 0.81091 |  | 0 |  | 0 |  | 0 |  | 0 |  | -0.1191% |  | -0.09506% |  |  | 0 | 0 | 311.9674 | 43.9524 | 335.409 | 0.092628
|  | FanCoil Stripmall CZ-15 Baseline | 369.2444 |  | 50.5778 |  | 0.04084 |  | 178.2826 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 2.5094 |  | 26.2136 |  | 2.0391 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 | 25 | 306.7131 | 44.135 | 369.1895 | 0.04084
| 111 | FanCoil Test Stripmall CZ-15 Low Eff | 372.6222 |  | 51.1111 |  | 0.04084 |  | 179.795 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 4.1426 |  | 26.4477 |  | 2.0424 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0.9148% |  | 1.054% |  |  | 0 | 25 | 306.7131 | 44.135 | 372.5725 | 0.04084
| 112 | FanCoil Test Stripmall CZ-15 High Eff | 368.7111 |  | 50.5333 |  | 0.04084 |  | 178.1799 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 2.0904 |  | 26.2136 |  | 2.0361 |  | 0 |  | 0 |  | 0 |  | 0 |  | -0.1444% |  | -0.08787% |  |  | 0 | 25 | 306.7131 | 44.135 | 368.6649 | 0.04084
|  | FanCoil Stripmall CZ-16 Baseline | 325.3333 |  | 45.3333 |  | 1.525 |  | 137.4464 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 2.1165 |  | 24.1173 |  | 0.48082 |  | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 46 | 2 | 264.8185 | 47.5087 | 323.8234 | 1.525
| 113 | FanCoil Test Stripmall CZ-16 Low Eff | 326.5778 |  | 45.3778 |  | 1.4715 |  | 137.7289 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 3.1131 |  | 24.1497 |  | 0.46651 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0.3825% |  | 0.09804% |  |  | 36 | 1 | 264.8185 | 47.5087 | 325.1206 | 1.4715
| 114 | FanCoil Test Stripmall CZ-16 High Eff | 324.9333 |  | 45.2889 |  | 1.5296 |  | 137.3795 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 1.7633 |  | 24.1173 |  | 0.4804 |  | 0 |  | 0 |  | 0 |  | 0 |  | -0.123% |  | -0.09804% |  |  | 46 | 2 | 264.8185 | 47.5087 | 323.4032 | 1.5296
|  | PSZ Stripmall CZ-6 Baseline | 286.5778 |  | 40.7111 |  | 1.794 |  | 63.7569 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 59.2741 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.0693 | [6 empty] | 31 | 9 | 461.1302 | 35.4294 | 281.7081 | 4.8638
| 115 | VRF Test Stripmall CZ-6 Low Eff | 250.8889 |  | 34.9778 |  | 1.9599 |  | 65.7577 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 24.4865 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -12.45% |  | -14.08% |  |  | 33 | 0 | 396.6151 | 33.0499 | 250.8816 | 0
| 116 | VRF Test Stripmall CZ-6 High Eff | 234.8444 |  | 33.0667 |  | 1.5427 |  | 50.1457 |  | 107.1361 |  | 38.4144 |  | 13.127 |  | 0 |  | 24.4865 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -18.05% |  | -18.78% |  |  | 33 | 0 | 396.6151 | 33.0499 | 234.852 | 0
|  | PSZ Stripmall CZ-15 Baseline | 360.5333 |  | 49.4222 |  | 1.1663 |  | 135.0747 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 61.1789 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 2.9822 | [6 empty] | 19 | 1155 | 450.8372 | 35.6132 | 356.3985 | 4.1485
| 117 | VRF Test Stripmall CZ-15 Low Eff | 320.2222 |  | 43.1556 |  | 1.1646 |  | 133.8558 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 25.0726 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -11.18% |  | -12.68% |  |  | 15 | 134 | 387.3439 | 32.2773 | 320.2383 | 0
| 118 | VRF Test Stripmall CZ-15 High Eff | 287.8222 |  | 39.2889 |  | 0.91659 |  | 101.6694 |  | 108.4493 |  | 38.4144 |  | 13.2811 |  | 0 |  | 25.0726 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -20.17% |  | -20.5% |  |  | 15 | 134 | 387.3439 | 32.2773 | 287.8039 | 0
|  | PSZ Stripmall CZ-16 Baseline | 314.2667 |  | 54.1778 |  | 24.9594 |  | 52.5165 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 73.9704 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 3.1674 | [6 empty] | 76 | 3 | 376.3795 | 40.2861 | 286.1492 | 28.1272
| 119 | VRF Test Stripmall CZ-16 Low Eff | 265.7333 |  | 37.2 |  | 14.9509 |  | 60.7899 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 30.3145 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -15.44% |  | -31.34% |  |  | 52 | 1 | 320.3664 | 26.6961 | 265.7181 | 0
| 120 | VRF Test Stripmall CZ-16 High Eff | 247.8222 |  | 35.0222 |  | 11.5393 |  | 46.3054 |  | 108.2691 |  | 38.4144 |  | 12.9797 |  | 0 |  | 30.3145 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | -21.14% |  | -35.36% |  |  | 52 | 1 | 320.3664 | 26.6961 | 247.822 | 0

## Summary(Reference) (hidden)
[17 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | [5 empty] | 16
|  |  | Annual Energy by End-Use [kBtu] | TDV | Total | Heating | Cooling | Interior Lighting | Interior Equipment | Exterior Lighting | Fans | Pumps | Refrigeration | Water Heating | Total Electric Use [kWh] | Total Gas Use [therms] | Total TDV EUI [kBtu/sf] | TDV EUI Electricity [kwh/sf] | TDV EUI Natural Gas[therm/sf] | Total EUI [kBtu/sf] | Heating EUI [kBtu/sf] | Cooling EUI [kBtu/sf] | Interior Lighting EUI [kBtu/sf] | Interior Equipment EUI [kBtu/sf] | Exterior Lighting EUI [kBtu/sf] | Fans EUI [kBtu/sf] | Pumps EUI [kBtu/sf] | Refrigeration EUI [kBtu/sf] | Water Heating EUI [kBtu/sf] | TDV Variation | Site Energy TDV EUI variation | Total Area [sf] | Gross Wall Area [sf] | Window Opening Area [sf] | Unmet Load Hrs - Occupied Heating | Unmet Load Hrs - Occupied Cooling | Total UMNL
3 |  | Medium Office CZ-15 Baseline | 0001 CZ15 MediumOffice Base | 15796829.7417 | 2720111.5391 | 18880.5144 | 802014.3007 | 271284.1783 | 694560.2887 | 0 | 115207.1549 | 6871.6732 | 0 | 811293.429 | 553886.1111 | 8303.829 | 294.5639 | 10.3283 | 0.15484 | 50.722 | 0.35207 | 14.9552 | 5.0586 | 12.9515 | 0 | 2.1483 | 0.12814 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 80.25 | 597 | 677.25
4 | 1 | Envelope Test Medium OfficeCZ-15 Roof Insulation | 0002 CZ15 MediumOffice RoofLtR+20 | 15752794.1645 | 2714604.7224 | 18207.5643 | 797426.8664 | 271284.1783 | 694560.2887 | 0 | 115027.0697 | 6814.8041 | 0 | 811293.429 | 552469.4444 | 8297.0978 | 293.7428 | 10.3019 | 0.15472 | 50.6193 | 0.33952 | 14.8696 | 5.0586 | 12.9515 | 0 | 2.1449 | 0.12708 | 0 | 15.1282 | 0.2788% | 0.2024% | 53627.8468 | 21287.4627 | 7027.0036 | 80.5 | 594 | 674.5
5 | 2 | Envelope Test Medium OfficeCZ-15 Wall Insulation | 0003 CZ15 MediumOffice WallLtR+20 | 15737458.4856 | 2713268.3005 | 17951.6538 | 796886.6108 | 271284.1783 | 694560.2887 | 0 | 114600.552 | 6710.5443 | 0 | 811293.429 | 552155.5556 | 8294.4432 | 293.4568 | 10.2961 | 0.15467 | 50.5944 | 0.33475 | 14.8596 | 5.0586 | 12.9515 | 0 | 2.137 | 0.12513 | 0 | 15.1282 | 0.3758% | 0.2516% | 53627.8468 | 21287.4627 | 7027.0036 | 79.75 | 597 | 676.75
6 | 3 | Envelope Test Medium OfficeCZ-15 Floor Slab Insulation | 0004 CZ15 MediumOffice UnhtSlabF24vR-5 | 15849566.2789 | 2725921.6572 | 18179.1298 | 807805.4625 | 271284.1783 | 694560.2887 | 0 | 116230.7972 | 6577.8499 | 0 | 811293.429 | 555797.2222 | 8296.7186 | 295.5473 | 10.364 | 0.15471 | 50.8303 | 0.33899 | 15.0632 | 5.0586 | 12.9515 | 0 | 2.1674 | 0.12266 | 0 | 15.1282 | -0.3338% | -0.2136% | 53627.8468 | 21287.4627 | 7027.0036 | 73.75 | 599.75 | 673.5
7 | 4 | Envelope Test Medium OfficeCZ-15 Infiltration | 0005 CZ15 MediumOffice BaseInfil+5 | 15823321.2266 | 2723021.3373 | 19667.2025 | 803815.1529 | 271284.1783 | 694560.2887 | 0 | 115358.8056 | 7042.2802 | 0 | 811293.429 | 554508.3333 | 8311.6979 | 295.0579 | 10.3399 | 0.15499 | 50.7763 | 0.36673 | 14.9888 | 5.0586 | 12.9515 | 0 | 2.1511 | 0.13132 | 0 | 15.1282 | -0.1677% | -0.107% | 53627.8468 | 21287.4627 | 7027.0036 | 82.25 | 593.75 | 676
8 |  | Medium Office CZ-16 Baseline | 0013 CZ16 MediumOffice Base | 11132717.1259 | 2521894.5724 | 456705.6156 | 177346.0366 | 271454.7853 | 694560.2887 | 0 | 79161.6748 | 31382.2205 | 0 | 811293.429 | 367480.5556 | 12683.182 | 207.5921 | 6.8524 | 0.2365 | 47.0258 | 8.5162 | 3.307 | 5.0618 | 12.9515 | 0 | 1.4761 | 0.58519 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 747.75 | 74.75 | 822.5
9 | 5 | Envelope Test Medium OfficeCZ-16 Roof Insulation | 0014 CZ16 MediumOffice RoofLtR+20 | 11100860.997 | 2511269.544 | 447530.7472 | 176398.2196 | 271454.7853 | 694560.2887 | 0 | 78981.5896 | 31059.9627 | 0 | 811293.429 | 367055.5556 | 12591.4102 | 206.9981 | 6.8445 | 0.23479 | 46.8277 | 8.3451 | 3.2893 | 5.0618 | 12.9515 | 0 | 1.4728 | 0.57918 | 0 | 15.1282 | 0.2861% | 0.4213% | 53627.8468 | 21287.4627 | 7027.0036 | 748 | 74.25 | 822.25
10 | 6 | Envelope Test Medium OfficeCZ-16 Wall Insulation | 0015 CZ16 MediumOffice WallLtR+20 | 11098861.1031 | 2508255.486 | 444184.9532 | 176834.2154 | 271454.7853 | 694560.2887 | 0 | 79019.5023 | 30908.312 | 0 | 811293.429 | 367152.7778 | 12557.9439 | 206.9608 | 6.8463 | 0.23417 | 46.7715 | 8.2827 | 3.2974 | 5.0618 | 12.9515 | 0 | 1.4735 | 0.57635 | 0 | 15.1282 | 0.3041% | 0.5408% | 53627.8468 | 21287.4627 | 7027.0036 | 747.25 | 73.75 | 821
11 | 7 | Envelope Test Medium OfficeCZ-16 Floor Slab Insulation | 0016 CZ16 MediumOffice UnhtSlabF24vR-5 | 11140991.5682 | 2519335.4666 | 452791.1315 | 178606.6332 | 271454.7853 | 694560.2887 | 0 | 79758.7995 | 30879.8775 | 0 | 811293.429 | 367877.7778 | 12644.0273 | 207.7464 | 6.8598 | 0.23577 | 46.9781 | 8.4432 | 3.3305 | 5.0618 | 12.9515 | 0 | 1.4873 | 0.57582 | 0 | 15.1282 | -0.07433% | 0.1015% | 53627.8468 | 21287.4627 | 7027.0036 | 741.5 | 75.25 | 816.75
12 | 8 | Envelope Test Medium OfficeCZ-16 Infiltration | 0017 CZ16 MediumOffice BaseInfil+5 | 11161985.7145 | 2536509.9104 | 470543.7436 | 177251.2549 | 271454.7853 | 694560.2887 | 0 | 79218.5438 | 32197.3431 | 0 | 811293.429 | 367708.3333 | 12821.5981 | 208.1379 | 6.8567 | 0.23908 | 47.2984 | 8.7742 | 3.3052 | 5.0618 | 12.9515 | 0 | 1.4772 | 0.60038 | 0 | 15.1282 | -0.2629% | -0.5795% | 53627.8468 | 21287.4627 | 7027.0036 | 743.75 | 73.25 | 817
13 |  | Medium Office CZ-6 Baseline | 0025 CZ06 MediumOffice Base | 11225233.5421 | 2220792.0717 | 36187.6526 | 329669.7047 | 271454.7853 | 694560.2887 | 0 | 67209.7026 | 10425.9869 | 0 | 811293.429 | 402477.7778 | 8476.9439 | 209.3173 | 7.505 | 0.15807 | 41.4112 | 0.67479 | 6.1474 | 5.0618 | 12.9515 | 0 | 1.2533 | 0.19441 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 181.25 | 64.5 | 245.75
14 | 9 | Envelope Test Medium OfficeCZ-6 Roof Insulation | 0026 CZ06 MediumOffice RoofLtR+20 | 11198941.0989 | 2216602.7206 | 33941.3263 | 327925.7215 | 271454.7853 | 694560.2887 | 0 | 67152.8336 | 10283.8143 | 0 | 811293.429 | 401911.1111 | 8454.3802 | 208.827 | 7.4944 | 0.15765 | 41.3331 | 0.6329 | 6.1148 | 5.0618 | 12.9515 | 0 | 1.2522 | 0.19176 | 0 | 15.1282 | 0.2342% | 0.1886% | 53627.8468 | 21287.4627 | 7027.0036 | 181.5 | 65.25 | 246.75
15 | 10 | Envelope Test Medium OfficeCZ-6 Wall Insulation | 0027 CZ06 MediumOffice WallLtR+20 | 11210779.333 | 2217692.7101 | 33742.2848 | 329252.6653 | 271454.7853 | 694560.2887 | 0 | 67313.9625 | 10075.2946 | 0 | 811293.429 | 402286.1111 | 8452.4841 | 209.0477 | 7.5014 | 0.15761 | 41.3534 | 0.62919 | 6.1396 | 5.0618 | 12.9515 | 0 | 1.2552 | 0.18787 | 0 | 15.1282 | 0.1288% | 0.1396% | 53627.8468 | 21287.4627 | 7027.0036 | 180.5 | 66 | 246.5
16 | 11 | Envelope Test Medium OfficeCZ-6 Floor Slab Insulation | 0028 CZ06 MediumOffice UnhtSlabF24vR-5 | 11245431.5221 | 2222100.0591 | 35372.53 | 331887.5965 | 271454.7853 | 694560.2887 | 0 | 67731.002 | 9819.384 | 0 | 811293.429 | 403102.7778 | 8468.6959 | 209.6939 | 7.5167 | 0.15792 | 41.4356 | 0.65959 | 6.1887 | 5.0618 | 12.9515 | 0 | 1.263 | 0.1831 | 0 | 15.1282 | -0.1799% | -0.0589% | 53627.8468 | 21287.4627 | 7027.0036 | 166.75 | 64.5 | 231.25
17 | 12 | Envelope Test Medium OfficeCZ-6 Infiltration | 0029 CZ06 MediumOffice BaseInfil+5 | 11225299.8893 | 2221692.4978 | 37476.6837 | 329186.3181 | 271454.7853 | 694560.2887 | 0 | 67067.5301 | 10653.4629 | 0 | 811293.429 | 402363.8889 | 8489.8375 | 209.3185 | 7.5029 | 0.15831 | 41.428 | 0.69883 | 6.1383 | 5.0618 | 12.9515 | 0 | 1.2506 | 0.19866 | 0 | 15.1282 | -0.0005911% | -0.04055% | 53627.8468 | 21287.4627 | 7027.0036 | 185.75 | 65 | 250.75
18 |  | Small Office CZ-15 SolarReflectance-Low Slope Baseline | 0037 CZ15 SmallOffice BaseLslope | 1237830.0299 | 185639.4353 | 4549.5215 | 48973.7038 | 33808.632 | 71256.8812 | 0 | 10710.332 | 0 | 0 | 16340.3649 | 48283.3333 | 208.9514 | 224.9749 | 8.7755 | 0.037977 | 33.7399 | 0.82687 | 8.9009 | 6.1447 | 12.9509 | 0 | 1.9466 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 25.33 | 121 | 146.33
19 | 13 | Envelope Test Small OfficeCZ-15 SolarReflectance-Low Slope | 0038 CZ15 SmallOffice SRefLSlope+20 | 1229233.3298 | 184672.6619 | 4615.8687 | 48149.103 | 33808.632 | 71256.8812 | 0 | 10511.2904 | 0 | 0 | 16340.3649 | 47980.5556 | 209.6151 | 223.4125 | 8.7204 | 0.038097 | 33.5642 | 0.83893 | 8.7511 | 6.1447 | 12.9509 | 0 | 1.9104 | 0 | 0 | 2.9699 | 0.6945% | 0.5208% | 5502.0804 | 3030.1484 | 642.3902 | 26 | 121.33 | 147.33
20 |  | Small Office CZ-16 SolarReflectance-Low Slope Baseline | 0045 CZ16 SmallOffice BaseLslope | 1253535.3574 | 187525.5911 | 4739.0849 | 50319.6039 | 33808.632 | 71256.8812 | 0 | 11051.5461 | 0 | 0 | 16340.3649 | 48780.5556 | 210.8476 | 227.8293 | 8.8658 | 0.038321 | 34.0827 | 0.86133 | 9.1456 | 6.1447 | 12.9509 | 0 | 2.0086 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 26 | 126.67 | 152.67
21 | 14 | Envelope Test Small OfficeCZ-16 SolarReflectance-Low Slope | 0046 CZ16 SmallOffice SRefLSlope+20 | 1241014.695 | 186122.8219 | 4843.3448 | 49115.8763 | 33808.632 | 71256.8812 | 0 | 10748.2446 | 0 | 0 | 16340.3649 | 48338.8889 | 211.8904 | 225.5537 | 8.7856 | 0.038511 | 33.8277 | 0.88028 | 8.9268 | 6.1447 | 12.9509 | 0 | 1.9535 | 0 | 0 | 2.9699 | 0.9988% | 0.748% | 5502.0804 | 3030.1484 | 642.3902 | 26.5 | 120.33 | 146.83
22 |  | Small Office CZ-6 SolarReflectance-Low Slope Baseline | 0041 CZ06 SmallOffice BaseLslope | 1018599.9606 | 166010.1454 | 11951.9722 | 24946.5431 | 33846.5446 | 71256.8812 | 0 | 7667.8394 | 0 | 0 | 16340.3649 | 40361.1111 | 282.9946 | 185.13 | 7.3356 | 0.051434 | 30.1722 | 2.1723 | 4.534 | 6.1516 | 12.9509 | 0 | 1.3936 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 52.33 | 26.5 | 78.83
23 | 15 | Envelope Test Small OfficeCZ-6 SolarReflectance-Low Slope | 0042 CZ06 SmallOffice SRefLSlope+20 | 1008117.1047 | 165043.3721 | 12226.8391 | 23989.248 | 33846.5446 | 71256.8812 | 0 | 7383.4943 | 0 | 0 | 16340.3649 | 39994.4444 | 285.8387 | 183.2247 | 7.269 | 0.051951 | 29.9965 | 2.2222 | 4.36 | 6.1516 | 12.9509 | 0 | 1.3419 | 0 | 0 | 2.9699 | 1.029% | 0.5824% | 5502.0804 | 3030.1484 | 642.3902 | 54.17 | 26.5 | 80.67
24 |  | Small Office CZ-15 SolarReflectance-Steep Slope Baseline | 0039 CZ15 SmallOffice BaseSslope | 1042883.0318 | 169137.9415 | 12577.5314 | 26794.7862 | 33846.5446 | 71256.8812 | 0 | 8312.355 | 0 | 0 | 16340.3649 | 41091.6667 | 289.3466 | 189.5434 | 7.4684 | 0.052589 | 30.7407 | 2.286 | 4.8699 | 6.1516 | 12.9509 | 0 | 1.5108 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 52.33 | 29.83 | 82.16
25 | 16 | Envelope Test Small OfficeCZ-15 SolarReflectance-Steep Slope | 0040 CZ15 SmallOffice SRefSSlope+20 | 1027111.3571 | 167640.3907 | 12994.5709 | 25344.6263 | 33846.5446 | 71256.8812 | 0 | 7866.881 | 0 | 0 | 16340.3649 | 40533.3333 | 293.4232 | 186.6769 | 7.3669 | 0.053329 | 30.4685 | 2.3618 | 4.6064 | 6.1516 | 12.9509 | 0 | 1.4298 | 0 | 0 | 2.9699 | 1.512% | 0.8854% | 5502.0804 | 3030.1484 | 642.3902 | 54.67 | 27.5 | 82.17
26 |  | Small Office CZ-16 SolarReflectance-Steep Slope Baseline | 0043 CZ06 SmallOffice BaseSslope | 999444.5792 | 187847.8488 | 42367.4194 | 16728.9698 | 33780.1974 | 71256.8812 | 0 | 7364.538 | 0 | 0 | 16340.3649 | 37847.2222 | 587.2256 | 181.6485 | 6.8787 | 0.10673 | 34.1412 | 7.7003 | 3.0405 | 6.1395 | 12.9509 | 0 | 1.3385 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 140.83 | 22.33 | 163.16
27 | 17 | Envelope Test Small OfficeCZ-16 SolarReflectance-Steep Slope | 0044 CZ06 SmallOffice SRefSSlope+20 | 994809.7542 | 187790.9798 | 42955.0659 | 16245.5832 | 33780.1974 | 71256.8812 | 0 | 7203.4091 | 0 | 0 | 16340.3649 | 37658.3333 | 593.1036 | 180.8061 | 6.8444 | 0.1078 | 34.1309 | 7.8071 | 2.9526 | 6.1395 | 12.9509 | 0 | 1.3092 | 0 | 0 | 2.9699 | 0.4637% | 0.03027% | 5502.0804 | 3030.1484 | 642.3902 | 140.83 | 19.67 | 160.5
28 |  | Small Office CZ-6 SolarReflectance-Steep Slope Baseline | 0047 CZ16 SmallOffice BaseSslope | 1011614.5494 | 189516.0067 | 42793.937 | 17610.4396 | 33780.1974 | 71256.8812 | 0 | 7734.1866 | 0 | 0 | 16340.3649 | 38211.1111 | 591.4919 | 183.8604 | 6.9448 | 0.1075 | 34.4444 | 7.7778 | 3.2007 | 6.1395 | 12.9509 | 0 | 1.4057 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 140.67 | 20.67 | 161.34
29 | 18 | Envelope Test Small OfficeCZ-6 SolarReflectance-Steep Slope | 0048 CZ16 SmallOffice SRefSSlope+20 | 1004714.4417 | 189373.8342 | 43618.5378 | 16890.0987 | 33780.1974 | 71256.8812 | 0 | 7487.7542 | 0 | 0 | 16340.3649 | 37927.7778 | 599.7399 | 182.6063 | 6.8934 | 0.109 | 34.4186 | 7.9276 | 3.0698 | 6.1395 | 12.9509 | 0 | 1.3609 | 0 | 0 | 2.9699 | 0.6821% | 0.07502% | 5502.0804 | 3030.1484 | 642.3902 | 140.33 | 18 | 158.33
30 |  | Envelope Test SmallOfficeCZ-15 Light | 0090 CZ15 SmallOffice BaseLt | 1230692.968 | 184852.7472 | 4710.6504 | 48215.4502 | 33808.632 | 71256.8812 | 0 | 10520.7686 | 0 | 0 | 16340.3649 | 48005.5556 | 210.5631 | 223.6777 | 8.725 | 0.03827 | 33.5969 | 0.85616 | 8.7631 | 6.1447 | 12.9509 | 0 | 1.9121 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 27.17 | 120.83 | 148
31 | 19 | Envelope Test Small OfficeCZ-15 Heavy | 0091 CZ15 SmallOffice Hvy | 1228465.598 | 184606.3147 | 4596.9124 | 48054.3213 | 33808.632 | 71256.8812 | 0 | 10539.7249 | 0 | 0 | 16340.3649 | 47966.6667 | 209.4255 | 223.2729 | 8.7179 | 0.038063 | 33.5521 | 0.83549 | 8.7338 | 6.1447 | 12.9509 | 0 | 1.9156 | 0 | 0 | 2.9699 | 0.181% | 0.08101% | 5502.0804 | 3030.1484 | 642.3902 | 26 | 124.67 | 150.67
32 |  | Envelope Test SmallofficeCZ-16 Light | 0092 CZ16 SmallOffice BaseLt | 997435.2072 | 187933.1524 | 42746.5462 | 16501.4938 | 33780.1974 | 71256.8812 | 0 | 7298.1908 | 0 | 0 | 16340.3649 | 37761.1111 | 591.0178 | 181.2833 | 6.8631 | 0.10742 | 34.1567 | 7.7692 | 2.9991 | 6.1395 | 12.9509 | 0 | 1.3264 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 138.5 | 21.67 | 160.17
33 | 20 | Envelope Test SmallOfficeCZ-16 Heavy | 0093 CZ16 SmallOffice Hvy | 995331.0535 | 187421.3312 | 42395.8539 | 16406.7121 | 33780.1974 | 71256.8812 | 0 | 7241.3218 | 0 | 0 | 16340.3649 | 37713.8889 | 587.51 | 180.9009 | 6.8545 | 0.10678 | 34.0637 | 7.7054 | 2.9819 | 6.1395 | 12.9509 | 0 | 1.3161 | 0 | 0 | 2.9699 | 0.211% | 0.1251% | 5502.0804 | 3030.1484 | 642.3902 | 139.67 | 19.67 | 159.34
34 |  | Envelope Test SmallOfficeCZ-6 Light | 0094 CZ06 SmallOffice BaseLt | 1014619.1292 | 165915.3637 | 12331.099 | 24576.8945 | 33846.5446 | 71256.8812 | 0 | 7573.0577 | 0 | 0 | 16340.3649 | 40222.2222 | 286.7868 | 184.4065 | 7.3104 | 0.052123 | 30.155 | 2.2412 | 4.4668 | 6.1516 | 12.9509 | 0 | 1.3764 | 0 | 0 | 2.9699 |  |  | 5502.0804 | 3030.1484 | 642.3902 | 53.67 | 26.17 | 79.84
35 | 21 | Envelope Test SmallOfficeCZ-6 Heavy | 0095 CZ06 SmallOffice Hvy | 1011756.7219 | 165242.4137 | 11866.6687 | 24415.7656 | 33846.5446 | 71256.8812 | 0 | 7516.1887 | 0 | 0 | 16340.3649 | 40161.1111 | 282.1413 | 183.8862 | 7.2993 | 0.051279 | 30.0327 | 2.1568 | 4.4376 | 6.1516 | 12.9509 | 0 | 1.3661 | 0 | 0 | 2.9699 | 0.2821% | 0.1519% | 5502.0804 | 3030.1484 | 642.3902 | 53.17 | 26.17 | 79.34
37 |  | Medium Office CZ-15 Baseline | 0001 CZ15 MediumOffice Base | 15796829.7417 | 2720111.5391 | 18880.5144 | 802014.3007 | 271284.1783 | 694560.2887 | 0 | 115207.1549 | 6871.6732 | 0 | 811293.429 | 553886.1111 | 8303.829 | 294.5639 | 10.3283 | 0.15484 | 50.722 | 0.35207 | 14.9552 | 5.0586 | 12.9515 | 0 | 2.1483 | 0.12814 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 80.25 | 597 | 677.25
38 | 22 | Envelope Glazing Test Medium OfficeCZ-15 Window U | 0006 CZ15 MediumOffice WinU-20 | 15689641.1186 | 2707666.7021 | 14871.2485 | 794336.9831 | 271303.1346 | 694560.2887 | 0 | 115264.0239 | 6037.5942 | 0 | 811293.429 | 551413.8889 | 8263.7262 | 292.5652 | 10.2822 | 0.15409 | 50.4899 | 0.2773 | 14.812 | 5.059 | 12.9515 | 0 | 2.1493 | 0.11258 | 0 | 15.1282 | 0.6785% | 0.4575% | 53627.8468 | 21287.4627 | 7027.0036 | 73.75 | 611 | 684.75
39 | 23 | Envelope Glazing Test Medium OfficeCZ-15 Window SHGC | 0007 CZ15 MediumOffice WinSHGC-20 | 15472913.2861 | 2682378.9448 | 21212.1442 | 767959.2363 | 271284.1783 | 694560.2887 | 0 | 109065.3008 | 7004.3675 | 0 | 811293.429 | 542144.4444 | 8327.1512 | 288.5239 | 10.1094 | 0.15528 | 50.0184 | 0.39554 | 14.3202 | 5.0586 | 12.9515 | 0 | 2.0337 | 0.13061 | 0 | 15.1282 | 2.051% | 1.387% | 53627.8468 | 21287.4627 | 7027.0036 | 94.25 | 542 | 636.25
40 | 24 | Envelope Glazing Test Medium OfficeCZ-15 Window U&SHGC | 0008 CZ15 MediumOffice WinU_SHGC-20 | 15360028.2829 | 2668597.6858 | 16349.843 | 759808.0102 | 271303.1346 | 694560.2887 | 0 | 109074.779 | 6217.6794 | 0 | 811293.429 | 539533.3333 | 8278.4211 | 286.4189 | 10.0607 | 0.15437 | 49.7614 | 0.30488 | 14.1682 | 5.059 | 12.9515 | 0 | 2.0339 | 0.11594 | 0 | 15.1282 | 2.765% | 1.894% | 53627.8468 | 21287.4627 | 7027.0036 | 89.25 | 544 | 633.25
41 |  | Medium Office CZ-16 Baseline | 0013 CZ16 MediumOffice Base | 11132717.1259 | 2521894.5724 | 456705.6156 | 177346.0366 | 271454.7853 | 694560.2887 | 0 | 79161.6748 | 31382.2205 | 0 | 811293.429 | 367480.5556 | 12683.182 | 207.5921 | 6.8524 | 0.2365 | 47.0258 | 8.5162 | 3.307 | 5.0618 | 12.9515 | 0 | 1.4761 | 0.58519 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 747.75 | 74.75 | 822.5
42 | 25 | Envelope Glazing Test Medium OfficeCZ-16 Window U | 0018 CZ16 MediumOffice WinU-20 | 11064180.4795 | 2476683.7021 | 409760.2402 | 179421.7558 | 271483.2198 | 694560.2887 | 0 | 80422.2714 | 29751.9753 | 0 | 811293.429 | 367988.8889 | 12213.6101 | 206.3141 | 6.8619 | 0.22775 | 46.1828 | 7.6408 | 3.3457 | 5.0624 | 12.9515 | 0 | 1.4996 | 0.55479 | 0 | 15.1282 | 0.6156% | 1.793% | 53627.8468 | 21287.4627 | 7027.0036 | 724.5 | 88.5 | 813
43 | 26 | Envelope Glazing Test Medium OfficeCZ-16 Window SHGC | 0019 CZ16 MediumOffice WinSHGC-20 | 10984772.3723 | 2512738.6603 | 463691.0268 | 166398.7504 | 271454.7853 | 694560.2887 | 0 | 74128.7666 | 31221.0916 | 0 | 811293.429 | 362750 | 12753.0537 | 204.8334 | 6.7642 | 0.23781 | 46.8551 | 8.6465 | 3.1028 | 5.0618 | 12.9515 | 0 | 1.3823 | 0.58218 | 0 | 15.1282 | 1.329% | 0.3631% | 53627.8468 | 21287.4627 | 7027.0036 | 796.5 | 46 | 842.5
44 | 27 | Envelope Glazing Test Medium OfficeCZ-16 Window U&SHGC | 0020 CZ16 MediumOffice WinU_SHGC-20 | 10910103.35 | 2466039.7173 | 415627.2274 | 168370.2097 | 271483.2198 | 694560.2887 | 0 | 75228.2343 | 29486.5865 | 0 | 811293.429 | 363150 | 12272.2947 | 203.441 | 6.7717 | 0.22884 | 45.9843 | 7.7502 | 3.1396 | 5.0624 | 12.9515 | 0 | 1.4028 | 0.54984 | 0 | 15.1282 | 2% | 2.215% | 53627.8468 | 21287.4627 | 7027.0036 | 764 | 51.5 | 815.5
45 |  | Medium Office CZ-6 Baseline | 0025 CZ06 MediumOffice Base | 11225233.5421 | 2220792.0717 | 36187.6526 | 329669.7047 | 271454.7853 | 694560.2887 | 0 | 67209.7026 | 10425.9869 | 0 | 811293.429 | 402477.7778 | 8476.9439 | 209.3173 | 7.505 | 0.15807 | 41.4112 | 0.67479 | 6.1474 | 5.0618 | 12.9515 | 0 | 1.2533 | 0.19441 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 181.25 | 64.5 | 245.75
46 | 28 | Envelope Glazing Test Medium OfficeCZ-6 Window U | 0030 CZ06 MediumOffice WinU-20 | 11250653.9937 | 2219569.3878 | 29714.0626 | 334456.1805 | 271483.2198 | 694560.2887 | 0 | 68830.4697 | 9241.2156 | 0 | 811293.429 | 404016.6667 | 8412.1917 | 209.7913 | 7.5337 | 0.15686 | 41.3884 | 0.55408 | 6.2366 | 5.0624 | 12.9515 | 0 | 1.2835 | 0.17232 | 0 | 15.1282 | -0.2265% | 0.05506% | 53627.8468 | 21287.4627 | 7027.0036 | 165.5 | 65.5 | 231
47 | 29 | Envelope Glazing Test Medium OfficeCZ-6 Window SHGC | 0031 CZ06 MediumOffice WinSHGC-20 | 11040352.3604 | 2201579.8214 | 38386.588 | 311973.9616 | 271454.7853 | 694560.2887 | 0 | 63200.4368 | 10719.8101 | 0 | 811293.429 | 396202.7778 | 8498.9388 | 205.8698 | 7.388 | 0.15848 | 41.0529 | 0.7158 | 5.8174 | 5.0618 | 12.9515 | 0 | 1.1785 | 0.19989 | 0 | 15.1282 | 1.647% | 0.8651% | 53627.8468 | 21287.4627 | 7027.0036 | 209.75 | 59.75 | 269.5
48 | 30 | Envelope Glazing Test Medium OfficeCZ-6 Window U&SHGC | 0032 CZ06 MediumOffice WinU_SHGC-20 | 11061744.5899 | 2199409.3205 | 31249.5261 | 316656.1775 | 271483.2198 | 694560.2887 | 0 | 64688.5094 | 9487.648 | 0 | 811293.429 | 397658.3333 | 8427.5502 | 206.2687 | 7.4151 | 0.15715 | 41.0124 | 0.58271 | 5.9047 | 5.0624 | 12.9515 | 0 | 1.2062 | 0.17692 | 0 | 15.1282 | 1.456% | 0.9628% | 53627.8468 | 21287.4627 | 7027.0036 | 195.75 | 62.75 | 258.5
49 |  | Large Office CZ-7 Baseline | 0049 CZ07 LargeOffice Base | 104292284.0115 | 17039484.1601 | 258346.4764 | 1653106.565 | 3073685.1883 | 7496853.2476 | 0 | 1270055.8075 | 840609.4084 | 0 | 2302664.5031 | 4243263.8889 | 25615.1338 | 209.1751 | 8.5106 | 0.051375 | 34.1755 | 0.51816 | 3.3156 | 6.1648 | 15.0362 | 0 | 2.5473 | 1.686 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 49903.1033 | 3.25 | 322.5 | 325.75
50 | 31 | Envelope Glazing Test Large OfficeCZ-7 WWR 20% | 0050 CZ07 LargeOffice WWR20 | 102825300.2684 | 16879151.4384 | 235759.9976 | 1578646.0624 | 3073685.1883 | 7496853.2476 | 0 | 1255743.7709 | 797862.8623 | 0 | 2302655.0249 | 4202897.2222 | 25389.1174 | 206.2328 | 8.4296 | 0.050922 | 33.8539 | 0.47285 | 3.1662 | 6.1648 | 15.0362 | 0 | 2.5186 | 1.6002 | 0 | 4.6183 | 1.407% | 0.9409% | 498588.4208 | 124748.7703 | 28752.8804 | 3 | 191 | 194
51 | 32 | Envelope Glazing Test Large OfficeCZ-7 WWR 60% | 0051 CZ07 LargeOffice WWR60 | 105474894.2236 | 17177173.5339 | 282961.2836 | 1715842.5714 | 3073685.1883 | 7496853.2476 | 0 | 1284367.844 | 871223.8971 | 0 | 2302664.5031 | 4276402.7778 | 25861.3439 | 211.547 | 8.577 | 0.051869 | 34.4516 | 0.56752 | 3.4414 | 6.1648 | 15.0362 | 0 | 2.576 | 1.7474 | 0 | 4.6184 | -1.134% | -0.8081% | 498588.4208 | 124748.7703 | 64961.5987 | 5.25 | 471.75 | 477
52 | 33 | Envelope Glazing Test Large OfficeCZ-7 WWR 60% with South overhang | 0052 CZ07 LargeOffice WWR60wSOverhg | 104616437.4213 | 17079557.8623 | 283710.059 | 1673266.6323 | 3073685.1883 | 7496853.2476 | 0 | 1247450.3723 | 855329.0062 | 0 | 2302664.5031 | 4247575 | 25868.8335 | 209.8252 | 8.5192 | 0.051884 | 34.2558 | 0.56903 | 3.356 | 6.1648 | 15.0362 | 0 | 2.502 | 1.7155 | 0 | 4.6184 | -0.3108% | -0.2352% | 498588.4208 | 124748.7703 | 64961.5987 | 5.25 | 475.5 | 480.75
53 |  | Large Office CZ-1 Baseline | 0065 CZ01 LargeOffice Base | 89859865.2583 | 17228365.1294 | 2667725.6942 | 135623.1328 | 3073685.1883 | 7496853.2476 | 0 | 1404968.0775 | 144409.3963 | 0 | 2302664.5031 | 3592875 | 49702.1917 | 180.2285 | 7.2061 | 0.099686 | 34.5543 | 5.3506 | 0.27201 | 6.1648 | 15.0362 | 0 | 2.8179 | 0.28964 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 49903.1033 | 140.5 | 206.5 | 347
54 | 34 | Envelope Glazing Test Large OfficeCZ-1 WWR 20% | 0066 CZ01 LargeOffice WWR20 | 89421888.5064 | 17042735.1724 | 2471650.7939 | 129860.4055 | 3073685.1883 | 7496853.2476 | 0 | 1427213.3422 | 138495.0183 | 0 | 2302664.5031 | 3595927.7778 | 47741.2336 | 179.3501 | 7.2122 | 0.095753 | 34.182 | 4.9573 | 0.26046 | 6.1648 | 15.0362 | 0 | 2.8625 | 0.27777 | 0 | 4.6184 | 0.4874% | 1.077% | 498588.4208 | 124748.7703 | 28752.8804 | 124.75 | 156 | 280.75
55 | 35 | Envelope Glazing Test Large OfficeCZ-1 WWR 60% | 0067 CZ01 LargeOffice WWR60 | 90264412.5051 | 17360414.9922 | 2779217.4065 | 137660.9393 | 3073685.1883 | 7496853.2476 | 0 | 1419507.5901 | 148342.8368 | 0 | 2302664.5031 | 3598902.7778 | 50817.2947 | 181.0399 | 7.2182 | 0.10192 | 34.8191 | 5.5742 | 0.2761 | 6.1648 | 15.0362 | 0 | 2.8471 | 0.29753 | 0 | 4.6184 | -0.4502% | -0.7665% | 498588.4208 | 124748.7703 | 64961.5987 | 151 | 240 | 391
57 |  | Medium Office CZ-15 Baseline | 0001 CZ15 MediumOffice Base | 15796829.7417 | 2720111.5391 | 18880.5144 | 802014.3007 | 271284.1783 | 694560.2887 | 0 | 115207.1549 | 6871.6732 | 0 | 811293.429 | 553886.1111 | 8303.829 | 294.5639 | 10.3283 | 0.15484 | 50.722 | 0.35207 | 14.9552 | 5.0586 | 12.9515 | 0 | 2.1483 | 0.12814 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 80.25 | 597 | 677.25
58 | 36 | Lighting Tests Medium OfficeCZ-15 low LPD | 0009 CZ15 MediumOffice LPD-20 | 15326996.8608 | 2651536.98 | 19705.1152 | 787417.919 | 217021.6557 | 694560.2887 | 0 | 114676.3774 | 6862.195 | 0 | 811293.429 | 533547.2222 | 8312.0771 | 285.803 | 9.9491 | 0.155 | 49.4433 | 0.36744 | 14.683 | 4.0468 | 12.9515 | 0 | 2.1384 | 0.12796 | 0 | 15.1282 | 2.974% | 2.521% | 53627.8468 | 21287.4627 | 7027.0036 | 85.25 | 624.25 | 709.5
59 | 37 | Lighting Tests Medium OfficeCZ-15 high LPD | 0010 CZ15 MediumOffice LPD+20 | 16271430.1421 | 2789074.7031 | 18065.3918 | 816857.1147 | 325537.2227 | 694560.2887 | 0 | 115851.6704 | 6919.064 | 0 | 811293.429 | 574336.1111 | 8295.6757 | 303.4138 | 10.7097 | 0.15469 | 52.008 | 0.33687 | 15.232 | 6.0703 | 12.9515 | 0 | 2.1603 | 0.12902 | 0 | 15.1282 | -3.004% | -2.535% | 53627.8468 | 21287.4627 | 7027.0036 | 75.5 | 571 | 646.5
60 |  | Medium Office CZ-16 Baseline | 0013 CZ16 MediumOffice Base | 11132717.1259 | 2521894.5724 | 456705.6156 | 177346.0366 | 271454.7853 | 694560.2887 | 0 | 79161.6748 | 31382.2205 | 0 | 811293.429 | 367480.5556 | 12683.182 | 207.5921 | 6.8524 | 0.2365 | 47.0258 | 8.5162 | 3.307 | 5.0618 | 12.9515 | 0 | 1.4761 | 0.58519 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 747.75 | 74.75 | 822.5
61 | 38 | Lighting Tests Medium OfficeCZ-16 low LPD | 0021 CZ16 MediumOffice LPD-20 | 10721639.4201 | 2464561.1228 | 461103.4865 | 172407.9101 | 217163.8283 | 694560.2887 | 0 | 77171.2592 | 30870.3993 | 0 | 811293.429 | 349388.8889 | 12727.1718 | 199.9267 | 6.5151 | 0.23732 | 45.9567 | 8.5982 | 3.2149 | 4.0495 | 12.9515 | 0 | 1.439 | 0.57564 | 0 | 15.1282 | 3.693% | 2.273% | 53627.8468 | 21287.4627 | 7027.0036 | 763.25 | 82.5 | 845.75
62 | 39 | Lighting Tests Medium OfficeCZ-16 high LPD | 0022 CZ16 MediumOffice LPD+20 | 11533397.2794 | 2573124.0806 | 446109.0217 | 182322.0758 | 325745.7424 | 694560.2887 | 0 | 81190.0032 | 31894.0416 | 0 | 811293.429 | 385597.2222 | 12577.2842 | 215.0636 | 7.1902 | 0.23453 | 47.9811 | 8.3186 | 3.3998 | 6.0742 | 12.9515 | 0 | 1.514 | 0.59473 | 0 | 15.1282 | -3.599% | -2.031% | 53627.8468 | 21287.4627 | 7027.0036 | 739.25 | 67 | 806.25
63 |  | Medium Office CZ-6 Baseline | 0025 CZ06 MediumOffice Base | 11225233.5421 | 2220792.0717 | 36187.6526 | 329669.7047 | 271454.7853 | 694560.2887 | 0 | 67209.7026 | 10425.9869 | 0 | 811293.429 | 402477.7778 | 8476.9439 | 209.3173 | 7.505 | 0.15807 | 41.4112 | 0.67479 | 6.1474 | 5.0618 | 12.9515 | 0 | 1.2533 | 0.19441 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 181.25 | 64.5 | 245.75
64 | 40 | Lighting Tests Medium OfficeCZ-6 low LPD | 0033 CZ06 MediumOffice LPD-20 | 10786517.4929 | 2156463.7327 | 37817.8978 | 320001.9715 | 217163.8283 | 694560.2887 | 0 | 65276.156 | 10359.6397 | 0 | 811293.429 | 383150 | 8493.1557 | 201.1365 | 7.1446 | 0.15837 | 40.2116 | 0.70519 | 5.9671 | 4.0495 | 12.9515 | 0 | 1.2172 | 0.19318 | 0 | 15.1282 | 3.908% | 2.897% | 53627.8468 | 21287.4627 | 7027.0036 | 191.5 | 67.25 | 258.75
65 | 41 | Lighting Tests Medium OfficeCZ-6 high LPD | 0034 CZ06 MediumOffice LPD+20 | 11668347.4621 | 2285215.1924 | 34585.8419 | 339422.7415 | 325745.7424 | 694560.2887 | 0 | 69162.2056 | 10454.4214 | 0 | 811293.429 | 421830.5556 | 8460.827 | 217.58 | 7.8659 | 0.15777 | 42.6125 | 0.64492 | 6.3292 | 6.0742 | 12.9515 | 0 | 1.2897 | 0.19494 | 0 | 15.1282 | -3.947% | -2.901% | 53627.8468 | 21287.4627 | 7027.0036 | 170.5 | 64.5 | 235
67 |  | Large Office CZ-7 Baseline | 0049 CZ07 LargeOffice Base | 104292284.0115 | 17039484.1601 | 258346.4764 | 1653106.565 | 3073685.1883 | 7496853.2476 | 0 | 1270055.8075 | 840609.4084 | 0 | 2302664.5031 | 4243263.8889 | 25615.1338 | 209.1751 | 8.5106 | 0.051375 | 34.1755 | 0.51816 | 3.3156 | 6.1648 | 15.0362 | 0 | 2.5473 | 1.686 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 49903.1033 | 3.25 | 322.5 | 325.75
68 | 42 | Daylighting Tests Large OfficeCZ-7 Continuous Dimming | 0053 CZ07 LargeOffice BaseContDim | 100548331.0838 | 16522885.989 | 278023.1571 | 1611848.0915 | 2631812.9085 | 7496853.2476 | 0 | 1244170.9255 | 817075.1126 | 0 | 2302664.5031 | 4086102.7778 | 25811.7606 | 201.666 | 8.1953 | 0.05177 | 33.1393 | 0.55762 | 3.2328 | 5.2785 | 15.0362 | 0 | 2.4954 | 1.6388 | 0 | 4.6184 | 3.59% | 3.032% | 498588.4208 | 124748.7703 | 49903.1033 | 4 | 362.5 | 366.5
69 | 43 | Daylighting Tests Large OfficeCZ-7 Continuous Dimming and high VT | 0054 CZ07 LargeOffice BaseContDimVT+20 | 100572149.7248 | 16521208.3529 | 278516.0219 | 1613355.1205 | 2628647.1998 | 7496853.2476 | 0 | 1243706.4952 | 817008.7654 | 0 | 2302664.5031 | 4085466.6667 | 25816.6904 | 201.7138 | 8.1941 | 0.05178 | 33.136 | 0.55861 | 3.2358 | 5.2722 | 15.0362 | 0 | 2.4945 | 1.6386 | 0 | 4.6184 | 3.567% | 3.042% | 498588.4208 | 124748.7703 | 49903.1033 | 4 | 362.5 | 366.5
70 | 44 | Daylighting Tests Large OfficeCZ-7 Stepped Dimming | 0055 CZ07 LargeOffice BaseStDim | 99182934.3656 | 16325019.7146 | 285169.6972 | 1595185.4688 | 2462902.4431 | 7496853.2476 | 0 | 1236285.0882 | 807028.2525 | 0 | 2302664.5031 | 4026019.4444 | 25883.2439 | 198.9275 | 8.0748 | 0.051913 | 32.7425 | 0.57195 | 3.1994 | 4.9398 | 15.0362 | 0 | 2.4796 | 1.6186 | 0 | 4.6184 | 4.899% | 4.193% | 498588.4208 | 124748.7703 | 49903.1033 | 4.5 | 379.25 | 383.75
71 | 45 | Daylighting Tests Large OfficeCZ-7 Stepped Dimming and high VT | 0056 CZ07 LargeOffice BaseStDimVT+20 | 99105601.9775 | 16311465.9317 | 286553.51 | 1591536.3734 | 2453481.1422 | 7496853.2476 | 0 | 1234797.0155 | 806781.8201 | 0 | 2302664.5031 | 4021641.6667 | 25897.0856 | 198.7724 | 8.0661 | 0.051941 | 32.7153 | 0.57473 | 3.1921 | 4.9209 | 15.0362 | 0 | 2.4766 | 1.6181 | 0 | 4.6184 | 4.973% | 4.273% | 498588.4208 | 124748.7703 | 49903.1033 | 4.5 | 379.75 | 384.25
72 |  | Large Office CZ-7 WWR 20% Baseline | 0050 CZ07 LargeOffice WWR20 | 102825300.2684 | 16879151.4384 | 235759.9976 | 1578646.0624 | 3073685.1883 | 7496853.2476 | 0 | 1255743.7709 | 797862.8623 | 0 | 2302655.0249 | 4202897.2222 | 25389.1174 | 206.2328 | 8.4296 | 0.050922 | 33.8539 | 0.47285 | 3.1662 | 6.1648 | 15.0362 | 0 | 2.5186 | 1.6002 | 0 | 4.6183 |  |  | 498588.4208 | 124748.7703 | 28752.8804 | 3 | 191 | 194
73 | 46 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Continuous Dimming | 0057 CZ07 LargeOffice WWR20ContDim | 99257574.9534 | 16381395.869 | 249209.5206 | 1528061.0697 | 2659716.6406 | 7496853.2476 | 0 | 1235507.8783 | 775247.9489 | 0 | 2302664.5031 | 4053080.5556 | 25523.5517 | 199.0772 | 8.1291 | 0.051192 | 32.8555 | 0.49983 | 3.0648 | 5.3345 | 15.0362 | 0 | 2.478 | 1.5549 | 0 | 4.6184 | 3.47% | 2.949% | 498588.4208 | 124748.7703 | 28752.8804 | 3.25 | 212.25 | 215.5
74 | 47 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Continuous Dimming and high VT | 0058 CZ07 LargeOffice WWR20ContDimVT+20 | 99099877.1629 | 16370391.7138 | 250839.7659 | 1527719.8556 | 2649347.5228 | 7496853.2476 | 0 | 1234105.1091 | 774840.3876 | 0 | 2302664.5031 | 4049377.7778 | 25539.8582 | 198.7609 | 8.1217 | 0.051224 | 32.8335 | 0.5031 | 3.0641 | 5.3137 | 15.0362 | 0 | 2.4752 | 1.5541 | 0 | 4.6184 | 3.623% | 3.014% | 498588.4208 | 124748.7703 | 28752.8804 | 3.25 | 212 | 215.25
75 | 48 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Stepped Dimming | 0059 CZ07 LargeOffice WWR20StDim | 98273049.0135 | 16246502.5553 | 249512.8221 | 1516630.3969 | 2548310.2319 | 7496853.2476 | 0 | 1231043.6602 | 768537.4046 | 0 | 2302655.0249 | 4013458.3333 | 25526.5854 | 197.1025 | 8.0496 | 0.051198 | 32.585 | 0.50044 | 3.0418 | 5.111 | 15.0362 | 0 | 2.4691 | 1.5414 | 0 | 4.6183 | 4.427% | 3.748% | 498588.4208 | 124748.7703 | 28752.8804 | 3.25 | 221.75 | 225
76 | 49 | Daylighting Tests Large OfficeCZ-7 WWR-20%,Stepped Dimming and high VT | 0060 CZ07 LargeOffice WWR20StDimVT+20 | 98055761.969 | 16214608.5137 | 252214.1005 | 1517132.7399 | 2516292.974 | 7496853.2476 | 0 | 1230143.2341 | 766471.1636 | 0 | 2302664.5031 | 4003316.6667 | 25553.6998 | 196.6667 | 8.0293 | 0.051252 | 32.521 | 0.50586 | 3.0429 | 5.0468 | 15.0362 | 0 | 2.4673 | 1.5373 | 0 | 4.6184 | 4.638% | 3.937% | 498588.4208 | 124748.7703 | 28752.8804 | 3.25 | 222 | 225.25
77 |  | Large Office CZ-7 WWR 60% Baseline | 0051 CZ07 LargeOffice WWR60 | 105474894.2236 | 17177173.5339 | 282961.2836 | 1715842.5714 | 3073685.1883 | 7496853.2476 | 0 | 1284367.844 | 871223.8971 | 0 | 2302664.5031 | 4276402.7778 | 25861.3439 | 211.547 | 8.577 | 0.051869 | 34.4516 | 0.56752 | 3.4414 | 6.1648 | 15.0362 | 0 | 2.576 | 1.7474 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 64961.5987 | 5.25 | 471.75 | 477
78 | 50 | Daylighting Tests Large OfficeCZ-7WWR-60%,Continuous Dimming | 0061 CZ07 LargeOffice WWR60ContDim | 101790445.2465 | 16660480.5811 | 300856.0683 | 1673863.757 | 2633082.9833 | 7496853.2476 | 0 | 1259923.6439 | 847462.1252 | 0 | 2302664.5031 | 4119736.1111 | 26040.1471 | 204.1573 | 8.2628 | 0.052228 | 33.4153 | 0.60342 | 3.3572 | 5.2811 | 15.0362 | 0 | 2.527 | 1.6997 | 0 | 4.6184 | 3.493% | 3.008% | 498588.4208 | 124748.7703 | 64961.5987 | 6.25 | 516.25 | 522.5
79 | 51 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Continuous Dimming and high VT | 0062 CZ07 LargeOffice WWR60ContDimVT+20 | 101728827.6641 | 16652187.1825 | 301311.0205 | 1669181.5411 | 2629632.9294 | 7496853.2476 | 0 | 1259402.3445 | 847471.6034 | 0 | 2302664.5031 | 4117172.2222 | 26044.6978 | 204.0337 | 8.2577 | 0.052237 | 33.3987 | 0.60433 | 3.3478 | 5.2742 | 15.0362 | 0 | 2.5259 | 1.6997 | 0 | 4.6184 | 3.552% | 3.056% | 498588.4208 | 124748.7703 | 64961.5987 | 6.25 | 516 | 522.25
80 | 52 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Stepped Dimming | 0063 CZ07 LargeOffice WWR60StDim | 100346180.6767 | 16455799.5026 | 306997.9224 | 1648376.9582 | 2466267.1934 | 7496853.2476 | 0 | 1252710.7566 | 837841.7828 | 0 | 2302664.5031 | 4057952.7778 | 26101.4863 | 201.2606 | 8.1389 | 0.052351 | 33.0048 | 0.61573 | 3.3061 | 4.9465 | 15.0362 | 0 | 2.5125 | 1.6804 | 0 | 4.6184 | 4.862% | 4.2% | 498588.4208 | 124748.7703 | 64961.5987 | 6.25 | 530 | 536.25
81 | 53 | Daylighting Tests Large OfficeCZ-7 WWR-60%,Stepped Dimming and high VT | 0064 CZ07 LargeOffice WWR60StDimVT+20 | 100260204.1977 | 16441591.7259 | 308457.5605 | 1644225.5198 | 2456172.9425 | 7496853.2476 | 0 | 1251326.9438 | 837964.999 | 0 | 2302664.5031 | 4053361.1111 | 26116.0864 | 201.0881 | 8.1297 | 0.05238 | 32.9763 | 0.61866 | 3.2978 | 4.9263 | 15.0362 | 0 | 2.5097 | 1.6807 | 0 | 4.6184 | 4.944% | 4.282% | 498588.4208 | 124748.7703 | 64961.5987 | 6.25 | 530 | 536.25
82 |  | Large Office CZ-1 Baseline | 0065 CZ01 LargeOffice Base | 89859865.2583 | 17228365.1294 | 2667725.6942 | 135623.1328 | 3073685.1883 | 7496853.2476 | 0 | 1404968.0775 | 144409.3963 | 0 | 2302664.5031 | 3592875 | 49702.1917 | 180.2285 | 7.2061 | 0.099686 | 34.5543 | 5.3506 | 0.27201 | 6.1648 | 15.0362 | 0 | 2.8179 | 0.28964 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 49903.1033 | 140.5 | 206.5 | 347
83 | 54 | Daylighting Tests Large OfficeCZ-1 Continuous Dimming | 0068 CZ01 LargeOffice BaseContDim | 86954891.4939 | 16987050.9243 | 2909400.0698 | 130419.6175 | 2639812.4839 | 7496853.2476 | 0 | 1365387.2401 | 140144.2198 | 0 | 2302664.5031 | 3451375 | 52117.8373 | 174.4021 | 6.9223 | 0.10453 | 34.0703 | 5.8353 | 0.26158 | 5.2946 | 15.0362 | 0 | 2.7385 | 0.28108 | 0 | 4.6184 | 3.233% | 1.401% | 498588.4208 | 124748.7703 | 49903.1033 | 144.5 | 210.25 | 354.75
84 | 55 | Daylighting Tests Large OfficeCZ-1 Continuous Dimming and high VT | 0069 CZ01 LargeOffice BaseContDimVT+20 | 86922703.629 | 16984965.7269 | 2913902.2005 | 130419.6175 | 2634296.189 | 7496853.2476 | 0 | 1364306.7287 | 140153.698 | 0 | 2302664.5031 | 3449444.4444 | 52162.8699 | 174.3376 | 6.9184 | 0.10462 | 34.0661 | 5.8443 | 0.26158 | 5.2835 | 15.0362 | 0 | 2.7363 | 0.2811 | 0 | 4.6184 | 3.269% | 1.413% | 498588.4208 | 124748.7703 | 49903.1033 | 144.5 | 210 | 354.5
85 | 56 | Daylighting Tests Large OfficeCZ-1 Stepped Dimming | 0070 CZ01 LargeOffice BaseStDim | 85912321.2417 | 16903462.9441 | 2990267.8152 | 128523.9836 | 2487867.9426 | 7496853.2476 | 0 | 1356790.54 | 138163.2823 | 0 | 2302664.5031 | 3403197.2222 | 52926.0546 | 172.3111 | 6.8257 | 0.10615 | 33.9026 | 5.9975 | 0.25778 | 4.9898 | 15.0362 | 0 | 2.7213 | 0.27711 | 0 | 4.6184 | 4.393% | 1.886% | 498588.4208 | 124748.7703 | 49903.1033 | 146 | 213.25 | 359.25
86 | 57 | Daylighting Tests Large OfficeCZ-1 Stepped Dimming and high VT | 0071 CZ01 LargeOffice BaseStDimVT+20 | 85823795.135 | 16898174.1254 | 3004854.7186 | 128457.6364 | 2472247.9186 | 7496853.2476 | 0 | 1352743.3615 | 138021.1098 | 0 | 2302664.5031 | 3397375 | 53071.8656 | 172.1336 | 6.814 | 0.10644 | 33.892 | 6.0267 | 0.25764 | 4.9585 | 15.0362 | 0 | 2.7131 | 0.27682 | 0 | 4.6184 | 4.492% | 1.917% | 498588.4208 | 124748.7703 | 49903.1033 | 146.25 | 213 | 359.25
87 |  | Large Office CZ-1 WWR-20% Baseline | 0066 CZ01 LargeOffice WWR20 | 89421888.5064 | 17042735.1724 | 2471650.7939 | 129860.4055 | 3073685.1883 | 7496853.2476 | 0 | 1427213.3422 | 138495.0183 | 0 | 2302664.5031 | 3595927.7778 | 47741.2336 | 179.3501 | 7.2122 | 0.095753 | 34.182 | 4.9573 | 0.26046 | 6.1648 | 15.0362 | 0 | 2.8625 | 0.27777 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 28752.8804 | 124.75 | 156 | 280.75
88 | 58 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Continuous Dimming | 0072 CZ01 LargeOffice WWR20ContDim | 86770607.437 | 16845371.241 | 2714822.7203 | 126344.0045 | 2683288.8491 | 7496853.2476 | 0 | 1384684.794 | 134466.7961 | 0 | 2302655.0249 | 3466872.2222 | 50171.7636 | 174.0325 | 6.9534 | 0.10063 | 33.7861 | 5.445 | 0.2534 | 5.3818 | 15.0362 | 0 | 2.7772 | 0.26969 | 0 | 4.6183 | 2.965% | 1.158% | 498588.4208 | 124748.7703 | 28752.8804 | 129.5 | 165.75 | 295.25
89 | 59 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Continuous Dimming and high VT | 0073 CZ01 LargeOffice WWR20ContDimVT+20 | 86691578.4565 | 16843579.8669 | 2731125.1725 | 126268.1791 | 2668408.1224 | 7496853.2476 | 0 | 1381604.3888 | 134390.9707 | 0 | 2302664.5031 | 3461569.4444 | 50334.8292 | 173.874 | 6.9427 | 0.10095 | 33.7825 | 5.4777 | 0.25325 | 5.3519 | 15.0362 | 0 | 2.771 | 0.26954 | 0 | 4.6184 | 3.053% | 1.169% | 498588.4208 | 124748.7703 | 28752.8804 | 130 | 166 | 296
90 | 60 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Stepped Dimming | 0074 CZ01 LargeOffice WWR20StDim | 86098074.415 | 16770218.832 | 2729826.6632 | 124865.41 | 2601511.1994 | 7496853.2476 | 0 | 1379386.497 | 132874.4635 | 0 | 2302655.0249 | 3440455.5556 | 50321.6512 | 172.6837 | 6.9004 | 0.10093 | 33.6354 | 5.4751 | 0.25044 | 5.2178 | 15.0362 | 0 | 2.7666 | 0.2665 | 0 | 4.6183 | 3.717% | 1.599% | 498588.4208 | 124748.7703 | 28752.8804 | 130.25 | 171.75 | 302
91 | 61 | Daylighting Tests Large OfficeCZ-1 WWR-20%,Stepped Dimming and high VT | 0075 CZ01 LargeOffice WWR20StDimVT+20 | 85893345.9456 | 16768863.4537 | 2771236.7874 | 124571.5867 | 2563873.3868 | 7496853.2476 | 0 | 1374941.2353 | 132485.8586 | 0 | 2302655.0249 | 3427930.5556 | 50735.5723 | 172.273 | 6.8753 | 0.10176 | 33.6327 | 5.5582 | 0.24985 | 5.1423 | 15.0362 | 0 | 2.7577 | 0.26572 | 0 | 4.6183 | 3.946% | 1.607% | 498588.4208 | 124748.7703 | 28752.8804 | 130.25 | 171.5 | 301.75
92 |  | Large Office CZ-1 WWR-60% Baseline | 0067 CZ01 LargeOffice WWR60 | 90264412.5051 | 17360414.9922 | 2779217.4065 | 137660.9393 | 3073685.1883 | 7496853.2476 | 0 | 1419507.5901 | 148342.8368 | 0 | 2302664.5031 | 3598902.7778 | 50817.2947 | 181.0399 | 7.2182 | 0.10192 | 34.8191 | 5.5742 | 0.2761 | 6.1648 | 15.0362 | 0 | 2.8471 | 0.29753 | 0 | 4.6184 |  |  | 498588.4208 | 124748.7703 | 64961.5987 | 151 | 240 | 391
93 | 62 | Daylighting Tests Large OfficeCZ-1WWR-60%,Continuous Dimming | 0076 CZ01 LargeOffice WWR60ContDim | 87318076.0073 | 17081567.2343 | 2976609.7724 | 132694.3783 | 2641954.5503 | 7496853.2476 | 0 | 1385026.0081 | 143338.3631 | 0 | 2302664.5031 | 3459369.4444 | 52790.3879 | 175.1306 | 6.9383 | 0.10588 | 34.2599 | 5.9701 | 0.26614 | 5.2989 | 15.0362 | 0 | 2.7779 | 0.28749 | 0 | 4.6184 | 3.264% | 1.606% | 498588.4208 | 124748.7703 | 64961.5987 | 155.25 | 249.25 | 404.5
94 | 63 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Continuous Dimming and high VT | 0077 CZ01 LargeOffice WWR60ContDimVT+20 | 87282599.2175 | 17078534.22 | 2981073.9904 | 132675.422 | 2636021.2159 | 7496853.2476 | 0 | 1383500.0227 | 143328.8849 | 0 | 2302664.5031 | 3457175 | 52834.9465 | 175.0594 | 6.9339 | 0.10597 | 34.2538 | 5.979 | 0.2661 | 5.287 | 15.0362 | 0 | 2.7748 | 0.28747 | 0 | 4.6184 | 3.303% | 1.624% | 498588.4208 | 124748.7703 | 64961.5987 | 155.75 | 249 | 404.75
95 | 64 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Stepped Dimming | 0078 CZ01 LargeOffice WWR60StDim | 86278690.4202 | 16985629.1988 | 3038473.7872 | 132059.3409 | 2492796.5909 | 7496853.2476 | 0 | 1378912.5885 | 141452.2073 | 0 | 2302664.5031 | 3413138.8889 | 53408.6149 | 173.0459 | 6.8456 | 0.10712 | 34.0674 | 6.0942 | 0.26487 | 4.9997 | 15.0362 | 0 | 2.7656 | 0.28371 | 0 | 4.6184 | 4.416% | 2.159% | 498588.4208 | 124748.7703 | 64961.5987 | 157.75 | 252 | 409.75
96 | 65 | Daylighting Tests Large OfficeCZ-1 WWR-60%,Stepped Dimming and high VT | 0079 CZ01 LargeOffice WWR60StDimVT+20 | 86184704.8877 | 16978321.5299 | 3051089.2313 | 131983.5156 | 2476835.3528 | 7496853.2476 | 0 | 1374931.7572 | 141537.5108 | 0 | 2302664.5031 | 3407300 | 53534.8011 | 172.8574 | 6.8339 | 0.10737 | 34.0528 | 6.1195 | 0.26471 | 4.9677 | 15.0362 | 0 | 2.7576 | 0.28388 | 0 | 4.6184 | 4.52% | 2.201% | 498588.4208 | 124748.7703 | 64961.5987 | 158 | 250.25 | 408.25
97 |  | Stand Alone Retail CZ-7 Baseline | 0080 CZ07 SAloneRetail BaseStDim | 6896648.14 | 1113485.9192 | 65370.9377 | 145783.7309 | 194700.5657 | 264848.5009 | 0 | 235077.5693 | 0 | 0 | 207714.0929 | 246297.2222 | 2731.5377 | 279.3036 | 9.9747 | 0.11062 | 45.0945 | 2.6474 | 5.904 | 7.8851 | 10.726 | 0 | 9.5203 | 0 | 0 | 8.4121 |  |  | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
98 | 66 | Daylighting Tests Stand Alone Retail CZ-7 Skylight VT | 0081 CZ07 SAloneRetail BaseStDimSVT+20 | 6810766.4427 | 1103022.0197 | 65712.1518 | 144826.4358 | 185393.0028 | 264848.5009 | 0 | 234518.3573 | 0 | 0 | 207714.0929 | 243130.5556 | 2734.9507 | 275.8255 | 9.8464 | 0.11076 | 44.6707 | 2.6612 | 5.8652 | 7.5081 | 10.726 | 0 | 9.4976 | 0 | 0 | 8.4121 | 1.245% | 0.9397% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
99 | 67 | Daylighting Tests Stand Alone Retail CZ-7 SRR-5% | 0082 CZ07 SAloneRetail SkyLt5StDim | 6765138.5329 | 1097410.9431 | 68517.6901 | 149091.6122 | 166427.1849 | 264848.5009 | 0 | 240783.4276 | 0 | 0 | 207733.0492 | 240658.3333 | 2763.2027 | 273.9776 | 9.7463 | 0.11191 | 44.4434 | 2.7749 | 6.038 | 6.74 | 10.726 | 0 | 9.7514 | 0 | 0 | 8.4129 | 1.907% | 1.444% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
100 | 68 | Daylighting Tests Stand Alone Retail CZ-7 SRR-5% and high VT | 0083 CZ07 SAloneRetail SkyLt5StDimSVT+20 | 6745518.7213 | 1094870.7936 | 68792.557 | 148845.1798 | 164929.6341 | 264848.5009 | 0 | 239731.3508 | 0 | 0 | 207733.0492 | 239833.3333 | 2765.9521 | 273.1831 | 9.7129 | 0.11202 | 44.3406 | 2.786 | 6.028 | 6.6794 | 10.726 | 0 | 9.7087 | 0 | 0 | 8.4129 | 2.191% | 1.672% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
101 |  | Stand Alone Retail CZ-1 Baseline | 0084 CZ01 SAloneRetail BaseStDim | 6109524.0442 | 1234275.7162 | 272089.8227 | 19202.7722 | 201790.2367 | 264848.5009 | 0 | 268412.2928 | 0 | 0 | 207922.6126 | 221052.7778 | 4801.3326 | 247.4263 | 8.9523 | 0.19445 | 49.9863 | 11.0192 | 0.77768 | 8.1722 | 10.726 | 0 | 10.8703 | 0 | 0 | 8.4205 |  |  | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
102 | 69 | Daylighting Tests Stand Alone Retail CZ-1 Skylight VT | 0085 CZ01 SAloneRetail BaseStDimSVT+20 | 6031063.754 | 1224636.4174 | 273483.1137 | 19041.6433 | 191572.7696 | 264848.5009 | 0 | 267767.7773 | 0 | 0 | 207932.0908 | 217816.6667 | 4815.3638 | 244.2487 | 8.8212 | 0.19501 | 49.5959 | 11.0756 | 0.77116 | 7.7584 | 10.726 | 0 | 10.8442 | 0 | 0 | 8.4209 | 1.284% | 0.781% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
103 | 70 | Daylighting Tests Stand Alone Retail CZ-1 SRR-5% | 0086 CZ01 SAloneRetail SkyLt5StDim | 5875849.244 | 1210438.1189 | 287245.4164 | 19951.5476 | 166815.7899 | 264848.5009 | 0 | 263597.3825 | 0 | 0 | 207960.5253 | 209611.1111 | 4953.4007 | 237.9628 | 8.4889 | 0.20061 | 49.0209 | 11.633 | 0.80801 | 6.7558 | 10.726 | 0 | 10.6753 | 0 | 0 | 8.4221 | 3.825% | 1.931% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
104 | 71 | Daylighting Tests Stand Alone Retail CZ-1 SRR-5% and high VT | 0087 CZ01 SAloneRetail SkyLt5StDimSVT+20 | 5854817.1851 | 1207812.6659 | 288269.0587 | 19998.9384 | 164180.8586 | 264848.5009 | 0 | 262545.3057 | 0 | 0 | 207970.0035 | 208541.6667 | 4963.6397 | 237.111 | 8.4456 | 0.20102 | 48.9145 | 11.6745 | 0.80993 | 6.6491 | 10.726 | 0 | 10.6327 | 0 | 0 | 8.4225 | 4.169% | 2.144% | 24692.3029 | 12669.3378 | 903.5226 | 0 | 0 | 0
106 |  | Medium Office CZ-15 Baseline | 0001 CZ15 MediumOffice Base | 15796829.7417 | 2720111.5391 | 18880.5144 | 802014.3007 | 271284.1783 | 694560.2887 | 0 | 115207.1549 | 6871.6732 | 0 | 811293.429 | 553886.1111 | 8303.829 | 294.5639 | 10.3283 | 0.15484 | 50.722 | 0.35207 | 14.9552 | 5.0586 | 12.9515 | 0 | 2.1483 | 0.12814 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 80.25 | 597 | 677.25
107 | 72 | Equipment test Medium OfficeCZ-15 low EPD | 0011 CZ15 MediumOffice EPD-20 | 14511987.9893 | 2534367.844 | 20662.4103 | 760357.744 | 271284.1783 | 555648.231 | 0 | 108174.3528 | 6956.9767 | 0 | 811293.429 | 498927.7778 | 8321.6524 | 270.6055 | 9.3035 | 0.15517 | 47.2584 | 0.38529 | 14.1784 | 5.0586 | 10.3612 | 0 | 2.0171 | 0.12973 | 0 | 15.1282 | 8.134% | 6.829% | 53627.8468 | 21287.4627 | 7027.0036 | 92.25 | 648 | 740.25
108 | 73 | Equipment test Medium OfficeCZ-15 high EPD | 0012 CZ15 MediumOffice EPD+20 | 17083387.043 | 2906404.9681 | 17098.6185 | 844002.5932 | 271284.1783 | 833462.8683 | 0 | 122438.9985 | 6824.2823 | 0 | 811293.429 | 609005.5556 | 8286.0056 | 318.5544 | 11.3561 | 0.15451 | 54.1958 | 0.31884 | 15.7381 | 5.0586 | 15.5416 | 0 | 2.2831 | 0.12725 | 0 | 15.1282 | -8.144% | -6.849% | 53627.8468 | 21287.4627 | 7027.0036 | 70.5 | 552.5 | 623
109 |  | Medium Office CZ-16 Baseline | 0013 CZ16 MediumOffice Base | 11132717.1259 | 2521894.5724 | 456705.6156 | 177346.0366 | 271454.7853 | 694560.2887 | 0 | 79161.6748 | 31382.2205 | 0 | 811293.429 | 367480.5556 | 12683.182 | 207.5921 | 6.8524 | 0.2365 | 47.0258 | 8.5162 | 3.307 | 5.0618 | 12.9515 | 0 | 1.4761 | 0.58519 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 747.75 | 74.75 | 822.5
110 | 74 | Equipment test Medium OfficeCZ-16 low EPD | 0023 CZ16 MediumOffice EPD-20 | 10058451.8736 | 2380669.8412 | 476969.9428 | 162825.4804 | 271454.7853 | 555648.231 | 0 | 71806.615 | 30671.3577 | 0 | 811302.9071 | 320150 | 12885.9711 | 187.5602 | 5.9698 | 0.24029 | 44.3924 | 8.8941 | 3.0362 | 5.0618 | 10.3612 | 0 | 1.339 | 0.57193 | 0 | 15.1284 | 9.65% | 5.6% | 53627.8468 | 21287.4627 | 7027.0036 | 791 | 82.75 | 873.75
111 | 75 | Equipment test Medium OfficeCZ-16 high EPD | 0024 CZ16 MediumOffice EPD+20 | 12188414.6434 | 2652560.6224 | 425626.6966 | 191942.4182 | 271454.7853 | 833462.8683 | 0 | 86848.4706 | 31931.9543 | 0 | 811293.429 | 414883.3333 | 12372.3146 | 227.2777 | 7.7363 | 0.23071 | 49.4624 | 7.9367 | 3.5792 | 5.0618 | 15.5416 | 0 | 1.6195 | 0.59544 | 0 | 15.1282 | -9.483% | -5.181% | 53627.8468 | 21287.4627 | 7027.0036 | 722.5 | 64.25 | 786.75
112 |  | Medium Office CZ-6 Baseline | 0025 CZ06 MediumOffice Base | 11225233.5421 | 2220792.0717 | 36187.6526 | 329669.7047 | 271454.7853 | 694560.2887 | 0 | 67209.7026 | 10425.9869 | 0 | 811293.429 | 402477.7778 | 8476.9439 | 209.3173 | 7.505 | 0.15807 | 41.4112 | 0.67479 | 6.1474 | 5.0618 | 12.9515 | 0 | 1.2533 | 0.19441 | 0 | 15.1282 |  |  | 53627.8468 | 21287.4627 | 7027.0036 | 181.25 | 64.5 | 245.75
113 | 76 | Equipment test Medium OfficeCZ-6 low EPD | 0035 CZ06 MediumOffice EPD-20 | 10047485.6311 | 2049474.1511 | 39694.5755 | 300505.376 | 271454.7853 | 555648.231 | 0 | 60205.3351 | 10662.9411 | 0 | 811293.429 | 351241.6667 | 8512.022 | 187.3558 | 6.5496 | 0.15872 | 38.2166 | 0.74019 | 5.6035 | 5.0618 | 10.3612 | 0 | 1.1227 | 0.19883 | 0 | 15.1282 | 10.49% | 7.714% | 53627.8468 | 21287.4627 | 7027.0036 | 210.25 | 66.75 | 277
114 | 77 | Equipment test Medium OfficeCZ-6 high EPD | 0036 CZ06 MediumOffice EPD+20 | 12411018.9412 | 2393133.6346 | 33391.5925 | 358919.337 | 271454.7853 | 833462.8683 | 0 | 74451.0244 | 10170.0763 | 0 | 811293.429 | 453808.3333 | 8448.8815 | 231.4286 | 8.4622 | 0.15755 | 44.6248 | 0.62265 | 6.6928 | 5.0618 | 15.5416 | 0 | 1.3883 | 0.18964 | 0 | 15.1282 | -10.56% | -7.76% | 53627.8468 | 21287.4627 | 7027.0036 | 153.75 | 62.75 | 216.5
115 |  | Fast food Restaurant CZ-6 Baseline | 0088 CZ06 QSRest Base | 6477532.9461 | 1091885.1701 | 50708.2089 | 120894.0568 | 51788.7202 | 614441.3188 | 0 | 101369.0269 | 0 | 62612.7902 | 90080.5265 | 260872.2222 | 2018.0311 | 2590.0943 | 104.3119 | 0.80693 | 436.5992 | 20.2761 | 48.3405 | 20.7081 | 245.6894 | 0 | 40.5332 | 0 | 25.0362 | 36.0194 |  |  | 2500.8869 | 2000.9033 | 280.0769 | 22.33 | 75.33 | 97.66
116 | 78 | Equipment test Fast food RestaurantCZ-6 high Process load | 0089 CZ06 QSRest ProsLoad5h | 6697483.3563 | 1123826.6026 | 49713.001 | 125282.4495 | 51788.7202 | 641567.8409 | 0 | 102752.8397 | 0 | 62650.7029 | 90080.5265 | 270522.2222 | 2008.1713 | 2678.0432 | 108.1705 | 0.80298 | 449.3712 | 19.8781 | 50.0952 | 20.7081 | 256.5361 | 0 | 41.0866 | 0 | 25.0514 | 36.0194 | -3.396% | -2.925% | 2500.8869 | 2000.9033 | 280.0769 | 21.17 | 73 | 94.17
117

## Zonelvl
LARGE OFFICE
Baseline Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2
| Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
WWR20 Case Daylighting | Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
WWR60 Case Daylighting | Perimeter_ZN_1 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_2 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
| Perimeter_ZN_3 | 1901.26 | 1471.24 | 0 | X: 119.93 ft, Y: 8.20 ft, Z: 2.50 ft | X: 119.93 ft, Y: 14.75ft, Z: 2.50 ft | 0.563 | 0.436 | 287.5 lux | 287.5 lux
| Perimeter_ZN_4 | 1239.39 | 934.46 | 0 | X: 231.65 ft, Y: 79.95 ft, Z: 2.50 ft | X: 225.08 ft, Y: 79.95 ft, Z: 2.50 ft | 0.57 | 0.429 | 287.5 lux | 287.5 lux
STAND ALONE RETAIL
Name | Area [ft2] | Conditioned
BACK_SPACE | 4089 | Yes
CORE_RETAIL | 17227 | Yes
POINT_OF_SALE | 1623 | Yes
FRONT_RETAIL | 1623 | Yes
FRONT_ENTRY | 129 | Yes
Conditioned Total | 24692
Unconditioned Total | 0
Baseline Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2 | SRR3.04 Case Daylighting | Zone | Prim. Daylit Area [ft2] | Sec. Daylit Area [ft2] | Skylit Area [ft2] | Ref.Pt 1 Location | Ref.Pt 2 Location | Ref.Pt 1 Ctrl Fraction | Ref. Pt 2 Ctrl Fraction | Illum. Setpt in Ref. Pt 1 | Illum. Setpt in Ref. Pt 2
| Core_Retail | NA | NA | 16742.62 | UnderSkylight | NA | 0.97 |  | 550 lux |  |  | Core_Retail | NA | NA | 16934.71 | UnderSkylight | NA | 0.97 |  | 550 lux
| Point_Of_Sale | 718.07 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux |  |  | Point_Of_Sale | 717.0473 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux
| Front_Retial | 718.07 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux |  |  | Front_Retial | 717.0473 | NA | NA | In Prim. Daylit Zn | NA | 0.44172 |  | 550 lux
| Front_Entry | 114.3 | NA | NA | In Prim. Daylit Zn | NA | 0.88 |  | 550 lux |  |  | Front_Entry | 85.9294 | NA | NA | In Prim. Daylit Zn | NA | 0.88 |  | 550 lux
Baseline Skylight Layout | [10 empty] | TestCase Skylight Layout
STRIP MALL
Name | Area [ft2] | Conditioned
LGSTORE1 | 3750.0388 | Yes
SMSTORE1 | 1874.9656 | Yes
SMSTORE2 | 1874.9656 | Yes
SMSTORE3 | 1874.9656 | Yes
SMSTORE4 | 1874.9656 | Yes
LGSTORE2 | 3750.0388 | Yes
SMSTORE5 | 1874.9656 | Yes
SMSTORE6 | 1874.9656 | Yes
SMSTORE7 | 1874.9656 | Yes
SMSTORE8 | 1874.9656 | Yes
Total | 18749.7632
Conditioned Total | 18749.7632
Unconditioned Total | 0
Skylight Layout

## ConstructionAssembly
Name | Layers | Overall UFactor All Climate Zones | Overall CFactor All Climate Zones | Overall FFactor All Climate Zones | Material Name | Thickness (in) | Conductivity (Btu/h*ft*F) | Density (lb/ft³) | Specific Heat (Btu/lb*F) | Rvalue (ft2*F*hr/Btu)
NACM MetalFrameWall |  | 0.053 | NA | NA | Stucco - 7/8 in | 0.875 | 0.405 | 115.866 | 0.20063 | 0.18
Outside Layer | Stucco - 7/8 in |  |  |  | Building Paper - 1/16 in | 0.06 | 0.1667 | 70 | 0.3 | 0.03
Layer 2 | Building Paper - 1/16 in |  |  |  | Expanded Polystyrene - EPS - 4 1/16 in | 4.05 | 0.02 | 1 | 0.27 | 16.88
Layer 3 | Expanded Polystyrene - EPS - 4 1/16 in |  |  |  | Gypsum Board - 1/2 in | 0.5 | 0.092 | 40 | 0.27 | 0.45
Layer 4 | Air - Metal Wall Framing - 16 or 24 in OC |  |  |  | Composite Wood Frame 24 in OC 2x12 R13 |  |  |  |  | 12.85
Layer 5 | Gypsum Board - 1/2 in |  |  |  | Metal Standing Seam - 1/16 in | 0.0625 | 0.333 | 488.22 | 0.12
NACM Roof |  | 0.065 | NA | NA | Expanded Polystyrene - EPS - 3 1/2 in | 3.5 | 0.02 | 1 | 0.27 | 14.58
Outside Layer | Metal Standing Seam - 1/16 in |  |  |  | Expanded Polystyrene - EPS - 1 1/2 in | 1.5 | 0.02 | 1 | 0.27 | 6.25
Layer 2 | Expanded Polystyrene - EPS- 3 1/2 in |  |  |  | Carpet - 3/4 in | 0.75 | 0.0263 | 18 | 0.33 | 2.38
NACM BasementWall |  | NA | 1.14 | NA | Acoustic Tile - 3/4 in | 0.75 | 0.0333 | 18 | 0.19 | 1.89
Layer 2 | Concrete - Solid Grout - 115 lb/ft3 - 8 in |  |  |  | Concrete - Solid Grout - 115 lb/ft3 - 8 in | 8 | 0.433 | 115 | 0.2 | 1.538
NACM Interior wall |  | 0.42 | NA | NA | NA
Outside Layer | Gypsum Board - 1/2 in |  |  |  | NA
Layer 2 | Gypsum Board - 1/2 in |  |  |  | Expanded Polystyrene - EPS - 2 in | 2 | 0.02 | 1 | 0.27 | 8.33
NACM Interior Floor slab |  | 0.238 | NA | NA | NA
Outside Layer | Concrete - 140 lb/ft3 - 4 in |  |  |  | Concrete - 140 lb/ft3 - 4 in | 4 | 1.128 | 139.78 | 0.22 | 0.3
Layer 2 | Carpet - 3/4 in |  |  |  | Expanded Polystyrene - EPS - 1 7/8 in | 1.9 | 0.02 | 1 | 0.27 | 8
Drop Ceiling |  | 0.292 | NA | NA | Plywood - 5/8 in | 0.63 | 0.0667 | 30 | 0.45 | 0.78
Outside Layer | Acoustic Tile- 3/4 in. |  |  |  | Asphalt shingles - 1/4 in | 0.3 | 0.0467 | 69.89 | 0.3 | 0.45
NACM Floor Slab |  | NA | NA | 0.72 | Air - Metal Wall Framing - 16 or 24 in OC | 5.5 | 0.705 | 0.08 | 0.24 | 0.65
MetalFramedWallMassHeavy |  | 0.053 | NA | NA | Expanded Polystyrene - EPS - 1 in | 1 | 0.02 | 1 | 0.27 | 4.17
Outside Layer | Stucco - 7/8 in |  |  |  | Expanded Polystyrene - EPS - 4 1/16 in | 4.05 | 0.02 | 1 | 0.27 | 16.88
Layer 2 | Expanded Polystyrene - EPS - 2 in |  |  |  | Continuous Insulation - R5 |  |  |  |  | 5
Layer 3 | Expanded Polystyrene - EPS - 1 7/8 in |  |  |  | 12 in Horizontal Insulation - R5 |  |  |  |  | 5
Layer 4 | Concrete - 140 lb/ft3 - 4 in |  |  |  | Compliance insulation R24.86 |  |  |  |  | 24.86
Layer 5 | Air - Metal Wall Framing - 16 or 24 in OC
Layer 6 | Gypsum Board - 1/2 in |  |  |  | Outside Air Film | ** All construction assembley Ufactors in this tab include air films ** |  |  |  | Rvalue (ft2*F*hr/Btu)
NACMRoofWoodFrame |  | 0.065 | NA | NA | Exterior Wall |  |  |  |  | 0.17
Outside Layer | Asphalt shingles - 1/4 in |  |  |  | Roof |  |  |  |  | 0.17
Layer 2 | Building Paper - 1/16 in |  |  |  | Exterior Floor |  |  |  |  | 0.17
Layer 3 | Plywood - 5/8 in |  |  |  | Underground Wall |  |  |  |  | 0
Layer 4 | Composite Wood Frame 24 in OC 2x12 R13 |  |  |  | Underground Floor |  |  |  |  | 0
Layer 5 | Gypsum Board - 1/2 in |  |  |  | Interior Wall |  |  |  |  | 0.68
NACMMetalFramedWall - Insulation Sens. Test |  | 0.043 | NA | NA | Ceiling |  |  |  |  | 0.92
Outside Layer | Stucco - 7/8 in |  |  |  | Interior Floor |  |  |  |  | 0.61
Layer 2 | Building Paper - 1/16 in |  |  |  | Inside Air Film | ** All construction assembley Ufactors in this tab include air films ** |  |  |  | Rvalue (ft2*F*hr/Btu)
Layer 3 | Expanded Polystyrene - EPS - 4 1/16 in |  |  |  | Exterior Wall |  |  |  |  | 0.68
Layer 4 | Expanded Polystyrene - EPS - 1 in |  |  |  | Roof |  |  |  |  | 0.61
Layer 5 | Air - Metal Wall Framing - 16 or 24 in OC |  |  |  | Exterior Floor
Layer 6 | Gypsum Board - 1/2 in |  |  |  | Underground Wall
NACM Floor Slab - Insulation Sens. Test |  | NA | NA | 0.46 | Underground Floor
Outside Layer | Continuous Insulation - R5 |  |  |  | Interior Wall
Layer 2 | Concrete - 140 lb/ft3 - 4 in |  |  |  | Ceiling
Layer 3 | Carpet - 3/4 in |  |  |  | Interior Floor
NACM Roof - Insulation Sens. Test |  | 0.05 | NA | NA | Exterior Floor |  |  |  |  | 0.92
Outside Layer | Metal Standing Seam - 1/16 in |  |  |  | Underground Wall |  |  |  |  | 0.68
Layer 2 | Expanded Polystyrene - EPS - 1 1/2 in |  |  |  | Underground Floor |  |  |  |  | 0.92
Layer 3 | Expanded Polystyrene - EPS - 1 1/2 in |  |  |  | Interior Wall |  |  |  |  | 0.68
Layer 4 | Expanded Polystyrene - EPS - 1 1/2 in |  |  |  | Ceiling |  |  |  |  | 0.61
Layer 5 | Gypsum Board - 1/2 in |  |  |  | Interior Floor |  |  |  |  | 0.92
NACM_AtticRfWood |  | 0.039 | NA | NA
Outside Layer | Metal Standing Seam - 1/16 in
Layer 2 | Compliance insulation R24.86

## Schedules
Input | Schedule | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
DesignDay Schedules:
OnDay Schedules are 1 for every hour of the day; OffDay Schedules are 0 for every hour of the day. See columns AD and AE for design day schedule mapping.
For broken links, please refer to the RulesFormatDay tab of Appendix 5.4B.xls for hourly schedules, and RulesFormatWeek for design Day schedule references.
Medium Office Hourly Operation Schedules
Schedule Group | Office
Input | Schedule | Day of Week | App 5.4B Sch Name | Wk Schedule | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | WinterDesignDaty | SummerDesignDay
Interior Light | T24BLDG_LIGHT_SCH | WD | OfficeLightsWD | OfficeLightsWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | OffDay | OnDay
fraction | Lights | Sat | OfficeLightsSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sun | OfficeLightsSun |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Interior Equipment | T-24 BLDG_EQUIP_SCH_ADV | WD | OfficeReceptacleWD | OfficeReceptacleWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | OffDay | OnDay
fraction | Receptacle | Sat | OfficeReceptacleSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sun | OfficeReceptacleSun |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Occupancy | T24 BLDG_OCC_SCH | WD | OfficeOccupancyWD | OfficeOccupancyWk | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | OffDay | OnDay
fraction | Occupancy | Sat | OfficeOccupancySat |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  | Sun | OfficeOccupancySun |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Service Hot Water | T24 BLDG_SWH_SCH | WD | OfficeServiceHotWaterWD | OfficeServiceHotWaterWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | OffDay | OnDay
fraction | ServiceHotWater | Sat | OfficeServiceHotWaterSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sun | OfficeServiceHotWaterSun |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
temperature | WtrHtrSetPt | WD | OfficeWtrHtrSetPtWD | OfficeWtrHtrSetPtWk | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | OfficeWtrHtrSetPtWD | OfficeWtrHtrSetPtWD
|  | Sat | OfficeWtrHtrSetPtSat |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
|  | Sun | OfficeWtrHtrSetPtSun |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
Envelope Infiltration | T24 INFIL_SCH | WD | OfficeInfiltrationWD | OfficeInfiltrationWk | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | OfficeInfiltrationWD | OfficeInfiltrationWD
fraction | Infiltration | Sat | OfficeInfiltrationSat |  | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
|  | Sun | OfficeInfiltrationSun |  | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Fan operation | T24 HVACOperationSchd | WD | OfficeHVACAvailWD | OfficeHVACAvailWk | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OnDay | OnDay
fraction | HVACAvail | Sat | OfficeHVACAvailSat |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  | Sun | OfficeHVACAvailSun |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Heating Setpoint (◦C) | T24 HTGSETP_SCH | WD | OfficeHtgSetPtWD | OfficeHtgSetPtWk | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | OfficeHtgSetPtWD | OfficeHtgSetPtWD
temperature | HtgSetPt | Sat | OfficeHtgSetPtSat |  | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
|  | Sun | OfficeHtgSetPtSun |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint(◦C) | T24 CLGSETP_SCH | WD | OfficeClgSetPtWD | OfficeClgSetPtWk | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | OfficeClgSetPtWD | OfficeClgSetPtWD
temperature | ClgSetPt | Sat | OfficeClgSetPtSat |  | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85
|  | Sun | OfficeClgSetPtSun |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Large Office Operation Schedules
Input | Schedule | Day of Week |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Interior Light | T24BLDG_LIGHT_SCH | WD | OfficeLightsWD | OfficeLightsWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | OffDay | OnDay
fraction | Lights | Sat | OfficeLightsSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sun | OfficeLightsSun |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Interior Equipment | T-24 BLDG_EQUIP_SCH_ADV | WD | OfficeReceptacleWD | OfficeReceptacleWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | OffDay | OnDay
fraction | Receptacle | Sat | OfficeReceptacleSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Sun | OfficeReceptacleSun |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Occupancy | T24 BLDG_OCC_SCH | WD | OfficeOccupancyWD | OfficeOccupancyWk | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | OffDay | OnDay
fraction | Occupancy | Sat | OfficeOccupancySat |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  | Sun | OfficeOccupancySun |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Service Hot Water | T24 BLDG_SWH_SCH | WD | OfficeServiceHotWaterWD | OfficeServiceHotWaterWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | OffDay | OnDay
fraction | ServiceHotWater | Sat | OfficeServiceHotWaterSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  | Sun | OfficeServiceHotWaterSun |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
temperature | WtrHtrSetPt | WD | OfficeWtrHtrSetPtWD | OfficeWtrHtrSetPtWk | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | OfficeWtrHtrSetPtWD | OfficeWtrHtrSetPtWD
|  | Sat | OfficeWtrHtrSetPtSat |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
|  | Sun | OfficeWtrHtrSetPtSun |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
Envelope Infiltration | T24 INFIL_SCH | WD | OfficeInfiltrationWD | OfficeInfiltrationWk | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | OfficeInfiltrationWD | OfficeInfiltrationWD
fraction | Infiltration | Sat | OfficeInfiltrationSat |  | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
|  | Sun | OfficeInfiltrationSun |  | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Fan operation | T24 HVACOperationSchd | WD | OfficeHVACAvailWD | OfficeHVACAvailWk | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OnDay | OnDay
fraction | HVACAvail | Sat | OfficeHVACAvailSat |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  | Sun | OfficeHVACAvailSun |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Heating Setpoint (◦C) | T24 HTGSETP_SCH | WD | OfficeHtgSetPtWD | OfficeHtgSetPtWk | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | OfficeHtgSetPtWD | OfficeHtgSetPtWD
temperature | HtgSetPt | Sat | OfficeHtgSetPtSat |  | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
|  | Sun | OfficeHtgSetPtSun |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint(◦C) | T24 CLGSETP_SCH | WD | OfficeClgSetPtWD | OfficeClgSetPtWk | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | OfficeClgSetPtWD | OfficeClgSetPtWD
temperature | ClgSetPt | Sat | OfficeClgSetPtSat |  | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85
|  | Sun | OfficeClgSetPtSun |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Stand Alone Retail Hourly Operation Schedules
Input | Schedule | Day of Week |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Interior Lighting | Retail | WD | RetailLightsWD | RetailLightsWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05 | OffDay | OnDay
| Lights | Sat | RetailLightsSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun | RetailLightsSun |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Inerior Equipment | Retail | WD | RetailReceptacleWD | RetailReceptacleWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | OffDay | OnDay
| Receptacle | Sat | RetailReceptacleSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun | RetailReceptacleSun |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Occupancy | Retail | WD | RetailOccupancyWD | RetailOccupancyWk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | OffDay | OnDay
| Occupancy | Sat | RetailOccupancySat |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  | Sun | RetailOccupancySun |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
Service Hot Water | Retail | WD | RetailServiceHotWaterWD | RetailServiceHotWaterWk | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | OffDay | OnDay
fraction | ServiceHotWater | Sat | RetailServiceHotWaterSat |  | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
|  | Sun | RetailServiceHotWaterSun |  | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
temperature(F) | WtrHtrSetPt | WD | RetailWtrHtrSetPtWD | RetailWtrHtrSetPtWk | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | RetailWtrHtrSetPtWD | RetailWtrHtrSetPtWD
|  | Sat | RetailWtrHtrSetPtSat |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
|  | Sun | RetailWtrHtrSetPtSun |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
Infiltration | Retail | WD | RetailInfiltrationWD | RetailInfiltrationWk | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | RetailInfiltrationWD | RetailInfiltrationWD
fraction | Infiltration | Sat | RetailInfiltrationSat |  | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  | Sun | RetailInfiltrationSun |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
HVACOperation | Retail | WD | RetailHVACAvailWD | RetailHVACAvailWk | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | OnDay | OnDay
fraction | HVACAvail | Sat | RetailHVACAvailSat |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | Sun | RetailHVACAvailSun |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Heating Setpoint(◦C) | Retail | WD | RetailHtgSetPtWD | RetailHtgSetPtWk | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | RetailHtgSetPtWD | RetailHtgSetPtWD
temperature | HtgSetPt | Sat | RetailHtgSetPtSat |  | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  | Sun | RetailHtgSetPtSun |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint (◦C) | Retail | WD | RetailClgSetPtWD | RetailClgSetPtWk | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | RetailClgSetPtWD | RetailClgSetPtWD
temperature | ClgSetPt | Sat | RetailClgSetPtSat |  | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  | Sun | RetailClgSetPtSun |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85
Strip Mall Hourly Operation Schedules
Input | Schedule | Day of Week |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Interior Lighting | T24RetailLightSch | WD | RetailLightsWD | RetailLightsWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05 | OffDay | OnDay
fraction | Lights | Sat | RetailLightsSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun | RetailLightsSun |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Inerior Equipment | T24RetailReceptacleSch | WD | RetailReceptacleWD | RetailReceptacleWk | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | OffDay | OnDay
| Receptacle | Sat | RetailReceptacleSat |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  | Sun | RetailReceptacleSun |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Occupancy | T24RetailOccupancySch | WD | RetailOccupancyWD | RetailOccupancyWk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | OffDay | OnDay
| Occupancy | Sat | RetailOccupancySat |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  | Sun | RetailOccupancySun |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
Infiltration | T24RetailInfiltrationSch | WD | RetailInfiltrationWD | RetailInfiltrationWk | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | RetailInfiltrationWD | RetailInfiltrationWD
fraction | Infiltration | Sat | RetailInfiltrationSat |  | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  | Sun | RetailInfiltrationSun |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
HVACOperation | T24RetailHVACAvailSch | WD | RetailHVACAvailWD | RetailHVACAvailWk | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | OnDay | OnDay
fraction | HVACAvail | Sat | RetailHVACAvailSat |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | Sun | RetailHVACAvailSun |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Heating Setpoint(◦C) | T24RetailHtgSetPtSch | WD | RetailHtgSetPtWD | RetailHtgSetPtWk | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | RetailHtgSetPtWD | RetailHtgSetPtWD
| HtgSetPt | Sat | RetailHtgSetPtSat |  | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60
|  | Sun | RetailHtgSetPtSun |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60
Cooling Setpoint(◦C) | T24RetailClgSetPtSch | WD | RetailClgSetPtWD | RetailClgSetPtWk | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | RetailClgSetPtWD | RetailClgSetPtWD
temperature | ClgSetPt | Sat | RetailClgSetPtSat |  | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85
|  | Sun | RetailClgSetPtSun |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 85

## Test Criteria
|  | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 60 | 61 | 62 | 63 | 64 | 65 | 66 (To Be Completed) | 67 (To Be Completed) |  | 10 | 11 (VOID - Removed) | 12 | 13 | 14 | 15 | 16 (VOID - Removed) | 17 | 18 | 19 | 20 | 21 (VOID - Removed) | 22 | 23 | 24 | 30 | 31 | 32 | 33 | 34 | 35 | 36 (VOID - Removed) | 37 (VOID - Removed) | 38 (VOID - Removed) | 39 (VOID - Removed) | 40 (VOID - Removed) | 41 (VOID - Removed) | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 |  | 25 | 26 | 27 (Void - Removed) | 28 | 29 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 |  | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 |  | 110 | 111 | 112 | 113 | 114 | 115 |  | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 |  | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124
Test Run Name | Stand Alone Retail 0500 RetlMed | 050115--RetlMed-EnvelopeRoofInsulation | 050215--RetlMed-EnvelopeWallInsulation | 050315--RetlMed-EnvelopeHeavy | 050416--RetlMed-EnvelopeRoofInsulation | 050516--RetlMed-EnvelopeWallInsulation | 050616--RetlMed-EnvelopeHeavy | 050706--RetlMed-EnvelopeRoofInsulation | 050806--RetlMed-RetlMed-EnvelopeWallInsulation | 050906--RetlMed-RetlMed-EnvelopeHeavy | 056007--RetlMed-Daylighting SRRBaseHighVT | 056107--RetlMed-Daylighting SRR4.67 | 0562 07--RetlMed-Daylighting SRR4.67HighVT | 0563 01--RetlMed-Daylighting SRRBaseHighVT | 0564 01--RetlMed-Daylighting SRR4.67 | 056501--RetlMed-Daylighting SRR4.67HighVT | 0566 (To Be Completed)16--RetlMed-HVAC DuctLoss | 0567 (To Be Completed)06--RetlMed-HVAC DuctLoss | Medium Office 0300 OffMed | 031015-OffMed-FloorSlabInsulation | 0311 (VOID - Removed)15-OffMed-Envelope Infiltration | 031215-OffMed-GlazingWindowU | 031315-OffMed-GlazingWindowSHGC | 031415-OffMed-GlazingWindowUSHGC | 031516-OffMed-FloorSlabInsulation | 0316 (VOID - Removed)16-OffMed-Envelope Infiltration | 031716-OffMed-GlazingWindowU | 031816-OffMed-GlazingWindowSHGC | 031916-OffMed-GlazingWindowUSHGC | 032006-OffMed-FloorSlabInsulation | 0321 (VOID - Removed)06-OffMed-Envelope Infiltration | 032206-OffMed-GlazingWindowU | 032306-OffMed-GlazingWindowSHGC | 032406-OffMed-GlazingWindowUSHGC | 033015-OffMed-LightingLowLPD | 033115-OffMed-LightingHighLPD | 033216-OffMed-LightingLowLPD | 033316-OffMed-LightingHighLPD | 033406-OffMed-LightingLowLPD | 033506-OffMed-LightingHighLPD | 0336 (VOID - Removed)15-OffMed-Int.Eqpt LowEPD | 0337 (VOID - Removed)15-OffMed-37CZ15MediumOffice Int.Eqpt HighEPD | 0338 (VOID - Removed)16-OffMed-38CZ16MediumOffice Int.Eqpt LowEPD | 0339 (VOID - Removed)16-OffMed-39CZ16MediumOffice Int.Eqpt HighEPD | 0340 (VOID - Removed)06-OffMed-40CZ06MediumOffice Int.Eqpt LowEPD | 0341 (VOID - Removed)06-OffMed-41CZ06MediumOffice Int.Eqpt HighEPD | 036815-OffMed-HVACPVAV Design | 036915-OffMed-HVACPVAV SATControl | 037015-OffMed-HVACPVAV VAVControl | 037115-OffMed-HVACPVAV EconomizerType | 037216-OffMed-HVACPVAV Design | 037316-OffMed-HVACPVAV SATControl | 037416-OffMed-HVACPVAV VAVControl | 037516-OffMed-HVACPVAV EconomizerType | 037606-OffMed-HVACPVAV Design | 037706-OffMed-HVACPVAV SATControl | 037806-OffMed-HVACPVAV VAVControl | 037906-OffMed-HVACPVAV EconomizerType | Large Office | 042507-OffLrg-WWR20 | 042607-OffLrg-WWR60 | 0427 (Void - Removed)07-OffLrg-27CZ07LargeOffice Glazing WWR60%SouthOverhang | 042801-OffLrg-WWR20 | 042901-OffLrg-WWR60 | 044207-OffLrg-Cont.DimHighVT | 044307-OffLrg-StepDim | 044407-OffLrg-StepDimHighVT | 044507-OffLrg-WWR20Cont.DimHighVT | 044607-OffLrg-WWR20StepDim | 044707-OffLrg-WWR20StepDimHighVT | 044807-OffLrg-WWR60Cont.DimHighVT | 044907-OffLrg-WWR60StepDim | 045007-OffLrg-WWR60StepDimHighVT | 045101-OffLrg-Cont.DimHighVT | 045201-OffLrg-StepDim | 045301-OffLrg-StepDimHighVT | 045401-OffLrg-WWR20Cont.DimHighVT | 045501-OffLrg-WWR20StepDim | 045601-OffLrg-WWR20StepDimHighVT | 045701-OffLrg-WWR60Cont.DimHighVT | 045801-OffLrg-WWR60StepDim | 045901-OffLrg-WWR60StepDimHighVT | 048015--OffLrg-HVACChillerCOP | 048115--OffLrg-HVACChWDeltaT | 048215--OffLrg-HVACVAV CWSetpoint | 048315--OffLrg-HVACTowerEff | 048416--OffLrg-HVACChillerCOP | 048516--OffLrg-HVACChWDeltaT | 048616--OffLrg-HVACVAV CWSetpoint | 048716--OffLrg-HVACTowerEff | 048806--OffLrg-HVACChillerCOP | 048906--OffLrg-HVACChWDeltaT | 049006--OffLrg-HVACVAV CWSetpoint | 049106--OffLrg-HVACTowerEff | Strip Mall 1000 RetlStrp | 109215--RetlStrp-HVACPSZ DXCOP | 109315--RetlStrp-HVACPSZ HeatEff | 109415--RetlStrp-HVACPSZ EconomizerControl | 109516--RetlStrp-HVACPSZ DXCOP | 109616--RetlStrp-HVACPSZ HeatEff | 109716--RetlStrp-HVACPSZ EconomizerControl | 109806--RetlStrp-HVACPSZ DXCOP | 109906--RetlStrp-HVACPSZ HeatEff | 1010006--RetlStrp-HVACPSZ EconomizerControl | 1010115--RetlStrp-HVACPTAC DXCOP | 1010216--RetlStrp-HVACPTAC DXCOP | 1010306--RetlStrp-HVACPTAC DXCOP | 1010415--RetlStrp-HVACPTAC vsFanCoil | 1010516--RetlStrp-HVACPTAC vsFanCoil | 10106 06--RetlStrp-HVACPTAC vsFanCoil | Simple Geometry Small Office 02000 OffSml-SG | 0211015-OffSml-SG-EnvRoofInsulation | 0211116-OffSml-SG-EnvRoofInsulation | 0211206-OffSml-SG-EnvRoofInsulation | 0211315-OffSml-SG-EnvWallInsulation | 0211416-OffSml-SG-EnvWallInsulation | 0211506-OffSml-SG-EnvWallInsulation | Simple Geometry Medium Office 03000 OffMed-SG | 0311615-OffMed-SG-WWR40 | 0311715-OffMed-SG-WWR20 | 0311816-OffMed-SG-WWR40 | 0311916-OffMed-SG-WWR20 | 0312006-OffMed-SG-WWR40 | 0312106-OffMed-SG-WWR20 | 0312215-OffMed-SG-WinUSHGC | 0312316-OffMed-SG-WinUSHGC | 0312406-OffMed-SG-WinUSHGC | Simple Geometry Medium Retail 05000 RetlMed-SG | 0511615RetlMed-SG-SRR5 | 0511716RetlMed-SG-SRR5 | 0511806RetlMed-SG-SRR5 | 0511915RetlMed-SG-SRR1 | 0512016RetlMed-SG-SRR1 | 0512106RetlMed-SG-SRR1 | 0512215RetlMed-SG-SkyUSHGC | 0512316RetlMed-SG-SkyUSHGC | 0512406RetlMed-SG-SkyUSHGC
Baseline |  | 050015-RetlMed-Baseline | 050015-RetlMed-Baseline | 050015-RetlMed-Baseline | 050016-RetlMed-Baseline | 050016-RetlMed-Baseline | 050016-RetlMed-Baseline | 050006-RetlMed-Baseline | 050006-RetlMed-Baseline | 050006-RetlMed-Baseline | 050007-RetlMed-Baseline | 050007-RetlMed-Baseline | 050007-RetlMed-Baseline | 050001-RetlMed-Baseline | 050001-RetlMed-Baseline | 050001-RetlMed-Baseline | 050016-RetlMed-Baseline | 050006-RetlMed-Baseline |  | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030015-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030016-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline | 030006-OffMed-Baseline |  | 040007-OffLrg-Baseline | 040007-OffLrg-Baseline | 040007-OffLrg-Baseline | 040001-OffLrg-Baseline | 040001-OffLrg-Baseline | 040007-OffLrg-Baseline | 040007-OffLrg-Baseline | 040007-OffLrg-Baseline | 042507-OffLrg-WWR20 | 042507-OffLrg-WWR20 | 042507-OffLrg-WWR20 | 042607-OffLrg-WWR60 | 042607-OffLrg-WWR60 | 042607-OffLrg-WWR60 | 040001-OffLrg-Baseline | 040001-OffLrg-Baseline | 040001-OffLrg-Baseline | 042801-OffLrg-WWR20 | 042801-OffLrg-WWR20 | 042801-OffLrg-WWR20 | 042901-OffLrg-WWR60 | 042901-OffLrg-WWR60 | 042901-OffLrg-WWR60 | 040015-OffLrg-Baseline | 040015-OffLrg-Baseline | 040015-OffLrg-Baseline | 040015-OffLrg-Baseline | 040016-OffLrg-Baseline | 040016-OffLrg-Baseline | 040016-OffLrg-Baseline | 040016-OffLrg-Baseline | 040006-OffLrg-Baseline | 040006-OffLrg-Baseline | 040006-OffLrg-Baseline | 040006-OffLrg-Baseline |  | 100015-RetlStrp-BaselinePSZ | 100015-RetlStrp-BaselinePSZ | 100015-RetlStrp-BaselinePSZ | 100016-RetlStrp-BaselinePSZ | 100016-RetlStrp-BaselinePSZ | 100016-RetlStrp-BaselinePSZ | 100006-RetlStrp-BaselinePSZ | 100006-RetlStrp-BaselinePSZ | 100006-RetlStrp-BaselinePSZ | 100015-RetlStrp-BaselinePTAC | 100016-RetlStrp-BaselinePTAC | 100006-RetlStrp-BaselinePTAC | 100015-RetlStrp-BaselinePTAC | 100016-RetlStrp-BaselinePTAC | 100006-RetlStrp-BaselinePTAC |  | 0200015-OffSml-SG-Baserun | 0200016-OffSml-SG-Baserun | 0200006-OffSml-SG-Baserun | 0200015-OffSml-SG-Baserun | 0200016-OffSml-SG-Baserun | 0200006-OffSml-SG-Baserun |  | 0300015-OffMed-SG-Baseline | 0300015-OffMed-SG-Baseline | 0300016-OffMed-SG-Baseline | 0300016-OffMed-SG-Baseline | 0300006-OffMed-SG-Baseline | 0300006-OffMed-SG-Baseline | 0300015-OffMed-SG-Baseline | 0300016-OffMed-SG-Baseline | 0300006-OffMed-SG-Baseline |  | 050015RetlMed-SG-Baseline | 050016RetlMed-SG-Baseline | 050006RetlMed-SG-Baseline | 050015RetlMed-SG-Baseline | 050016RetlMed-SG-Baseline | 050006RetlMed-SG-Baseline | 050015RetlMed-SG-Baseline | 050016RetlMed-SG-Baseline | 050006RetlMed-SG-Baseline
Test Description |  | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Change Roof and Wall construction asssembly to Wood Framed Roof and Heavy Mass wall. Roof and Wall assembly overall U value of test case= Baseline construction assembly U value | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Change Roof and Wall construction asssembly to Wood Framed Roof and Heavy Mass wall. Roof and Wall assembly overall U value of test case= Baseline construction assembly U value | Decrease overall U value of Roof by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Change Roof and Wall construction asssembly to Wood Framed Roof and Heavy Mass wall. Roof and Wall assembly overall U value of test case= Baseline construction assembly U value | Increase Visible Transmittance of skylights by 20% compared to baseline case | Increase skylight area such that overall SRR fraction is 0.0467. | Increase skylight area such that overall SRR fraction is 0.0467 and visible transmittance of skylights by 20% compared to baseline case. | Increase Visible Transmittance of skylights by 20% compared to baseline case | Increase skylight area such that overall SRR fraction is 0.0467. | Increase skylight area such that overallSRR fraction is 0.0467 and visible transmittance of skylights by 20% compared to baseline case | Increase ductloss in the zones served by Pacakaged Single Zone systems to 14%. The baseline for this test is a modified version of Stand-Alone Retail prototype. See details below | Increase ductloss in the zones served by Pacakaged Single Zone systems to 14%. The baseline for this test is a modified version of Stand-Alone Retail prototype. See details below |  | Change Floor slab F factor of permiter zones in the bottom floor to 0.46 | Increase Exterior Wall Infiltration by 10% compared to baseline case | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case | Change Floor slab F factor of permiter zones in the bottom floor to 0.46 | Increase Exterior Wall Infiltration by 10% compared to baseline case | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case | Change Floor slab F factor of permiter zones in the bottom floor to 0.46 | Increase Exterior Wall Infiltration by 10% compared to baseline case | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case | Decrease LPD by 20% compared to baseline case | Increase LPD by 20% compared to baseline case | Decrease LPD by 20% compared to baseline case | Increase LPD by 20% compared to baseline case | Decrease LPD by 20% compared to baseline case | Increase LPD by 20% compared to baseline case | Decrease EPD by 20% compared to baseline case | Increase EPD by 20% compared to baseline case | Decrease EPD by 20% compared to baseline case | Increase EPD by 20% compared to baseline case | Decrease EPD by 20% compared to baseline case | Increase EPD by 20% compared to baseline case | Change static pressure and motor efficiency of all VAV fans. See details below | Change supply air temperature reset based on Outside air. See details below | Change VAV damper control to dual maximum. | Change Economizer Type to Fixed Dry bulb with 70 F high limit | Change static pressure and motor efficiency of all VAV fans. See details below | Change supply air temperature reset based on Outside air. See details below | Change VAV damper control to dual maximum. | Change Economizer Type to Fixed Dry bulb with 70 F high limit | Change static pressure and motor efficiency of all VAV fans. See details below | Change supply air temperature reset based on Outside air. See details below | Change VAV damper control to dual maximum. | Change Economizer Type to Fixed Dry bulb with 70 F high limit |  | Reduce window area such that overall window to wall ratio is 20% | Increase window area such that overall window to wall ratio is 60% | Increase window area such that overall window to wall ratio is 60%. Include horizontal overhang of two feet for all south facing windows | Reduce window area such that overall window to wall ratio is 20% | Increase window area such that overall window to wall ratio is 60% | Increase Visible Transmittance of windows by 20% compared to baseline case | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20% | Increase Visible Transmittance of windows by 20% compared to baseline case. Reduce window area such that overall window to wall ratio is 20% Note for this test, 042507-OffLrg-WWR20 is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps.Reduce window area such that overall window to wall ratio is 20% Note for this test, 042507-OffLrg-WWR20is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20%. Reduce window area such that overall window to wall ratio is 0.2 Note for this test, 042507-OffLrg-WWR20 is the baseline | Increase Visible Transmittance of windows by 20% compared to baseline case. Increase window area such that overall window to wall ratio is 60% Note for this test, 042607-OffLrg-WWR60 is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps.Reduce window area such that overall window to wall ratio is 60% Note for this test, Run 26CZ07LargeOffice WWR60% is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20%. Reduce window area such that overall window to wall ratio is 60% Note for this test, 042607-OffLrg-WWR60 is the baseline | Increase Visible Transmittance of windows by 20% compared to baseline case | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20% | Increase Visible Transmittance of windows by 20% compared to baseline case. Reduce window area such that overall window to wall ratio is 20% Note for this test, 042801-OffLrgWWR20 is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps.Reduce window area such that overall window to wall ratio is 20% Note for this test, 042801-OffLrgWWR20 is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20%. Reduce window area such that overall window to wall ratio is 20% Note for this test,042801-OffLrgWWR20 is the baseline | Increase Visible Transmittance of windows by 20% compared to baseline case. Reduce window area such that overall window to wall ratio is 60% Note for this test, 042901-OffLrgWWR60 is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps.Reduce window area such that overall window to wall ratio is 60% Note for this test,042901-OffLrgWWR60 is the baseline | Change daylighting controls in Primary and Secondary daylit areas to Stepped dimming with 4 control steps and increase visible transmittance of windows by 20%. Reduce window area such that overall window to wall ratio is 60% Note for this test, Run 29CZ07LargeOffice WWR60% is the baseline | Increase Chiller COP by 18% compared to baseline case | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 80 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 25 gpm/hp | Increase Chiller COP by 18% compared to baseline case | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 80 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 80 gpm/hp | Increase Chiller COP by 18% compared to baseline case | Change the Chilled water loop design temperature difference to 12F. See below for details | Change condenser water setpoint reset (50F to 95F) based on Outdoor air wet bulb temperature | Change Tower Efficiency to 80 gpm/hp. Note: For this test run Ratio of Cooling Tower design water flow rate(gpm) to Fan Power (hp)= 25 gpm/hp |  | Increase COP of DX coil to 3.8 | Increase efficiency of the Heating coil to 90% | Change Economizer from Integrated as in baseline to NonIntegrated. See below for details | Increase COP of DX coil to 3.8 | Increase efficiency of the Heating coil to 90% | Change Economizer from Integrated as in baseline to NonIntegrated. See below for details | Increase COP of DX coil to 3.8 | Increase efficiency of the Heating coil to 90% | Change Economizer from Integrated as in baseline to NonIntegrated. See below for details | Increase COP of DX coil to 3.8 | Increase COP of DX coil to 3.8 | Increase COP of DX coil to 3.8 | Comparison of PTAC system with Fan Coil System. For details on Fan Coil system, refer StripMall FanCoil | Comparison of PTAC system with Fan Coil System. For details on Fan Coil system, refer StripMall FanCoil | Comparison of PTAC system with Fan Coil System. For details on Fan Coil system, refer StripMall FanCoil |  | Decrease overall U value of Roof by 20% compared to baserun case | Decrease overall U value of Roof by 20% compared to baserun case | Decrease overall U value of Roof by 20% compared to baserun case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case | Decrease overall U value of Exterior Wall by 20% compared to baseline case |  | Change WWR from 33% to 40% | Change WWR from 33% to 20% | Change WWR from 33% to 40% | Change WWR from 33% to 20% | Change WWR from 33% to 40% | Change WWR from 33% to 20% | Decrease U value of windows by 20% compared to baseline case | Decrease SHGC of windows by 20% compared to baseline case | Decrease U value & SHGC of windows by 20% compared to baseline case |  | Change SRR to 5% | Change SRR to 5% | Change SRR to 5% | Change SRR to 1% | Change SRR to 1% | Change SRR to 1% | Decrease U value of skylights by 20% compared to baseline case | Decrease U value of skylights by 20% compared to baseline case | Decrease U value of skylights by 20% compared to baseline case
Location |  | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ07 | CZ07 | CZ07 | CZ01 | CZ01 | CZ01 | CZ16 | CZ06 | CZ00 | CZ15 | CZ15 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ06 | CZ06 | CZ15 | CZ15 | CZ16 | CZ16 | CZ06 | CZ06 | CZ15 | CZ15 | CZ16 | CZ16 | CZ06 | CZ06 | CZ15 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ06 | CZ00 | CZ07 | CZ07 | CZ07 | CZ01 | CZ01 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ07 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ01 | CZ15 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ06 | CZ00 | CZ15 | CZ15 | CZ15 | CZ16 | CZ16 | CZ16 | CZ06 | CZ06 | CZ06 | CZ15 | CZ16 | CZ06 | CZ15 | CZ16 | CZ06 | CZ000 | CZ15 | CZ16 | CZ06 | CZ15 | CZ16 | CZ06 | CZ00 | CZ15 | CZ15 | CZ16 | CZ16 | CZ06 | CZ06 | CZ15 | CZ16 | CZ06 | CZ00 | CZ15 | CZ16 | CZ06 | CZ15 | CZ16 | CZ06 | CZ15 | CZ16 | CZ06
Fuel Type |  | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail | Refer StandAloneRetail Ductloss Baseline | Refer StandAloneRetail Ductloss Baseline |  | Refer MediumOffice | Refer MediumOffice | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer MediumOffice | Refer MediumOffice | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer MediumOffice | Refer MediumOffice | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office |  | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office | Refer Large Office |  | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PSZ | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC |  | Small Office | Small Office | Small Office | Small Office | Small Office | Small Office
Total Floor Area (sq feet)
Building shape
Aspect Ratio
Number of Floors
Window Fraction (Window-to-Wall Ratio) | [59 empty] | 20% of above-grade gross wall | 60% of above-grade gross wall | 60% of above-grade gross wall | 28: 20% of above-grade gross wall; 29: 60% of above-grade gross wall; 45: 20% of above-grade gross wall; 46: 20% of above-grade gross wall; 47: 20% of above-grade gross wall; 48: 60% of above-grade gross wall; 49: 60% of above-grade gross wall; 50: 60% of above-grade gross wall; 54: 20% of above-grade gross wall; 55: 20% of above-grade gross wall; 56: 20% of above-grade gross wall; 57: 60% of above-grade gross wall; 58: 60% of above-grade gross wall; 59: 60% of above-grade gross wall
Window Locations | [59 empty] | Refer Large Office | Refer Large Office | Refer Large Office | 28: Refer Large Office; 29: Refer Large Office; 45: Refer Large Office; 46: Refer Large Office; 47: Refer Large Office; 48: Refer Large Office; 49: Refer Large Office; 50: Refer Large Office; 54: Refer Large Office; 55: Refer Large Office; 56: Refer Large Office; 57: Refer Large Office; 58: Refer Large Office; 59: Refer Large Office
Shading Geometry | [61 empty] | 2 feet deep overhang on South windows
Azimuth | [61 empty] | Refer Large Office
Thermal Zoning
Floor to floor height (feet)
Floor to ceiling height (feet)
Glazing sill height (feet)
Exterior walls
Construction |  |  |  | HeavyMass Wall |  |  | HeavyMass Wall |  |  | HeavyMass Wall
Construction Assembly Layers |  |  |  | Refer MetalFramedWallMassHeavy |  |  | Refer T24NRWallMassHeavy |  |  | Refer T24NRWallMassHeavy
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) |  |  | 0.043 Btu / h * ft2 * °F | 0.053 Btu / h * ft2 * °F |  | 0.043 Btu / h * ft2 * °F | 0.053 Btu / h * ft2 * °F |  | 0.043 Btu / h * ft2 * °F | 0.053 Btu / h * ft2 * °F | [104 empty] | 0.043 Btu / h * ft2 * °F | 0.043 Btu / h * ft2 * °F | 0.043 Btu / h * ft2 * °F
Dimensions |  |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail | [104 empty] | Small Office | Small Office | Small Office
Tilts and orientations
Roof
Construction |  |  |  | Wood Framed Roof |  |  | Wood Framed Roof |  |  | Wood Framed Roof
Construction Assembly Layers |  |  |  | Refer NACMRoofWoodFrame |  |  | Refer T24NRRoofWood |  |  | Refer T24NRRoofWood
U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) |  | 0.050 Btu / h * ft2 * °F |  | U=0.065 Btu / h * ft2 * °F | 0.051 Btu / h * ft2 * °F |  | U=0.065 Btu / h * ft2 * °F | 0.051 Btu / h * ft2 * °F |  | U=0.065 Btu / h * ft2 * °F | [101 empty] | 0.050 Btu / h * ft2 * °F | 0.050 Btu / h * ft2 * °F | 0.050 Btu / h * ft2 * °F
Dimensions |  | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | [101 empty] | Small Office | Small Office | Small Office
Tilts and orientations
Window
Dimensions
Glass-Type and frame
U-factor (Btu / h * ft2 * °F) | [21 empty] | 0.29 |  | 0.29 |  |  | 0.29 |  | 0.29 |  |  | 0.29 |  | 0.29
SHGC | [21 empty] | Refer Medium Office | 0.2 | 0.2 |  |  | Refer Medium Office | 0.2 | 0.2 |  |  | Refer Medium Office | 0.2 | 0.2
Visible transmittance | [22 empty] | Refer Medium Office | Refer Medium Office |  |  |  | Refer Medium Office | Refer Medium Office |  |  |  | Refer Medium Office | Refer Medium Office | [28 empty] | 42: 0.504; 44: 0.504; 45: 0.504; 47: 0.504; 48: 0.504; 50: 0.504; 51: 0.504; 53: 0.504; 54: 0.504; 56: 0.504; 57: 0.504; 59: 0.504
Operable area | [62 empty] | 42: Refer Large Office; 44: Refer Large Office; 45: Refer Large Office; 47: Refer Large Office; 48: Refer Large Office; 50: Refer Large Office; 51: Refer Large Office; 53: Refer Large Office; 54: Refer Large Office; 56: Refer Large Office; 57: Refer Large Office; 59: Refer Large Office
Skylight
Dimensions | [11 empty] | Skylight to Roof Ratio- 0.0467 Core Retail, Refer Skylight Layout for details | Skylight to Roof Ratio- 0.0467 Core Retail, Refer Skylight Layout for details |  | Skylight to Roof Ratio- 0.0467 Core Retail, Refer Skylight Layout for details | Skylight to Roof Ratio- 0.0467 Core Retail, Refer Skylight Layout for details
Glass-Type and frame | [11 empty] | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail
U-factor (Btu / h * ft2 * °F)
SHGC
Visible transmittance | [10 empty] | 0.588 |  | 0.588 | 0.588 |  | 0.588
Foundation | [10 empty] | Refer StandAloneRetail |  | Refer StandAloneRetail | Refer StandAloneRetail |  | Refer StandAloneRetail
Foundation Type
Construction
Construction Assembly Layers
Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | [19 empty] | F factor= 0.46 |  |  |  |  | F factor= 0.46 |  |  |  |  | F factor= 0.46
Thermal properties for basement walls | [19 empty] | Refer MediumOffice |  |  |  |  | Refer MediumOffice |  |  |  |  | Refer MediumOffice
Dimensions
Interior Surfaces
Construction
Construction Assembly Layers
Dimensions
Internal Mass
Air Barrier System
Infiltration | [20 empty] | Peak: 0.2218 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  |  |  | Peak: 0.2218 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  |  |  | Peak: 0.2218 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on)
HVAC System Type | [20 empty] | Refer MediumOffice |  |  |  |  | Refer MediumOffice |  |  |  |  | Refer MediumOffice
System Type
Heating type
Cooling type
Distribution and terminal units | [16 empty] | 3 single-zone roof top units serving thermal zones back_space, point_of_sale, and front_retail with Duct loss - 14% of design flow rate. | 3 single-zone roof top units serving thermal zones back_space, point_of_sale, and front_retail with Duct loss - 14% of design flow rate. | [30 empty] | Dual- max control on all VAV dampers |  |  |  | Dual- max control on all VAV dampers |  |  |  | Dual- max control on all VAV dampers
HVAC Sizing | [16 empty] | Refer StandAloneRetail Ductloss Baseline | Refer StandAloneRetail Ductloss Baseline | [30 empty] | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | Refer Medium Office
Cooling
Heating
HVAC Efficiency
Cooling | [62 empty] | 80: Chiller COP -6.8; 84: Chiller COP -6.8; 88: Chiller COP -6.8 |  | 3.8 (COP)/ 13 (EER) |  |  | 3.8 (COP)/ 13 (EER) 17.5 (SEER) |  |  | 3.8 (COP)/ 13 (EER) 17.5 (SEER) |  |  | 3.8 (COP)/ 13 (EER) | 3.8 (COP)/ 13 (EER) | 3.8 (COP)/ 13 (EER)
Heating | [62 empty] | 80: Refer Large Office; 84: Refer Large Office; 88: Refer Large Office |  | Refer StripMall PSZ | 90% |  | Refer StripMall PSZ | 90% |  | Refer StripMall PSZ | 90% |  | Refer StripMall PTAC | Refer StripMall PTAC | Refer StripMall PTAC
HVAC Control | [96 empty] | Refer StripMall PSZ |  |  | Refer StripMall PSZ |  |  | Refer StripMall PSZ
Thermostat Setpoint
Thermostat Setback
Design Supply air temperature
Supply air temperature reset | [47 empty] | Reset by Outdoor Air. Outdoor temperature- max 80F, min 60 F Setpoint at Outdor high- 64.4 F, low- 55 F |  |  |  | Reset by Outdoor Air. Outdoor temperature- max 80F, min 60 F Setpoint at Outdor high- 64.4 F, low- 55 F |  |  |  | Reset by Outdoor Air. Outdoor temperature- max 80F, min 60 F Setpoint at Outdor high- 64.4 F, low- 55 F
Chilled water supply temperatures | [47 empty] | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | Refer Medium Office | [6 empty] | 81: 44 F; 85: 44 F; 89: 44 F
Chilled water return temperatures | [62 empty] | 81: 56 F; 85: 56 F; 89: 56 F
Chilled water supply temperature reset | [62 empty] | 81: Refer Large Office; 85: Refer Large Office; 89: Refer Large Office
Condenser Type | [62 empty] | 82: Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature; 86: Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature; 90: Water-cooled Condenser with Setpoint Reset (50F to 95F) based on Outdoor WetBulb temperature
Hot water supply temperatures | [62 empty] | 82: Refer Large Office; 86: Refer Large Office; 90: Refer Large Office
Hot water supply temperature reset
Economizers | [49 empty] | Fixed Dry bulb -70F high limit |  |  |  | Fixed Dry bulb -70F high limit |  |  |  | Fixed Dry bulb -70F high limit | [39 empty] | Non-Integrated Economizer (Diff. DB) Economizer max limit set to 55 F(cooling supply temperature) |  |  | Non-Integrated Economizer (Diff. DB) Economizer max limit set to 55 F(cooling supply temperature) |  |  | Non-Integrated Economizer (Diff. DB) Economizer max limit set to 55 F(cooling supply temperature)
Ventilation | [49 empty] | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | Refer Medium Office | [39 empty] | Refer StripMall PSZ |  |  | Refer StripMall PSZ |  |  | Refer StripMall PSZ
Supply Fan
Fan type
Fan schedules
Supply Fan Total Efficiency (%)
Fan Motor Efficiency | [46 empty] | 93.6% |  |  |  | 93.6% |  |  |  | 93.6%
Supply Fan Pressure Rise | [46 empty] | 5.08 in H2O |  |  |  | 5.08 in H2O |  |  |  | 5.08 in H2O
Pump | [46 empty] | Refer Medium Office |  |  |  | Refer Medium Office |  |  |  | Refer Medium Office
Pump Type
Rated Pump Head
Pump Power
Pump Efficiency
Cooling Tower
Cooling Tower Type
Tower range
Tower Approach
Design Flow rate
Cooling Tower Efficiency | [62 empty] | 83: 80 gpm/hp; 87: 80 gpm/hp; 91: 80 gpm/hp
Service Water Heating | [62 empty] | 83: Refer Large Office; 87: Refer Large Office; 91: Refer Large Office
SWH type
Fuel type
Thermal efficiency (%)
Peak Use Flow rate (gpm)
Peak Use Flow rate Schedule
Water temperature setpoint
Water temperature setpoint Schedule
Water Heater Max Capacity (Btuh)
Water consumption
Lighting Load
Lighting power density (W/ft2) | [34 empty] | 0.6 W/ft2 | 0.9 W/ft2 | 0.6 W/ft2 | 0.9 W/ft2 | 0.6 W/ft2 | 0.9 W/ft2
Schedule | [34 empty] | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office
Daylighting Controls | [11 empty] | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . |  | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . | Cont. control in Skylit area in Core Retail, Primary and Secondary daylit area in Front Retail, Point of sale and Primary daylit area in Font entry . | [43 empty] | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details | Refer LargeOfficeDaylight for details | 28: Refer LargeOfficeDaylight for details; 29: Refer LargeOfficeDaylight for details; 43: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 44: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 45: Refer LargeOfficeDaylight for details; 46: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 47: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 48: Refer LargeOfficeDaylight for details; 49: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 50: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 52: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 53: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 54: Refer LargeOfficeDaylight for details; 55: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 56: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 57: Refer LargeOfficeDaylight for details; 58: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.; 59: 4 Stepped control in Primary and Secondary daylit area in all above grade perimeter zones.
[12 empty] | Refer StandAloneDaylight for more details | Refer StandAloneDaylight for more details |  | Refer StandAloneDaylight for more details | Refer StandAloneDaylight for more details | [46 empty] | 46: Refer LargeOfficeDaylight for details; 47: Refer LargeOfficeDaylight for details; 49: Refer LargeOfficeDaylight for details; 50: Refer LargeOfficeDaylight for details; 55: Refer LargeOfficeDaylight for details; 56: Refer LargeOfficeDaylight for details; 58: Refer LargeOfficeDaylight for details; 59: Refer LargeOfficeDaylight for details
Plug load | [11 empty] | Refer Stand Alone Retail | Refer Stand Alone Retail |  | Refer Stand Alone Retail | Refer Stand Alone Retail | [43 empty] | Refer Large Office | Refer Large Office | Refer Large Office | 28: Refer Large Office; 29: Refer Large Office; 43: Refer Large Office; 44: Refer Large Office; 45: Refer Large Office; 46: Refer Large Office; 47: Refer Large Office; 48: Refer Large Office; 49: Refer Large Office; 50: Refer Large Office; 52: Refer Large Office; 53: Refer Large Office; 54: Refer Large Office; 55: Refer Large Office; 56: Refer Large Office; 57: Refer Large Office; 58: Refer Large Office; 59: Refer Large Office
Electric power density (W/ft2) | [40 empty] | 1.2 W/ft2 | 1.8 W/ft2 | 1.2 W/ft2 | 1.8 W/ft2 | 1.2 W/ft2 | 1.8 W/ft2
Schedule | [40 empty] | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office | Refer Medium Office
Occupancy
Average people
Schedule
| 05-RetlMed | EnvelopeRoofInsulation | EnvelopeWallInsulation | EnvelopeHeavy | EnvelopeRoofInsulation | EnvelopeWallInsulation | EnvelopeHeavy | EnvelopeRoofInsulation | RetlMed-EnvelopeWallInsulation | RetlMed-EnvelopeHeavy | Daylighting SRRBaseHighVT | Daylighting SRR4.67 | Daylighting SRR4.67HighVT | Daylighting SRRBaseHighVT | Daylighting SRR4.67 | Daylighting SRR4.67HighVT | HVAC DuctLoss | HVAC DuctLoss | 03-OffMed | FloorSlabInsulation | Envelope Infiltration | GlazingWindowU | GlazingWindowSHGC | GlazingWindowUSHGC | FloorSlabInsulation | Envelope Infiltration | GlazingWindowU | GlazingWindowSHGC | GlazingWindowUSHGC | FloorSlabInsulation | Envelope Infiltration | GlazingWindowU | GlazingWindowSHGC | GlazingWindowUSHGC | LightingLowLPD | LightingHighLPD | LightingLowLPD | LightingHighLPD | LightingLowLPD | LightingHighLPD | Int.Eqpt LowEPD | 37CZ15MediumOffice Int.Eqpt HighEPD | 38CZ16MediumOffice Int.Eqpt LowEPD | 39CZ16MediumOffice Int.Eqpt HighEPD | 40CZ06MediumOffice Int.Eqpt LowEPD | 41CZ06MediumOffice Int.Eqpt HighEPD | HVACPVAV Design | HVACPVAV SATControl | HVACPVAV VAVControl | HVACPVAV EconomizerType | HVACPVAV Design | HVACPVAV SATControl | HVACPVAV VAVControl | HVACPVAV EconomizerType | HVACPVAV Design | HVACPVAV SATControl | HVACPVAV VAVControl | HVACPVAV EconomizerType | 04-OffLrg | WWR20 | WWR60 | 27CZ07LargeOffice Glazing WWR60%SouthOverhang | WWR20 | WWR60 | Cont.DimHighVT | StepDim | StepDimHighVT | WWR20Cont.DimHighVT | WWR20StepDim | WWR20StepDimHighVT | WWR60Cont.DimHighVT | WWR60StepDim | WWR60StepDimHighVT | Cont.DimHighVT | StepDim | StepDimHighVT | WWR20Cont.DimHighVT | WWR20StepDim | WWR20StepDimHighVT | WWR60Cont.DimHighVT | WWR60StepDim | WWR60StepDimHighVT | HVACChillerCOP | HVACChWDeltaT | HVACVAV CWSetpoint | HVACTowerEff | HVACChillerCOP | HVACChWDeltaT | HVACVAV CWSetpoint | HVACTowerEff | HVACChillerCOP | HVACChWDeltaT | HVACVAV CWSetpoint | HVACTowerEff | 10-RetlStrp | HVACPSZ DXCOP | HVACPSZ HeatEff | HVACPSZ EconomizerControl | HVACPSZ DXCOP | HVACPSZ HeatEff | HVACPSZ EconomizerControl | HVACPSZ DXCOP | HVACPSZ HeatEff | HVACPSZ EconomizerControl | HVACPTAC DXCOP | HVACPTAC DXCOP | HVACPTAC DXCOP | HVACPTAC vsFanCoil | HVACPTAC vsFanCoil | HVACPTAC vsFanCoil | 02-OffSml-SG | EnvRoofInsulation | EnvRoofInsulation | EnvRoofInsulation | EnvWallInsulation | EnvWallInsulation | EnvWallInsulation | 03-OffMed-SG | WWR40 | WWR20 | WWR40 | WWR20 | WWR40 | WWR20 | WinUSHGC | WinUSHGC | WinUSHGC | 05-RetlMed-SG | SRR5 | SRR5 | SRR5 | SRR1 | SRR1 | SRR1 | SkyUSHGC | SkyUSHGC | SkyUSHGC
| 00 | 15 | 15 | 15 | 16 | 16 | 16 | 06 | 06 | 06 | 07 | 07 | 07 | 01 | 01 | 01 | 16 | 06 | 00 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 06 | 06 | 06 | 06 | 06 | 15 | 15 | 16 | 16 | 06 | 06 | 15 | 15 | 16 | 16 | 06 | 06 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 06 | 06 | 06 | 06 | 00 | 07 | 07 | 07 | 01 | 01 | 07 | 07 | 07 | 07 | 07 | 07 | 07 | 07 | 07 | 01 | 01 | 01 | 01 | 01 | 01 | 01 | 01 | 01 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 06 | 06 | 06 | 06 | 00 | 15 | 15 | 15 | 16 | 16 | 16 | 06 | 06 | 06 | 15 | 16 | 06 | 15 | 16 | 06 | 000 | 15 | 16 | 06 | 15 | 16 | 06 | 00 | 15 | 15 | 16 | 16 | 06 | 06 | 15 | 16 | 06 | 00 | 15 | 16 | 06 | 15 | 16 | 06 | 15 | 16 | 06
|  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -WWR20 | -WWR20 | -WWR20 | -WWR60 | -WWR60 | -WWR60 | -Baseline | -Baseline | -Baseline | -WWR20 | -WWR20 | -WWR20 | -WWR60 | -WWR60 | -WWR60 | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline |  | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePSZ | -BaselinePTAC | -BaselinePTAC | -BaselinePTAC | -BaselinePTAC | -BaselinePTAC | -BaselinePTAC |  | -Baserun | -Baserun | -Baserun | -Baserun | -Baserun | -Baserun |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline |  | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline | -Baseline

## Performance Curve (hidden)
Performance Curves |  | See Appendix 5.7 for a complete listing and for equivalent curves in IP units.
The performance curves described below have been used in the prototype models. The coefficients and variable ranges are in S.I units
Prototype | Component |  |  | Variables |  |  | Coefficients
|  | ACM Curve Name | Curve Type | Dependent | Independent
|  |  |  | Var1 | Var2 | Var3 | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10
Medium Office | DXCoil | CoilClgDXQRatio_fTwbToadbSI | BiQuadratic | QRatio | Twb | Toadb | 0.86779 | 0.014245 | 0.00055404 | -0.007569 | 3.24e-05 | -0.00019116
Medium Office | DXCoil | CoilClgDXSnglQRatio_fCFMRatio | Quadratic | QRatio | CFMRatio |  | 0.8 | 0.2 | 0 | 0 | 0 | 0
Medium Office | DXCoil | CoilClgDXEIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb | 0.11671 | 0.028458 | -0.00041148 | 0.021422 | 0.000162 | -0.0006804
Medium Office | DXCoil | CoilClgDXEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  | 0.20123 | -0.031217 | 1.9505 | -1.1205 | 0 | 0
Medium Office | DXCoil | CoilClgPTACEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  | 0.125 | 0.875 | 0 | 0 | 0 | 0
MediumOffice | DXCoil | CoilClgDXSnglEIRRatio_fCFMRatio | Quadratic | EIRRatio | CFMRatio |  | 1.156 | -0.1816 | 0.0256 | 0 | 0 | 0
MediumOffice | Fan | FanVSDPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  | 0.070429 | 0.38533 | -0.46086 | 1.0092 | 0 | 0
StripMall-PSZ | DXCoil | CoilClgDXQRatio_fTwbToadbSI | BiQuadratic | QRatio | Twb | Toadb | 0.86779 | 0.014245 | 0.00055404 | -0.007569 | 3.24e-05 | -0.00019116
StripMall-PSZ | DXCoil | CoilClgDXSnglQRatio_fCFMRatio | Quadratic | QRatio | CFMRatio |  | 0.8 | 0.2 | 0 | 0 | 0 | 0
StripMall-PSZ | DXCoil | CoilClgDXEIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb | 0.11671 | 0.028458 | -0.00041148 | 0.021422 | 0.000162 | -0.0006804
StripMall-PSZ | DXCoil | CoilClgDXEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  | 0.20123 | -0.031217 | 1.9505 | -1.1205 | 0 | 0
StripMall-PSZ | DXCoil | CoilClgDXSnglEIRRatio_fCFMRatio | Quadratic | EIRRatio | CFMRatio |  | 1.156 | -0.1816 | 0.0256 | 0 | 0 | 0
StripMall-PSZ | Heating | CoilHtgFurnFIRRatio_fQRatio | Quadratic | FIRRatio | QRatio |  | 0.01861 | 1.0942 | -0.11282 | 0 | 0 | 0
StripMall-PSZ | Fan | FanAForBIPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  | 0.1631 | 1.5901 | -0.8817 | 0.1281 | 0 | 0
StandAloneRetail | DXCoil | CoilClgDXQRatio_fTwbToadbSI | BiQuadratic | QRatio | Twb | Toadb | 0.86779 | 0.014245 | 0.00055404 | -0.007569 | 3.24e-05 | -0.00019116
StandAloneRetail | DXCoil | CoilClgDXSnglQRatio_fCFMRatio | Quadratic | QRatio | CFMRatio |  | 0.8 | 0.2 | 0 | 0 | 0 | 0
StandAloneRetail | DXCoil | CoilClgDXEIRRatio_fTwbToadbSI | BiQuadratic | EIRRatio | Twb | Toadb | 0.11671 | 0.028458 | -0.00041148 | 0.021422 | 0.000162 | -0.0006804
StandAloneRetail | DXCoil | CoilClgDXEIRRatio_fQRatio | Cubic | EIRRatio | QRatio |  | 0.20123 | -0.031217 | 1.9505 | -1.1205 | 0 | 0
StandAloneRetail | DXCoil | CoilClgDXSnglEIRRatio_fCFMRatio | Quadratic | EIRRatio | CFMRatio |  | 1.156 | -0.1816 | 0.0256 | 0 | 0 | 0
StandAloneRetail | Heating | CoilHtgFurnFIRRatio_fQRatio | Quadratic | FIRRatio | QRatio |  | 0.01861 | 1.0942 | -0.11282 | 0 | 0 | 0
StandAloneRetail | Fan | FanAForBIPwrRatio_fCFMRatio | Cubic | PwrRatio | CFMRatio |  | 0.1631 | 1.5901 | -0.8817 | 0.1281 | 0 | 0
<CrvDblQuad>
<Name>CoilClgDXQRatio_fTwbToadbSI</Name>
<Coef1>0.86779</Coef1>
<Coef2>0.014245</Coef2>
<Coef3>0.000554</Coef3>
<Coef4>-0.007569</Coef4>
<Coef5>3.2e-005</Coef5>
<Coef6>-0.000191</Coef6>
</CrvDblQuad>
<CrvQuad>
<Name>CoilClgDXSnglQRatio_fCFMRatio</Name>
<Coef1>0.8</Coef1>
<Coef2>0.2</Coef2>
<Coef3>0</Coef3>
<MaxVar1>1.5</MaxVar1>
<MinVar1>0.5</MinVar1>
</CrvQuad>
<CrvDblQuad>
<Name>CoilClgDXEIRRatio_fTwbToadbSI</Name>
<Coef1>0.116709</Coef1>
<Coef2>0.028458</Coef2>
<Coef3>-0.000411</Coef3>
<Coef4>0.021422</Coef4>
<Coef5>0.000162</Coef5>
<Coef6>-0.00068</Coef6>
</CrvDblQuad>
<CrvCubic>
<Name>CoilClgDXEIRRatio_fQRatio</Name>
<Coef1>0</Coef1>
<Coef2>5.1091</Coef2>
<Coef3>-8.5515</Coef3>
<Coef4>4.4744</Coef4>
</CrvCubic>
<CrvQuad>
<Name>CoilClgDXSnglEIRRatio_fCFMRatio</Name>
<Coef1>1.156</Coef1>
<Coef2>-0.1816</Coef2>
<Coef3>0.0256</Coef3>
<MaxVar1>1.5</MaxVar1>
<MinVar1>0.5</MinVar1>
</CrvQuad>
<CrvCubic>
<Name>FanVSDPwrRatio_fCFMRatio</Name>
<Coef1>0.070429</Coef1>
<Coef2>0.38533</Coef2>
<Coef3>-0.460864</Coef3>
<Coef4>1.0092</Coef4>
<MaxOut>1</MaxOut>
<MaxVar1>1</MaxVar1>
<MinOut>0.1</MinOut>
<MinVar1>0.08</MinVar1>
</CrvCubic>

## Sizing Values
Sizing Values | [24 empty] | Sizing Values
Object | Characteristics | Units | Medium Office | Medium Office | Medium Office | Large Office | Large Office | Large Office | Large Office | Large Office | Stand Alone Retail | Stand Alone Retail | Stand Alone Retail | Stand Alone Retail | Stand Alone Retail | Strip Mall - PSZ | Strip Mall - PSZ | Strip Mall - PSZ | Strip Mall - PTAC | Strip Mall - PTAC | Strip Mall - PTAC | Strip Mall - FPFC | Strip Mall - FPFC | Strip Mall - FPFC | Object | Characteristics | Units | Small Office-SG | Small Office-SG | Small Office-SG | Medium Office-SG | Medium Office-SG | Medium Office-SG | Medium Retail-SG | Medium Retail-SG | Medium Retail-SG
Building | Climate Zone | none | 6 | 15 | 16 | 1 | 6 | 7 | 15 | 16 | 16 | 15 | 6 | 7 | 1 | 16 | 15 | 6 | 16 | 15 | 6 | 16 | 15 | 6 | Building | Climate Zone | none | 6 | 15 | 16 | 6 | 15 | 16 | 6 | 15 | 16
Building | Weather Station | none | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | BLUE-CANYON_725845 | ARCATA_725945 | TORRANCE_722955 | SAN-DIEGO-LINDBERGH_722900 | PALM-SPRINGS-INTL_722868 | BLUE-CANYON_725845 | BLUE-CANYON_725845 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | TORRANCE_722955 | TORRANCE_722955 | BLUE-CANYON_725845 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | BLUE-CANYON_725845 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | BLUE-CANYON_725845 | PALM-SPRINGS-INTL_722868 | TORRANCE_722955 | Building | Weather Station | none | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | BLUE-CANYON_725845 | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | BLUE-CANYON_725845 | TORRANCE_722955 | PALM-SPRINGS-INTL_722868 | BLUE-CANYON_725845
Building | Zip Code | none | 90505 | 92262 | 95715 | 95521 | 90505 | 92101 | 92262 | 95715 | 95715 | 92262 | 90505 | 90505 | 90505 | 95715 | 92262 | 90505 | 95715 | 92262 | 90505 | 95715 | 92262 | 90505 | Building | Zip Code | none | 90505 | 92262 | 95715 | 90505 | 92262 | 95715 | 90505 | 92262 | 95715
ChilledWater Loop | [24 empty] | HotWater Loop
Chiller 1 | Rated Capacity | Btu/h | NA | NA | NA | 8226712 | 8226712 | 8226712 | 8284242 | 8284242 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Boiler 1 | Rated Capacity | Btu/h | NA | NA | NA | 1399322 | 1428055 | 1399322 | NA | NA | NA
Chiller 2 | Rated Capacity | Btu/h | NA | NA | NA | 8226712 | 8226712 | 8226712 | 8284242 | 8284242 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Boiler Pump | Flow Capacity | gpm | NA | NA | NA | 69.9 | 71.4 | 69.9 | NA | NA | NA
Chiller 1 Primary Pump | Flow Capacity | gpm | NA | NA | NA | 822.4 | 822.4 | 822.4 | 828.1 | 828.1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Boiler Pump | Electric Power | kW | NA | NA | NA | 1.255 | 1.281 | 1.255 | NA | NA | NA
Chiller 2 Primary Pump | Flow Capacity | gpm | NA | NA | NA | 822.4 | 822.4 | 822.4 | 828.1 | 828.1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Chiller Secondary Pump | Flow Capacity | gpm | NA | NA | NA | 1644.7 | 1644.7 | 1644.7 | 1656.2 | 1656.2 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Cooling Coils
Chiller Secondary Pump | Min Flow Rate | gpm | NA | NA | NA | 493.4 | 493.4 | 493.4 | 36.179 | 36.179 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bottom VAV Coil Cooling | Gross Capacity Total | Btu/h | NA | NA | NA | 608319 | 608319 | 608319 | NA | NA | NA
[25 empty] | Mid VAV Coil Cooling | Gross Capacity Total | Btu/h | NA | NA | NA | 608319 | 608319 | 608319 | NA | NA | NA
Condenser Water Loop | [24 empty] | Top VAV Coil Cooling | Gross Capacity Total | Btu/h | NA | NA | NA | 608319 | 657784 | 608319 | NA | NA | NA
Cooling Tower 1 | Rated Capacity | Btu/h | NA | NA | NA | 19182364 | 19182364 | 19182364 | 19316506 | 19316506 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BackSpace Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | 127988 | 191982 | 127988
Cooling Tower Pump | Flow Capacity | gpm | NA | NA | NA | 3835 | 3835 | 3835 | 3861.8 | 3861.8 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | PointOfSale Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | 50808.8 | 76213.3 | 50808.8
Cooling Tower Pump | Electric Power | kW | NA | NA | NA | 66.586 | 66.586 | 66.586 | 67.051 | 67.051 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | FrontRetail Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | 50808.8 | 76213.3 | 50808.8
[25 empty] | CoreRetail Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | 539213 | 808819 | 539213
HotWater Loop | [24 empty] | Perimeter_Zn_1 | Gross Capacity Total | Btu/h | 50420.7 | 50420.7 | 50420.7 | NA | NA | NA | NA | NA | NA
Boiler 1 | Rated Capacity | Btu/h | 1250836 | 1331536 | 1533283 | 11946706 | 11946706 | 11946706 | 12033276 | 12033276 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_2 | Gross Capacity Total | Btu/h | 38222.3 | 38222.3 | 38222.3 | NA | NA | NA | NA | NA | NA
Boiler Pump | Flow Capacity | gpm | 62.5 | 66.6 | 76.6 | 597.1 | 597.1 | 597.1 | 601.4 | 601.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_3 | Gross Capacity Total | Btu/h | 22673.9 | 22673.9 | 22673.9 | NA | NA | NA | NA | NA | NA
Boiler Pump | Electric Power | kW | 1.122 | 1.194 | 1.375 | 8.927 | 8.927 | 8.927 | 8.992 | 8.992 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_4 | Gross Capacity Total | Btu/h | 38222.3 | 38222.3 | 38222.3 | NA | NA | NA | NA | NA | NA
[25 empty] | CoreZn | Gross Capacity Total | Btu/h | 22673.9 | 22673.9 | 22673.9 | NA | NA | NA | NA | NA | NA
Cooling Coils
BasementCoilCooling | Gross Capacity Total | Btu/h | NA | NA | NA | 1270000 | 1270000 | 1270000 | 1270000 | 1270000 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Heating Coils
Bottom VAV Coil Cooling | Gross Capacity Total | Btu/h | 559512 | 559512 | 526599 | 1270000 | 1270000 | 1270000 | 1270000 | 1270000 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Bottom VAV Coil Heating | Gross Capacity Total | Btu/h | NA | NA | NA | 113077 | 113077 | 113077 | NA | NA | NA
Mid VAV Coil Cooling | Gross Capacity Total | Btu/h | 559512 | 615463 | 712106 | 1270000 | 1270000 | 1270000 | 1270000 | 1270000 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreBottomReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 209274 | 209274 | 209274 | NA | NA | NA
Hi VAV Coil Cooling | Gross Capacity Total | Btu/h | NA | NA | NA | 1270000 | 1270000 | 1270000 | 1270000 | 1270000 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | PerimeterBottom1ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 44116.5 | 44116.5 | 44116.5 | NA | NA | NA
Top VAV Coil Cooling | Gross Capacity Total | Btu/h | 615463 | 671414 | 712106 | 1270000 | 1270000 | 1270000 | 1270000 | 1270000 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | PerimeterBottom2ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 27929.6 | 27929.6 | 27929.6 | NA | NA | NA
BackSpace Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 127988 | 127988 | 127988 | 127988 | 127988 | NA | NA | NA | NA | NA | NA | NA | NA | NA | PerimeterBottom3ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 44116.5 | 44116.5 | 44116.5 | NA | NA | NA
PointOfSale Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 50808.9 | 70455 | 50808.9 | 50808.9 | 50808.9 | NA | NA | NA | NA | NA | NA | NA | NA | NA | PerimeterBottom4ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 27927.7 | 27927.7 | 27927.7 | NA | NA | NA
FrontRetail Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 50808.8 | 70454.8 | 50808.8 | 50808.8 | 50808.8 | NA | NA | NA | NA | NA | NA | NA | NA | NA | Mid VAV Coil Heating | Gross Capacity Total | Btu/h | NA | NA | NA | 113077 | 113077 | 113077 | NA | NA | NA
CoreRetail Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 539213 | 754887 | 539213 | 539213 | 539213 | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreMidReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 209274 | 209274 | 209274 | NA | NA | NA
LG Store 1 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 117374 | 152586 | 117374 | 117374 | 162759 | 117374 | 112500 | 158824 | 112500 | PerimeterMid1ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 44116.5 | 44116.5 | 44116.5 | NA | NA | NA
LG Store 2 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 117374 | 152586 | 117374 | 117374 | 162759 | 117374 | 112500 | 158824 | 112500 | PerimeterMid2ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 27929.6 | 27929.6 | 27929.6 | NA | NA | NA
SM Store 1 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 58687 | 76293.1 | 58687 | 58687 | 81396 | 58687 | 56250 | 79411.8 | 56250 | PerimeterMid3ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 44116.5 | 44116.5 | 44116.5 | NA | NA | NA
SM Store 2 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 58687 | 76293.1 | 58687 | 58687 | 81396 | 58687 | 56250 | 79411.8 | 56250 | PerimeterMid4ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 27927.7 | 27927.7 | 27927.7 | NA | NA | NA
SM Store 3 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 58687 | 76293.1 | 58687 | 58687 | 81396 | 58687 | 56250 | 79411.8 | 56250 | Top VAV Coil Heating | Gross Capacity Total | Btu/h | NA | NA | NA | 113077 | 122271 | 113077 | NA | NA | NA
SM Store 4 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 58687 | 76293.1 | 58687 | 58687 | 81396 | 58687 | 56250 | 79411.8 | 56250 | CoreTopReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 209274 | 226291 | 209274 | NA | NA | NA
SM Store 5 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 58687 | 76293.1 | 58687 | 58687 | 81396 | 58687 | 56250 | 79411.8 | 56250 | PerimeterTop1ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 44116.5 | 47703.9 | 44116.5 | NA | NA | NA
SM Store 6 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 58687 | 76293.1 | 58687 | 58687 | 81396 | 58687 | 56250 | 79411.8 | 56250 | PerimeterTop2ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 27929.6 | 30200.7 | 27929.6 | NA | NA | NA
SM Store 7 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 58687 | 76293.1 | 58687 | 58687 | 81396 | 58687 | 56250 | 79411.8 | 56250 | PerimeterTop3ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 44116.5 | 47703.9 | 44116.5 | NA | NA | NA
SM Store 8 Zn Cooling Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 58687 | 76293.1 | 58687 | 58687 | 87209.9 | 58687 | 56250 | 79411.8 | 56250 | PerimeterTop4ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 27927.7 | 30198.6 | 27927.7 | NA | NA | NA
[25 empty] | BackSpace Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | 89502.2 | 134253 | 89502.2
Heating Coils | [24 empty] | PointOfSale Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | 35530.8 | 53296.2 | 35530.8
BasementCoilHeating | Gross Capacity Total | Btu/h | NA | NA | NA | 230854 | 230854 | 230854 | 230854 | 230854 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | FrontRetail Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | 35530.8 | 53296.2 | 35530.8
Bottom VAV Coil Heating | Gross Capacity Total | Btu/h | 97817.1 | 97817.1 | 97817.1 | 230854 | 230854 | 230854 | 230854 | 230854 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreRetail Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | 377073 | 565610 | 377073
CoreBottomReheatCoil | Gross Capacity Total | Btu/h | 181033 | 181033 | 181033 | 512716 | 512716 | 512716 | 512716 | 512716 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_1 | Gross Capacity Total | Btu/h | 35259.4 | 35259.4 | 35259.4 | NA | NA | NA | NA | NA | NA
PerimeterBottom1ReheatCoil | Gross Capacity Total | Btu/h | 38163.2 | 38163.2 | 38163.2 | 63457.7 | 63457.7 | 63457.7 | 63457.7 | 63457.7 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_2 | Gross Capacity Total | Btu/h | 26729 | 26729 | 26729 | NA | NA | NA | NA | NA | NA
PerimeterBottom2ReheatCoil | Gross Capacity Total | Btu/h | 24160.6 | 24160.6 | 24160.6 | 40893.9 | 40893.9 | 40893.9 | 40893.9 | 40893.9 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_3 | Gross Capacity Total | Btu/h | 15855.9 | 15855.9 | 15855.9 | NA | NA | NA | NA | NA | NA
PerimeterBottom3ReheatCoil | Gross Capacity Total | Btu/h | 38163.2 | 38163.2 | 38163.2 | 63458.1 | 63458.1 | 63458.1 | 63458.1 | 63458.1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_4 | Gross Capacity Total | Btu/h | 26729 | 26729 | 26729 | NA | NA | NA | NA | NA | NA
PerimeterBottom4ReheatCoil | Gross Capacity Total | Btu/h | 24158.9 | 24158.9 | 24158.9 | 40893.6 | 40893.6 | 40893.6 | 40893.6 | 40893.6 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreZn | Gross Capacity Total | Btu/h | 15855.9 | 15855.9 | 15855.9 | NA | NA | NA | NA | NA | NA
Mid VAV Coil Heating | Gross Capacity Total | Btu/h | 97817.1 | 107599 | 136944 | 230854 | 230854 | 230854 | 230854 | 230854 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
CoreMidReheatCoil | Gross Capacity Total | Btu/h | 181033 | 199136 | 253446 | 512716 | 512716 | 512716 | 512716 | 512716 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Fans
PerimeterMid1ReheatCoil | Gross Capacity Total | Btu/h | 38163.2 | 41979.5 | 53428.4 | 63457.7 | 63457.7 | 63457.7 | 63457.7 | 63457.7 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BottomVAV SupplyFan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | 20664.6 | 20664.6 | 20664.6 | NA | NA | NA
PerimeterMid2ReheatCoil | Gross Capacity Total | Btu/h | 24160.6 | 26576.7 | 33824.9 | 40893.9 | 40893.9 | 40893.9 | 40893.9 | 40893.9 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | MidVAV SupplyFan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | 20664.6 | 20664.6 | 20664.6 | NA | NA | NA
PerimeterMid3ReheatCoil | Gross Capacity Total | Btu/h | 38163.2 | 41979.5 | 53428.4 | 63458.1 | 63458.1 | 63458.1 | 63458.1 | 63458.1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | TopVAV SupplyFan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | 20664.6 | 22344.9 | 20664.6 | NA | NA | NA
PerimeterMid4ReheatCoil | Gross Capacity Total | Btu/h | 24158.9 | 26574.7 | 33822.4 | 40893.6 | 40893.6 | 40893.6 | 40893.6 | 40893.6 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BackSpace Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 4089.1 | 6133.65 | 4089.1
Hi VAV Coil Heating | Gross Capacity Total | Btu/h | NA | NA | NA | 230854 | 230854 | 230854 | 230854 | 230854 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | PointOfSale Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 1623.3 | 2434.95 | 1623.3
CoreHiReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 512716 | 512716 | 512716 | 512716 | 512716 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | FrontRetail Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 1623.3 | 2434.95 | 1623.3
PerimeterHi1ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 63457.7 | 63457.7 | 63457.7 | 63457.7 | 63457.7 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreRetail Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 17227.4 | 25841.1 | 17227.4
PerimeterHi2ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 40893.9 | 40893.9 | 40893.9 | 40893.9 | 40893.9 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_1 | Flow Capacity (max air flow rate) | CFM | 1610.9 | 1610.9 | 1610.9 | NA | NA | NA | NA | NA | NA
PerimeterHi3ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 63458.1 | 63458.1 | 63458.1 | 63458.1 | 63458.1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_2 | Flow Capacity (max air flow rate) | CFM | 1221.17 | 1221.17 | 1221.17 | NA | NA | NA | NA | NA | NA
PerimeterHi4ReheatCoil | Gross Capacity Total | Btu/h | NA | NA | NA | 40893.6 | 40893.6 | 40893.6 | 40893.6 | 40893.6 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_3 | Flow Capacity (max air flow rate) | CFM | 724.411 | 724.411 | 724.411 | NA | NA | NA | NA | NA | NA
Top VAV Coil Heating | Gross Capacity Total | Btu/h | 107599 | 117381 | 136944 | 230854 | 230854 | 230854 | 230854 | 230854 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_4 | Flow Capacity (max air flow rate) | CFM | 1221.17 | 1221.17 | 1221.17 | NA | NA | NA | NA | NA | NA
CoreTopReheatCoil | Gross Capacity Total | Btu/h | 199136 | 217239 | 253446 | 512716 | 512716 | 512716 | 512716 | 512716 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreZn | Flow Capacity (max air flow rate) | CFM | 724.411 | 724.411 | 724.411 | NA | NA | NA | NA | NA | NA
PerimeterTop1ReheatCoil | Gross Capacity Total | Btu/h | 41979.5 | 45795.8 | 53428.4 | 63457.7 | 63457.7 | 63457.7 | 63457.7 | 63457.7 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterTop2ReheatCoil | Gross Capacity Total | Btu/h | 26576.7 | 28992.8 | 33824.9 | 40893.9 | 40893.9 | 40893.9 | 40893.9 | 40893.9 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Terminal Units
PerimeterTop3ReheatCoil | Gross Capacity Total | Btu/h | 41979.5 | 45795.8 | 53428.4 | 63458.1 | 63458.1 | 63458.1 | 63458.1 | 63458.1 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreBottomZn TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 12238.2 | 12238.2 | 12238.2 | NA | NA | NA
PerimeterTop4ReheatCoil | Gross Capacity Total | Btu/h | 26574.7 | 28990.6 | 33822.4 | 40893.6 | 40893.6 | 40893.6 | 40893.6 | 40893.6 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | PerimeterBottomZn1 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 2579.91 | 2579.91 | 2579.91 | NA | NA | NA
BackSpace Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 89502.7 | 89502.7 | 89502.7 | 89502.7 | 89502.7 | NA | NA | NA | NA | NA | NA | NA | NA | NA | PerimeterBottomZn2 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 1633.31 | 1633.31 | 1633.31 | NA | NA | NA
PointOfSale Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 35530.8 | 46190.1 | 35530.8 | 35530.8 | 35530.8 | NA | NA | NA | NA | NA | NA | NA | NA | NA | PerimeterBottomZn3 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 2579.91 | 2579.91 | 2579.91 | NA | NA | NA
FrontRetail Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 35530.7 | 46190 | 35530.7 | 35530.7 | 35530.7 | NA | NA | NA | NA | NA | NA | NA | NA | NA | PerimeterBottomZn4 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 1633.2 | 1633.2 | 1633.2 | NA | NA | NA
CoreRetail Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | 377073 | 527895 | 377073 | 377073 | 377073 | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreMidZn TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 12238.2 | 12238.2 | 12238.2 | NA | NA | NA
LG Store 1 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 82080 | 106704 | 82080 | 123120 | 160056 | 123120 | 123120 | 184680 | 123120 | PerimeterMidZn1 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 2579.91 | 2579.91 | 2579.91 | NA | NA | NA
LG Store 2 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 82080 | 106704 | 82080 | 123120 | 160056 | 123120 | 123120 | 184680 | 123120 | PerimeterMidZn2 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 1633.31 | 1633.31 | 1633.31 | NA | NA | NA
SM Store 1 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 41040 | 53352 | 41040 | 61560 | 80044.4 | 61560 | 61560 | 92340 | 61560 | PerimeterMidZn3 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 2579.91 | 2579.91 | 2579.91 | NA | NA | NA
SM Store 2 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 41040 | 53352 | 41040 | 61560 | 80044.4 | 61560 | 61560 | 92340 | 61560 | PerimeterMidZn4 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 1633.2 | 1633.2 | 1633.2 | NA | NA | NA
SM Store 3 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 41040 | 53352 | 41040 | 61560 | 80044.4 | 61560 | 61560 | 92340 | 61560 | CoreTopZn TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 12238.2 | 13233.4 | 12238.2 | NA | NA | NA
SM Store 4 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 41040 | 53352 | 41040 | 61560 | 80044.4 | 61560 | 61560 | 92340 | 61560 | PerimeterTopZn1 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 2579.91 | 2789.7 | 2579.91 | NA | NA | NA
SM Store 5 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 41040 | 53352 | 41040 | 61560 | 80044.4 | 61560 | 61560 | 92340 | 61560 | PerimeterTopZn2 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 1633.31 | 1766.13 | 1633.31 | NA | NA | NA
SM Store 6 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 41040 | 53352 | 41040 | 61560 | 80044.4 | 61560 | 61560 | 92340 | 61560 | PerimeterTopZn3 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 2579.91 | 2789.7 | 2579.91 | NA | NA | NA
SM Store 7 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 41040 | 53352 | 41040 | 61560 | 80044.4 | 61560 | 61560 | 92340 | 61560 | PerimeterTopZn4 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 1633.2 | 1766 | 1633.2 | NA | NA | NA
SM Store 8 Zn Heating Coil | Gross Capacity Total | Btu/h | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 41040 | 53352 | 41040 | 61560 | 80044.4 | 61560 | 61560 | 92340 | 61560 | BackSpace Sys TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 4089.1 | 6133.65 | 4089.1
[25 empty] | PointOfSale Sys TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 1623.3 | 2434.95 | 1623.3
Fans | [24 empty] | FrontRetail Sys TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 1623.3 | 2434.95 | 1623.3
Basement VAVFan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | 42188.3 | 42188.3 | 42188.3 | 42188.3 | 42188.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreRetail Sys TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | 17227.4 | 25841.1 | 17227.4
BottomVAV SupplyFan | Flow Capacity (max air flow rate) | CFM | 17875.9 | 17875.9 | 17875.9 | 42188.3 | 42188.3 | 42188.3 | 42188.3 | 42188.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_1 | Primary Air Flow (max air flow rate) | CFM | 1610.9 | 1610.9 | 1610.9 | NA | NA | NA | NA | NA | NA
MidVAV SupplyFan | Flow Capacity (max air flow rate) | CFM | 17875.9 | 19663.5 | 25026.3 | 42188.3 | 42188.3 | 42188.3 | 42188.3 | 42188.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_2 | Primary Air Flow (max air flow rate) | CFM | 1221.17 | 1221.17 | 1221.17 | NA | NA | NA | NA | NA | NA
Hi VAV Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | 42188.3 | 42188.3 | 42188.3 | 42188.3 | 42188.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_3 | Primary Air Flow (max air flow rate) | CFM | 724.411 | 724.411 | 724.411 | NA | NA | NA | NA | NA | NA
TopVAV SupplyFan | Flow Capacity (max air flow rate) | CFM | 19663.5 | 21451.1 | 25026.3 | 42188.3 | 42188.3 | 42188.3 | 42188.3 | 42188.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Perimeter_Zn_4 | Primary Air Flow (max air flow rate) | CFM | 1221.17 | 1221.17 | 1221.17 | NA | NA | NA | NA | NA | NA
BackSpace Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 4089.12 | 4089.12 | 4089.12 | 4089.12 | 4089.12 | NA | NA | NA | NA | NA | NA | NA | NA | NA | CoreZn | Primary Air Flow (max air flow rate) | CFM | 724.411 | 724.411 | 724.411 | NA | NA | NA | NA | NA | NA
PointOfSale Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 1623.3 | 1623.3 | 1623.3 | 1623.3 | 1623.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA
FrontRetail Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 1623.3 | 1623.3 | 1623.3 | 1623.3 | 1623.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA
CoreRetail Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 17227.4 | 17227.4 | 17227.4 | 17227.4 | 17227.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA
LG Store 1 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3750 | 4875 | 3750 | 3750 | 4875 | 3750 | 3750 | 5625 | 3750
LG Store 2 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3750 | 4875 | 3750 | 3750 | 4875 | 3750 | 3750 | 5625 | 3750
SM Store 1 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | 1875 | 2438 | 1875 | 1875 | 2812.5 | 1875
SM Store 2 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | 1875 | 2438 | 1875 | 1875 | 2812.5 | 1875
SM Store 3 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | 1875 | 2438 | 1875 | 1875 | 2812.5 | 1875
SM Store 4 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | 1875 | 2438 | 1875 | 1875 | 2812.5 | 1875
SM Store 5 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | 1875 | 2438 | 1875 | 1875 | 2812.5 | 1875
SM Store 6 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | 1875 | 2438 | 1875 | 1875 | 2812.5 | 1875
SM Store 7 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | 1875 | 2438 | 1875 | 1875 | 2812.5 | 1875
SM Store 8 Zn Supply Fan | Flow Capacity (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | 1875 | 2438 | 1875 | 1875 | 2812.5 | 1875
Terminal Units
CoreBottomZn TU | Primary Air Flow (max air flow rate) | CFM | 10586.7 | 10586.7 | 10586.7 | 29983.4 | 29983.4 | 29983.4 | 29983.4 | 29983.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterBottomZn1 TU | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2231.76 | 2231.76 | 3710.97 | 3710.97 | 3710.97 | 3710.97 | 3710.97 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterBottomZn2 TU | Primary Air Flow (max air flow rate) | CFM | 1412.9 | 1412.9 | 1412.9 | 2391.45 | 2391.45 | 2391.45 | 2391.45 | 2391.45 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterBottomZn3 TU | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2231.76 | 2231.76 | 3711 | 3711 | 3711 | 3711 | 3711 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterBottomZn4 TU | Primary Air Flow (max air flow rate) | CFM | 1412.8 | 1412.8 | 1412.8 | 2391.44 | 2391.44 | 2391.44 | 2391.44 | 2391.44 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
CoreMidZn TU | Primary Air Flow (max air flow rate) | CFM | 10586.7 | 11645.4 | 14821.4 | 29983.4 | 29983.4 | 29983.4 | 29983.4 | 29983.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterMidZn1 TU | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2454.94 | 3124.47 | 3710.97 | 3710.97 | 3710.97 | 3710.97 | 3710.97 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterMidZn2 TU | Primary Air Flow (max air flow rate) | CFM | 1412.9 | 1554.19 | 1978.06 | 2391.45 | 2391.45 | 2391.45 | 2391.45 | 2391.45 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterMidZn3 TU | Primary Air Flow (max air flow rate) | CFM | 2231.76 | 2454.94 | 3124.47 | 3711 | 3711 | 3711 | 3711 | 3711 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterMidZn4 TU | Primary Air Flow (max air flow rate) | CFM | 1412.8 | 1554.08 | 1977.92 | 2391.44 | 2391.44 | 2391.44 | 2391.44 | 2391.44 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
CoreHiZn TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 29983.4 | 29983.4 | 29983.4 | 29983.4 | 29983.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHiZn1 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 3710.97 | 3710.97 | 3710.97 | 3710.97 | 3710.97 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHiZn2 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 2391.45 | 2391.45 | 2391.45 | 2391.45 | 2391.45 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHiZn3 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 3711 | 3711 | 3711 | 3711 | 3711 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterHiZn4 TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | 2391.44 | 2391.44 | 2391.44 | 2391.44 | 2391.44 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
CoreTopZn TU | Primary Air Flow (max air flow rate) | CFM | 11645.4 | 12704 | 14821.4 | 29983.4 | 29983.4 | 29983.4 | 29983.4 | 29983.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterTopZn1 TU | Primary Air Flow (max air flow rate) | CFM | 2454.94 | 2678.12 | 3124.47 | 3710.97 | 3710.97 | 3710.97 | 3710.97 | 3710.97 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterTopZn2 TU | Primary Air Flow (max air flow rate) | CFM | 1554.19 | 1695.48 | 1978.06 | 2391.45 | 2391.45 | 2391.45 | 2391.45 | 2391.45 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterTopZn3 TU | Primary Air Flow (max air flow rate) | CFM | 2454.94 | 2678.12 | 3124.47 | 3711 | 3711 | 3711 | 3711 | 3711 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
PerimeterTopZn4 TU | Primary Air Flow (max air flow rate) | CFM | 1554.08 | 1695.36 | 1977.92 | 2391.44 | 2391.44 | 2391.44 | 2391.44 | 2391.44 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
BackSpace Sys TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 4089.12 | 4089.12 | 4089.12 | 4089.12 | 4089.12 | NA | NA | NA | NA | NA | NA | NA | NA | NA
PointOfSale Sys TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 1623.3 | 1623.3 | 1623.3 | 1623.3 | 1623.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA
FrontRetail Sys TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 1623.3 | 1623.3 | 1623.3 | 1623.3 | 1623.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA
CoreRetail Sys TU | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | 17227.4 | 17227.4 | 17227.4 | 17227.4 | 17227.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA
LG Store 1 Sys TU 1 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3750 | 4875 | 3750 | NA | NA | NA | NA | NA | NA
LG Store 2 Sys TU 2 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 3750 | 4875 | 3750 | NA | NA | NA | NA | NA | NA
SM Store 1 Sys TU 3 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | NA | NA | NA | NA | NA | NA
SM Store 2 Sys TU 4 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | NA | NA | NA | NA | NA | NA
SM Store 3 Sys TU 5 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | NA | NA | NA | NA | NA | NA
SM Store 4 Sys TU 6 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | NA | NA | NA | NA | NA | NA
SM Store 5 Sys TU 7 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | NA | NA | NA | NA | NA | NA
SM Store 6 Sys TU 8 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | NA | NA | NA | NA | NA | NA
SM Store 7 Sys TU 9 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | NA | NA | NA | NA | NA | NA
SM Store 8 Sys TU 10 | Primary Air Flow (max air flow rate) | CFM | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1875 | 2437.5 | 1875 | NA | NA | NA | NA | NA | NA

## Sheet1 (hidden)
0400-OffLrg Z coordinate changes: | [5 empty] | 20% WWR |  |  |  |  | Sill Ht |  | 60% WWR |  |  | Sill Ht
| Mid Floor Wall | Old Z | New Z |  |  |  | old Z | New Z | basNewZ | diff |  |  | old Z | New Z | diff
|  | 55.0141 | 65 | 9
|  | 64.0167 | 74 | 4
|  | 68.0167 | 78
| Mid Floor Window | 58.0148 | 68 | 3 |  | Mid Floor Window | 60.6157 | 70.6009 | 68 | 2.6005 | 5.6009 |  | 55.4139 | 65.3991 | 7.8023 | 0.39909
|  | 63.2162 | 73.2014 | 5.2014 |  |  | 63.2162 | 73.2014 | 73.2014 | 5.2014 |  |  | 63.2162 | 73.2014 | 5.2014
| HI Floor Wall | 97.0256 | 130 | 9
|  | 106.028 | 139 | 4
|  | 110.028 | 143
| Hi Floor Window | 100.026 | 133 | 3 |  | Hi Floor Window | 102.6269 | 135.6009 | 133 | 2.6011 | 5.6009 |  | 97.4251 | 130.3991 | 7.8029 | 0.39909
|  | 105.228 | 138.202 | 5.202 |  |  | 105.228 | 138.202 | 138.202 | 5.202 |  |  | 105.228 | 138.202 | 5.202
| Top Floor Wall | 110.028 | 143 | 9
|  | 119.031 | 152 | 4
|  | 123.031 | 156
| Top Floor Window | 113.029 | 146 | 3 |  | Top Floor Window | 115.6299 | 148.6009 | 146 | 2.6001 | 5.6009 |  | 110.4281 | 143.3991 | 7.8019 | 0.39909
|  | 118.23 | 151.201 | 5.201 |  |  | 118.23 | 151.201 | 151.201 | 5.201 |  |  | 118.23 | 151.201 | 5.201
[6 empty] | Bottom Flr Window | 5.6016 | 5.6016 | 3.0007 | 2.6005 |  |  | 0.39975 | 0.39975 | 7.8023
[7 empty] | 8.2021 | 8.2021 | 8.2021 | 5.2014 |  |  | 8.2021 | 8.2021 | 5.2014
| 042607-OffLrg-WWR60 | 0427 (Void - Removed)07-OffLrg-27CZ07LargeOffice Glazing WWR60%SouthOverhang | 042801-OffLrg-WWR20 | 042901-OffLrg-WWR60 | 044207-OffLrg-Cont.DimHighVT | 044307-OffLrg-StepDim | 044407-OffLrg-StepDimHighVT | 044507-OffLrg-WWR20Cont.DimHighVT | 044607-OffLrg-WWR20StepDim | 044707-OffLrg-WWR20StepDimHighVT | 044807-OffLrg-WWR60Cont.DimHighVT | 044907-OffLrg-WWR60StepDim | 045007-OffLrg-WWR60StepDimHighVT | 045101-OffLrg-Cont.DimHighVT | 045201-OffLrg-StepDim | 045301-OffLrg-StepDimHighVT | 045401-OffLrg-WWR20Cont.DimHighVT | 045501-OffLrg-WWR20StepDim | 045601-OffLrg-WWR20StepDimHighVT | 045701-OffLrg-WWR60Cont.DimHighVT | 045801-OffLrg-WWR60StepDim | 045901-OffLrg-WWR60StepDimHighVT | 048015--OffLrg-HVACChillerCOP | 048115--OffLrg-HVACChWDeltaT | 048215--OffLrg-HVACVAV CWSetpoint | 048315--OffLrg-HVACTowerEff | 048416--OffLrg-HVACChillerCOP | 048516--OffLrg-HVACChWDeltaT | 048616--OffLrg-HVACVAV CWSetpoint | 048716--OffLrg-HVACTowerEff | 048806--OffLrg-HVACChillerCOP | 048906--OffLrg-HVACChWDeltaT | 049006--OffLrg-HVACVAV CWSetpoint | 049106--OffLrg-HVACTowerEff