## Complete Building Method
2013 NACM | People | Sensible heat | Latent heat | Receptacle | Hot water | Lighting | Ventilation | Gas Appl Load | Refrig Load | Schedule
| # per 1000 ft² | Btu/h per person | Btu/h per person | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | Btu/h-ft2 | W/ft2
Auditorium Building | 143 | 245 | 105 | 1 | 0.09 | 1.5 | 1.07 | 0 | 0 | Assembly
Classroom Building | 40 | 246 | 171 | 1 | 0.162 | 1.1 | 0.32 | 0 | 0 | School
Commercial and Industrial Storage Building | 5 | 268 | 403 | 0.43 | 0.162 | 0.6 | 0.15 | 0 | 0.28 | Warehouse
Convention Center Building | 136 | 245 | 112 | 0.96 | 0.086 | 1.2 | 1.02 | 0.04 | 0.03 | Assembly
Data Center Buildings (Note 9) | 5 | 268 | 403 | note 9 | 0.162 | 0.8 | 0.15 | 0 | 0 | Data
Financial Institution Building | 10 | 250 | 250 | 1.5 | 0.18 | 1.1 | 0.15 | 0 | 0 | Office
General Commercia' or Industrial Work Building | 7 | 375 | 625 | 1 | 0.18 | 1 | 0.15 | 0 | 0.28 | Manufacturing
Grocery Store Buildings | 29 | 252 | 225 | 0.91 | 0.17 | 1.5 | 0.22 | 0.03 | 0.14 | Retail
Library Building | 10 | 250 | 250 | 1.5 | 0.18 | 1.3 | 0.15 | 0 | 0 | Office
Medical Building/Clinic Building | 10 | 250 | 213 | 1.18 | 0.165 | 1.1 | 0.15 | 0.33 | 1.12 | Health
Office Building | 10 | 250 | 206 | 1.34 | 0.159 | 0.8 | 0.15 | 0 | 0 | Office
Parking Garage Building | 10 | 250 | 200 | 0 | 0 | 0.2 | 0.15 | 0 | 0 | Parking
Religious Facility Building | 136 | 245 | 112 | 0.96 | 0.086 | 1.6 | 1.03 | 0.04 | 0 | Assembly
Restaurant Building | 45 | 274 | 334 | 0.79 | 0.549 | 1.2 | 0.38 | 5.14 | 0.06 | Restaurant
School Building | 40 | 246 | 171 | 1 | 0.162 | 1 | 0.32 | 0.04 | 0.03 | School
Theater Building | 130 | 268 | 403 | 0.54 | 0.09 | 1.3 | 0.98 | 0.04 | 0 | Assembly
All Other Buildings | 10 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0.04 | 0.03 | Office
Note 9 - Receptacle Load shall be specified by the user.

## Area Category Method
2013 NACM Space Type | People | Sensible heat | Latent heat | Receptacle | Hot water | Lighting | Ventilation | Gas Equipment Power | Refrig Load | Illuminance Setpoint for Daylighting |  | Primary Sidelit Daylighting Zone Setpoint Adjustment Factor | Secondary Sidelit Daylighting Zone Setpoint Adjustment Factor | Schedule | Notes
| # per 1000 ft² | per person | per person | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | Btu/h-ft2 | W/ft2 | Min (lux) | Max (lux)
Auditorium Area (Note 10) | 143 | 245 | 105 | 1 | 0.09 | 1.5 | 1.07 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly
Auto Repair Area | 10 | 275 | 475 | 1 | 0.18 | 0.9 | 1.5 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing
Bar, Cocktail Lounge and Casino Areas (Note 10) | 67 | 275 | 275 | 1 | 0.18 | 1.1 | 0.2 | 0 | 1.12 | 50 | 200 | 1.5 | 2 | Restaurant
Beauty Salon Area | 10 | 250 | 200 | 2 | 0.18 | 1.7 | 0.4 | 0 | 0 | 500 | 500 | 1.5 | 2 | Retail
Classrooms, Lecture, Training, Vocational Areas | 50 | 245 | 155 | 1 | 0.18 | 1.2 | 0.38 | 0 | 0 | 50 | 500 | 1.5 | 2 | School
Civic Meeting Place Area (Note 10) | 25 | 250 | 200 | 1.5 | 0.18 | 1.3 | 0.19 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly
Commercial and Industrial Storage Areas (conditioned or unconditioned) | 3 | 275 | 475 | 0.2 | 0.18 | 0.6 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse
Commercial and Industrial Storage Areas (refrigerated) | 0 | 275 | 475 | 0.2 | 0.18 | 0.7 | 0 | 0 | 10 | 50 | 300 | 1.5 | 2 | Warehouse
Computer Room (Note 11) | 3 | 275 | 475 | 0 | 0.18 | 0.8 | 0.15 | 0 | 0 | 75 | 300 | 1 | 4 | Data | SpcFunc only valid if user-input receptacle load is >= 20W/ft2
Convention, Conference, Multipurpose and Meeting Center Areas (Note 10) | 67 | 245 | 155 | 1 | 0.09 | 1.4 | 0.5 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly
Corridors, Restrooms, Stairs, and Support Areas | 10 | 250 | 250 | 0.2 | 0 | 0.6 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office
Dining Area (Note 10) | 67 | 275 | 275 | 0.5 | 0.578 | 1.1 | 0.5 | 0 | 0 | 50 | 200 | 1.5 | 2 | Restaurant
Dry Cleaning (Coin Operated) | 10 | 250 | 250 | 3 | 0.18 | 0.9 | 0.3 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing
Dry Cleaning (Full Service Commercial) | 10 | 250 | 250 | 3 | 0.18 | 0.9 | 0.45 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing
Electrical, Mechanical, Telephone Rooms | 3 | 250 | 250 | 3 | 0.18 | 0.7 | 0.15 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse
Exercise Center, Gymnasium Areas | 67 | 255 | 875 | 0.5 | 0.18 | 1 | 0.5 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail
Exhibit, Museum Areas (Note 10) | 67 | 250 | 250 | 1.5 | 0.09 | 2 | 0.5 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly
Financial Transaction Area | 10 | 250 | 250 | 1.5 | 0.18 | 1.2 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office
General Commercial and Industrial Work Areas, High Bay | 10 | 275 | 475 | 1 | 0.18 | 1 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing
General Commercial and Industrial Work Areas, Low Bay | 10 | 275 | 475 | 1 | 0.18 | 0.9 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing
General Commercial and Industrial Work Areas, Precision | 10 | 250 | 200 | 1 | 0.18 | 1.2 | 0.15 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing
Grocery Sales Areas (Note 10) | 33 | 250 | 200 | 1 | 0.18 | 1.2 | 0.25 | 1.1942 | 2.6 | 500 | 500 | 1.5 | 2 | Retail
High-Rise Residential Living Spaces (Note 9) | 5 | 245 | 155 | 0.5 | T24 RecircDHW | 0.5 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving
Hotel Function Area (Note 10) | 67 | 250 | 200 | 0.5 | 0.096 | 1.5 | 0.5 | 0 | 0 | 50 | 300 | 1.5 | 2 | Assembly
Hotel/Motel Guest Room (Note 9) | 5 | 245 | 155 | 0.5 | 4.48 | 0.5 | 0.15 | 0 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving
Housing, Public and Common Areas: Multi-family, Dormitory | 10 | 250 | 250 | 0.5 | 0.192 | 1 | 0.15 | 0 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon
Housing, Public and Common Areas: Senior Housing | 10 | 250 | 250 | 0.5 | 0.192 | 1.5 | 0.15 | 0 | 0 | 400 | 1000 | 1.5 | 2 | ResidentialCommon
Kitchen, Commercial Food Preparation | 5 | 275 | 475 | 1.5 | 0.578 | 1.6 | 0.15 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | GasEquipPwr only valid if hood length > 0. If there is an exhaust hood, set convective fraction to 0
Kitchenette or Residential Kitchen | 5 | 275 | 475 | 1 | 0.36 | 1.6 | 0.15 | 3 | 0.5 | 100 | 500 | 1.5 | 2 | Office
Laboratory, Scientific | 10 | 250 | 200 | 2 | 0.18 | 1.4 | see NACM | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory
Laboratory, Equipment Room | 5 | 250 | 200 | 10 | 0.18 | 1.4 | see NACM | 12.6926 | 0 | 500 | 1000 | 1.5 | 2 | Laboratory
Laundry | 10 | 250 | 250 | 3 | 0.578 | 0.9 | 0.15 | 0.75064 | 0 | 100 | 300 | 1.5 | 2 | Manufacturing
Library, Reading Areas | 20 | 250 | 200 | 1.5 | 0.18 | 1.2 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office
Library, Stacks | 10 | 250 | 200 | 1.5 | 0.18 | 1.5 | 0.15 | 0 | 0 | 200 | 300 | 1 | 4 | Office
Lobby, Hotel | 10 | 250 | 250 | 0.5 | 0.18 | 1.1 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly
Lobby, Main Entry | 10 | 250 | 250 | 0.5 | 0.09 | 1.5 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly
Locker/Dressing Room | 20 | 255 | 475 | 0.5 | 0.578 | 0.8 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly
Lounge, Recreation (Note 10) | 67 | 275 | 275 | 1 | 0.09 | 1.1 | 0.5 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly
Malls and Atria (Note 10) | 33 | 250 | 250 | 0.5 | 0.18 | 1.2 | 0.25 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail
Medical and Clinical Care | 10 | 250 | 200 | 1.5 | 0.24 | 1.2 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health
Office (Greater than 250 square feet in floor area) | 10 | 250 | 200 | 1.5 | 0.18 | 0.75 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office
Office (250 square feet in floor area or less) | 10 | 250 | 200 | 1.5 | 0.18 | 1 | 0.15 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office
Parking Garage Building, Parking Area | 10 | 250 | 200 | 0 | 0 | 0.14 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking
Parking Garage Area Dedicated Ramps | 10 | 250 | 200 | 0 | 0 | 0.3 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking
Parking Garage Area Daylight Adaptation Zones | 10 | 250 | 200 | 0 | 0 | 0.6 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking
Police Station and Fire Station | 10 | 250 | 200 | 1.5 | 0.18 | 0.9 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | ResidentialCommon
Religious Worship Area (Note 10) | 143 | 245 | 105 | 0.5 | 0.09 | 1.5 | 1.07 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly
Retail Merchandise Sales, Wholesale Showroom (Note 10) | 33 | 250 | 200 | 1 | 0.18 | 1.2 | 0.2 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail
Sports Arena, Indoor Playing Area | 143 | 245 | 105 | 1 | 0.09 | 2.3 | 1.07 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly
Theater, Motion Picture (Note 10) | 143 | 245 | 105 | 0.5 | 0.09 | 0.9 | 1.07 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly
Theater, Performance (Note 10) | 143 | 245 | 105 | 0.5 | 0.09 | 1.4 | 1.07 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly
Transportation Function (Note 10) | 33 | 250 | 250 | 0.5 | 0.18 | 1.2 | 0.25 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly
Unoccupied-Exclude from Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied
Unoccupied-Include in Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied
Videoconferencing Studio (Note S1) | 10 | 250 | 200 | 1.5 | 0.18 | 1.2 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office
Waiting Area | 10 | 250 | 250 | 0.5 | 0.18 | 1.1 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office
All Others (including unleased tenant space in multi-tenant facilities) | 10 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office
| [i] | From Benya, July 2006 Workshop, Changes to Lighting Power Density Values: Bringing Certain Values in Line with Standard 90.1, http://www.energy.ca.gov/title24/2008standards/documents/2006-07-12_workshop/MEASURE_BLD_02.PDF
| Note 7: | Refer to the Residential ACM, Appendix E for determining residential hot water load
| Note 10. | For these occupancies, when the proposed design is required to have demand control ventilation by §121(c) 3 the ventilation rate is the minimum that would occur at any time during occupied hours. Additional ventilation
would be provided through demand controlled ventilation to maintain CO2 levels according to §120.1.
| Note 11. | For data centers the process load from the servers and UPS shall be as designed, with the baseline same as proposed.
| Note S1: | Videoconferencing studios may install up to an additional 1.5 W/ft2 for videoconferencing rooms that meet all requirements in section 140.6(c)2Gvii.
| Reminder Note: | Data from this table for Unoccupied-Exclude from Gross Floor Area and Unoccupied-Include in Gross Floor Area are currently not used in the rules (August 2013). Rules should be updated to utilize this table data for those space types.
Note on F13: Roger Hedrick: Left at zero on assumption that the occupancy in this space is double counting of people already counted in other spaces.

## App5-4A_CompleteBuilding
// This table pasted into App5-4A_SpaceBySpace.csv
TABLE SpaceFunctionData
| FuncType | OccDens | OccSensHtRt | OccLatHtRt | RecptPwrDens | HotWtrHtgRt | IntLPDReg | VentRt | GasEqpPwrDens | CommRfrgEPD | IllumSetptMin | IllumSetptMax | IllumSetptAdjFacPri | IllumSetptAdjFacSec | FuncSchGrp | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | GasEqpSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef | ;
| //SpaceBySpace | # per 1000 ft² | Btu / occupant | Btu / occupant | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | Btu/h-ft2 | W/ft2 | lux | lux |  |  |  | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Gas Equipment Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule | ;
| Auditorium Area | 143 | 245 | 105 | 1 | 0.09 | 1.5 | 1.07 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Auto Repair Area | 10 | 275 | 475 | 1 | 0.18 | 0.9 | 1.5 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Bar, Cocktail Lounge and Casino Areas | 67 | 275 | 275 | 1 | 0.18 | 1.1 | 0.2 | 0 | 1.12 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Beauty Salon Area | 10 | 250 | 200 | 2 | 0.18 | 1.7 | 0.4 | 0 | 0 | 500 | 500 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Classrooms, Lecture, Training, Vocational Areas | 50 | 245 | 155 | 1 | 0.18 | 1.2 | 0.38 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt | ;
| Civic Meeting Place Area | 25 | 250 | 200 | 1.5 | 0.18 | 1.3 | 0.19 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Commercial and Industrial Storage Areas (conditioned or unconditioned) | 3 | 275 | 475 | 0.2 | 0.18 | 0.6 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Commercial and Industrial Storage Areas (refrigerated) | 0 | 275 | 475 | 0.2 | 0.18 | 0.7 | 0 | 0 | 10 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Computer Room | 3 | 275 | 475 | 20 | 0.18 | 0.8 | 0.15 | 0 | 0 | 75 | 300 | 1 | 4 | Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt | ;
| Convention, Conference, Multipurpose and Meeting Center Areas | 67 | 245 | 155 | 1 | 0.09 | 1.4 | 0.5 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Corridors, Restrooms, Stairs, and Support Areas | 10 | 250 | 250 | 0.2 | 0 | 0.6 | 0.15 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Dining Area | 67 | 275 | 275 | 0.5 | 0.578 | 1.1 | 0.5 | 0 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Dry Cleaning (Coin Operated) | 10 | 250 | 250 | 3 | 0.18 | 0.9 | 0.3 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Dry Cleaning (Full Service Commercial) | 10 | 250 | 250 | 3 | 0.18 | 0.9 | 0.45 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Electrical, Mechanical, Telephone Rooms | 3 | 250 | 250 | 3 | 0.18 | 0.7 | 0.15 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | ;
| Exercise Center, Gymnasium Areas | 67 | 255 | 875 | 0.5 | 0.18 | 1 | 0.5 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Exhibit, Museum Areas | 67 | 250 | 250 | 1.5 | 0.09 | 2 | 0.5 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Financial Transaction Area | 10 | 250 | 250 | 1.5 | 0.18 | 1.2 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| General Commercial and Industrial Work Areas, High Bay | 10 | 275 | 475 | 1 | 0.18 | 1 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| General Commercial and Industrial Work Areas, Low Bay | 10 | 275 | 475 | 1 | 0.18 | 0.9 | 0.15 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| General Commercial and Industrial Work Areas, Precision | 10 | 250 | 200 | 1 | 0.18 | 1.2 | 0.15 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Grocery Sales Areas | 33 | 250 | 200 | 1 | 0.18 | 1.2 | 0.25 | 1.1942 | 2.6 | 500 | 500 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| High-Rise Residential Living Spaces | 5 | 245 | 155 | 0.5 | T24 RecircDHW | 0.5 | 0.15 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | ;
| Hotel Function Area | 67 | 250 | 200 | 0.5 | 0.096 | 1.5 | 0.5 | 0 | 0 | 50 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Hotel/Motel Guest Room | 5 | 245 | 155 | 0.5 | 4.48 | 0.5 | 0.15 | 0 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | ;
| Housing, Public and Common Areas: Multi-family, Dormitory | 10 | 250 | 250 | 0.5 | 0.192 | 1 | 0.15 | 0 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Housing, Public and Common Areas: Senior Housing | 10 | 250 | 250 | 0.5 | 0.192 | 1.5 | 0.15 | 0 | 0 | 400 | 1000 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Kitchen, Commercial Food Preparation | 5 | 275 | 475 | 1.5 | 0.578 | 1.6 | 0.15 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | ;
| Kitchenette or Residential Kitchen | 5 | 275 | 475 | 1 | 0.36 | 1.6 | 0.15 | 3 | 0.5 | 100 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Laboratory, Scientific | 10 | 250 | 200 | 2 | 0.18 | 1.4 | see NACM | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | LabOccupancy | LabReceptacle | LabServiceHotWater | LabLights | LabGasEquip | LabRefrigeration | LabInfiltration | LabHVACAvail | LabHtgSetpt | LabClgSetpt | LabElevator | LabEscalator | LabWtrHtrSetpt | ;
| Laboratory, Equipment Room | 5 | 250 | 200 | 10 | 0.18 | 1.4 | see NACM | 12.6926 | 0 | 500 | 1000 | 1.5 | 2 | Laboratory | LabOccupancy | LabReceptacle | LabServiceHotWater | LabLights | LabGasEquip | LabRefrigeration | LabInfiltration | LabHVACAvail | LabHtgSetpt | LabClgSetpt | LabElevator | LabEscalator | LabWtrHtrSetpt | ;
| Laundry | 10 | 250 | 250 | 3 | 0.578 | 0.9 | 0.15 | 0.75064 | 0 | 100 | 300 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | ;
| Library, Reading Areas | 20 | 250 | 200 | 1.5 | 0.18 | 1.2 | 0.15 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Library, Stacks | 10 | 250 | 200 | 1.5 | 0.18 | 1.5 | 0.15 | 0 | 0 | 200 | 300 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Lobby, Hotel | 10 | 250 | 250 | 0.5 | 0.18 | 1.1 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lobby, Main Entry | 10 | 250 | 250 | 0.5 | 0.09 | 1.5 | 0.15 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Locker/Dressing Room | 20 | 255 | 475 | 0.5 | 0.578 | 0.8 | 0.15 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Lounge, Recreation | 67 | 275 | 275 | 1 | 0.09 | 1.1 | 0.5 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Malls and Atria | 33 | 250 | 250 | 0.5 | 0.18 | 1.2 | 0.25 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Medical and Clinical Care | 10 | 250 | 200 | 1.5 | 0.24 | 1.2 | 0.15 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | ;
| Office (Greater than 250 square feet in floor area) | 10 | 250 | 200 | 1.5 | 0.18 | 0.75 | 0.15 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Office (250 square feet in floor area or less) | 10 | 250 | 200 | 1.5 | 0.18 | 1 | 0.15 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Parking Garage Building, Parking Area | 10 | 250 | 200 | 0 | 0 | 0.14 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | ;
| Parking Garage Area Dedicated Ramps | 10 | 250 | 200 | 0 | 0 | 0.3 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | ;
| Parking Garage Area Daylight Adaptation Zones | 10 | 250 | 200 | 0 | 0 | 0.6 | 0.75 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | ;
| Police Station and Fire Station | 10 | 250 | 200 | 1.5 | 0.18 | 0.9 | 0.15 | 0 | 0 | 50 | 300 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | ;
| Religious Worship Area | 143 | 245 | 105 | 0.5 | 0.09 | 1.5 | 1.07 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Retail Merchandise Sales, Wholesale Showroom | 33 | 250 | 200 | 1 | 0.18 | 1.2 | 0.2 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | ;
| Sports Arena, Indoor Playing Area | 143 | 245 | 105 | 1 | 0.09 | 2.3 | 1.07 | 0 | 0 | 200 | 750 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Theater, Motion Picture | 143 | 245 | 105 | 0.5 | 0.09 | 0.9 | 1.07 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Theater, Performance | 143 | 245 | 105 | 0.5 | 0.09 | 1.4 | 1.07 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Transportation Function | 33 | 250 | 250 | 0.5 | 0.18 | 1.2 | 0.25 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | ;
| Unoccupied-Exclude from Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Unoccupied-Include in Gross Floor Area | 0 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | ;
| Videoconferencing Studio | 10 | 250 | 200 | 1.5 | 0.18 | 1.2 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| Waiting Area | 10 | 250 | 250 | 0.5 | 0.18 | 1.1 | 0.15 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
| All Others (including unleased tenant space in multi-tenant facilities) | 10 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | ;
ENDTABLE
//
// This table pasted into App5-4A_CompleteBuilding.csv
TABLE BldgUseData
| BldgType | OccDens | OccSensHtRt | OccLatHtRt | RecptPwrDens | HotWtrHtgRt | IntLPDReg | VentRt | GasEqpPwrDens | CommRfrgEPD | IllumSetptMin | IllumSetptMax | IllumSetptAdjFacPri | IllumSetptAdjFacSec | FuncSchGrp | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | GasEqpSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef
| //Complete Building | # per 1000 ft² | Btu / occupant | Btu / occupant | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | Btu/h-ft2 | W/ft2 | lux | lux | 0 | 0 | 0 | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Gas Equipment Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule
| Auditorium Building | 143 | 245 | 105 | 1 | 0.09 | 1.5 | 1.07 | 0 | 0 | NA | NA | NA | NA | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Classroom Building | 40 | 246 | 171 | 1 | 0.162 | 1.1 | 0.32 | 0 | 0 | NA | NA | NA | NA | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt
| Commercial and Industrial Storage Building | 5 | 268 | 403 | 0.43 | 0.162 | 0.6 | 0.15 | 0 | 0.28 | NA | NA | NA | NA | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt
| Convention Center Building | 136 | 245 | 112 | 0.96 | 0.086 | 1.2 | 1.02 | 0.04 | 0.03 | NA | NA | NA | NA | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Data Center Buildings | 5 | 268 | 403 | 20 | 0.162 | 0.8 | 0.15 | 0 | 0 | NA | NA | NA | NA | Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt
| Financial Institution Building | 10 | 250 | 250 | 1.5 | 0.18 | 1.1 | 0.15 | 0 | 0 | NA | NA | NA | NA | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| General Commercia' or Industrial Work Building | 7 | 375 | 625 | 1 | 0.18 | 1 | 0.15 | 0 | 0.28 | NA | NA | NA | NA | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt
| Grocery Store Buildings | 29 | 252 | 225 | 0.91 | 0.17 | 1.5 | 0.22 | 0.03 | 1.8 | NA | NA | NA | NA | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt
| Library Building | 10 | 250 | 250 | 1.5 | 0.18 | 1.3 | 0.15 | 0 | 0 | NA | NA | NA | NA | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| Medical Building/Clinic Building | 10 | 250 | 213 | 1.18 | 0.165 | 1.1 | 0.15 | 0.33 | 1.12 | NA | NA | NA | NA | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt
| Office Building | 10 | 250 | 206 | 1.34 | 0.159 | 0.8 | 0.15 | 0 | 0 | NA | NA | NA | NA | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| Parking Garage Building | 10 | 250 | 200 | 0 | 0 | 0.2 | 0.15 | 0 | 0 | NA | NA | NA | NA | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt
| Religious Facility Building | 136 | 245 | 112 | 0.96 | 0.086 | 1.6 | 1.03 | 0.04 | 0 | NA | NA | NA | NA | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Restaurant Building | 45 | 274 | 334 | 0.79 | 0.549 | 1.2 | 0.38 | 5.14 | 0.06 | NA | NA | NA | NA | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt
| School Building | 40 | 246 | 171 | 1 | 0.162 | 1 | 0.32 | 0.04 | 0.03 | NA | NA | NA | NA | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt
| Theater Building | 130 | 268 | 403 | 0.54 | 0.09 | 1.3 | 0.98 | 0.04 | 0 | NA | NA | NA | NA | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| All Other Buildings | 10 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0.04 | 0.03 | NA | NA | NA | NA | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
ENDTABLE
// | [15 empty] | Occupancy | Receptacle | ServiceHotWater | Lights | GasEquip | Refrigeration | Infiltration | HVACAvail | HtgSetpt | ClgSetpt | Elevator | Escalator | WtrHtrSetpt
Note on B13: David Reddy: Revise to 'Data Center'

## FuncSchGrp Table
// Schedule names by Space:FunctionScheduleGroup
TABLE SpaceFunctionGroups
| FuncGroup | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | ProcGasSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef
// | Function Group Name | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Process Gas Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule
| Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt
| Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt
| Laboratory | LabOccupancy | LabReceptacle | LabServiceHotWater | LabLights | LabGasEquip | LabRefrigeration | LabInfiltration | LabHVACAvail | LabHtgSetpt | LabClgSetpt | LabElevator | LabEscalator | LabWtrHtrSetpt | ;
| Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt
| Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt
| ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt
| ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt
| Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt
| Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt
| School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt
| Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt
ENDTABLE