## Outline
SDD Outline | [7 empty] | Properties or Array[] | Object References | Issues
Project | [7 empty] | PermitScope; BldgClassifyMethod; ClimateZone; Elevation; Latitude; Longitude; ClimateZoneCity; ClimateZoneCounty
| ConstructAssembly | [6 empty] | Material[10] |  | RHi: 1. From Scott's XML Sample Documentation: 8. There is an inconsistency between the SDD spreadsheet/SharePoint site (SDD sprd) and the XML file when it comes to object type names and references to objects (attributes) scattered throughout the SDD. In the XML file, ConstructAssembly is the name of the object type (as specified in the SDD sprd) and each surface object that references a ConstructAssembly uses an attribute called ConstructionReference. Likewise, the Material object type (from SDD sprd) is referenced by an attribute array called MaterialReference. This was a last minute change without full SDD working group consultation and may therefore be subject to change down the road. DP: The definition of ConstructAssembly as an array can be done in the Schema as a sequence of the same type, but the XML generated without a schema doesn't. Not sure where the attributes ConstructionReference and MaterialReference come from. There is a Referenced Object column and the idea is that it would return the object name, which is what is represented in the XML ConstructAssembly elements. SAC: I had to add some stuff here immediately prior to wrapping up the SDD XML for NREL, in part due to commetns from Rob & Jason. Changing names of properties should not be a problem, but I think Jason raised the concern that the name of a property in one object (Material[10] here) should not be identical to the name of anothe property or object elsewhere in the schema, and I tend to agree (though the ruleset database CAN handle non-unique names fine if need be).
| FenestrationConstruction | [6 empty] | AirInfiltrationRate; DividerMinimalSpacing; DividerThroughPanes; FenestrationFraming; FenestrationFramingThermalBreak; FenestrationOperability; GlazingForm; GlazingMaterial; GlazingTint; PanesDivider; PanesPerLite; RelativeSolarHeatGain; SolarHeatGainCoefficient; SolarReflectance; UFactor; VisibleTransmittance |  | RHi: 1. I still have concerns about no layered representation of fenestration constructions. DP: We can create a fenestration construction assembly that consists of material layers, but currently the Standards do not define acceptable materials for fenestration in their construction assembly tables.
| Material | [6 empty] | Density; Roughness; RValue; SolarAbsorbance; SpecificHeat; ThermalAbsorptance; ThermalConductivity; Thickness; VisibleAbsorptance |  | NREL: 1. Thickness plus ThermalConductivity is sufficient to calculate RValue. Should we check that these two calculation methods are equivalent to some tolerance?
| Building | [6 empty] | AboveGradeStoryCount; BldgTotlFloorArea; Name; Status; CBCOccup; RelocatablePublicSchoolBuilding; TopLevelOccupancy; WholeBldgOccup
|  | BuildingStory | [5 empty] | Name; Status
|  |  | Space |  |  |  |  | SpaceCondType; FloorArea; Volume |  | 2. JG: Need Classification from 5.4.1 ACM. Is this a small enough unit of area? DP: Subareas: We have OccupancyArea which allows more than one to be defined for a Space. 3. JG: Subareas are referenced as part of 5.4.2 ACM. ACM 5.4.6 Commercial Refrigeration Equipment is shown at space level, where is it supported in SDD? How about support for Elevators, Escaltors and Moving Walkways as appear in 5.4.7 of the ACM or Processs Gas equipment 5.4.8. DP: Refrig.equipment: just added to the SDD SP lists, so not in this spreadsheet, We will have to associate it with the space as floor area is used in its rules. Elevators and escalators & Process gas equip: we need to check with John Arendt if they will be in the final ACM? They are not regulated in T24 part 6 or the previous ACM. 4. RJH: SDD Working Group discussed simplifying ThermalZone-Space-OccupancyArea structure. After email thread with NREL I propose the following: A) Keep Project-Building-BuildingStory-Space hierarchy to minimize impact on current structure; B) Keep surface geometry at Space object (need not be closed volume if representing portion of actual room for lighting area purposes); C) Restrict Space to 1-and-only-1 OccupancyArea; D) Restrict Space/OccupancyArea to 1-and-only-1 SpaceType and 0-1 LightingArea/DaylightingArea; E) Keep ThermalZone as group of 1-N Spaces, but restrict to contiguous Spaces; F) Support Mulitplier on ThermalZone for simulation efficiency (would this lose BuildingStory information required by Title24?); G) Consider renaming Space to OccupancyArea or other term more consistent with T24/COMNET/2013ACM.
|  |  |  | Ceiling |  |  |  | CeilingConstructionType; FloorToCeilingHeight; Status; Name | ConstructAssembly
[5 empty] | AdjacentSpace |  |  |  | Space
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
|  |  |  | CeilingBelowAttic |  |  |  | CeilingConstructionType; Status; Name | ConstructAssembly
[5 empty] | AdjacentSpace |  |  |  | Space
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
|  |  |  | ExteriorFloor |  |  |  | ExtFloorConstructType; Status; Name | ConstructAssembly
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
|  |  |  | ExteriorWall |  |  |  | ExtWallConstructType; Status; Name | ConstructAssembly
[5 empty] | Door |  |  | DoorType; Name; Status | ConstructAssembly | SAC 2: ALSO - what about Glass Doors? Are they Doors or Windows? If Doors, then we need to add Opaque vs. Glass and if glass we need to include a FenestrationConstruction. DR: T24Sec101 definition for 'Door' indicates that if more the 50% area of door is glass, it is considered a glazed fenestration product. The 2008 NResComp (p3-29) manual has further guidance on how to deal with door that are <50% glazing: When a door has glazing of less than one-half the door area, the portion of the door with fenestration must be treated as part of the envelope fenestration independent of the remainder of the (opaque) door area. RHi: Proposed resolution - Divide opaque and glazed portions into opaque Door and glazed Window.
[6 empty] | PolyLoop |  | CartesianPoint[varies]
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
[5 empty] | Window |  |  | Name; Status; WindowStyle | FenestrationConstruction
[6 empty] | ExternalShadingObject |  | ShadingCoefficient; ShadingType | ConstructAssembly
[7 empty] | PolyLoop | CartesianPoint[varies]
[6 empty] | InternalShadingDevice |  |  |  | RHi: 1. Need material/construction?, control?, schedule? DP: 2013 NR ACM Internal Shading Devices descriptor does not mention construction properties. It does state that solar gain greater than x, should activate closing blinds. RHi: E+ supports extensive inside/between layers/outside shade/blind/screen alternatives with a variety of controls (schedule, solar gain, interior illuminance, glare, temperatures, etc.). We can't support everything without a lot of effort. We should only support what the codes care about. But that could still be tricky. Are shades assumed to be opaque pure reflectors?
[6 empty] | PolyLoop |  | CartesianPoint[varies]
|  |  |  | FloorAboveCrawlSpace |  |  |  | Name; Status | ConstructAssembly
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
|  |  |  | InteriorFloor |  |  |  | Name; Status | ConstructAssembly
[5 empty] | AdjacentSpace |  |  |  | Space
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
|  |  |  | InteriorWall |  |  |  | Name; Status | ConstructAssembly
[5 empty] | AdjacentSpace |  |  |  | Space
[5 empty] | Door |  |  | DoorType; Name; Status | ConstructAssembly | SAC 2: ALSO - what about Glass Doors? Are they Doors or Windows? If Doors, then we need to add Opaque vs. Glass and if glass we need to include a FenestrationConstruction. DR: T24Sec101 definition for 'Door' indicates that if more the 50% area of door is glass, it is considered a glazed fenestration product. The 2008 NResComp (p3-29) manual has further guidance on how to deal with door that are <50% glazing: When a door has glazing of less than one-half the door area, the portion of the door with fenestration must be treated as part of the envelope fenestration independent of the remainder of the (opaque) door area. RHi: Proposed resolution - Divide opaque and glazed portions into opaque Door and glazed Window.
[6 empty] | PolyLoop |  | CartesianPoint[varies]
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
|  |  |  | OccupancyArea |  |  |  | Area; Name; SpaceOccup; InfiltrationLoad; LightingLoad; LdSchedOccup; LdSchedType; OccupantDensity; OccuptLatHeat; OccuptSensHeat; ReceptacleLoad; VentilationLoad; WaterHeatingLoad |  | RHi: 2. Do we need Area? PolyLoop?. SAC: Seems like we would want an Area here, since most of the occupancy and load properties are defined in code (and various source materials as occup or load densities. Including an area allows these properties to remain in this native (density/intensity) form and allows users to easily scale up/down all loads via Area adjustments. This will probably add something to the ruleset list - to check sums of OccupancyArea Areas vs. parent Space Area...I had not invisioned PolyLoop here, but interested in the discussion... RHi: OK with Area, pending Daylighting code need for PolyLoop. DP: Area Resolution - Area property added to OccupancyArea.
[5 empty] | DaylitZone |  |  | DaylitZoneType | Skylight; Window
[5 empty] | IndoorLightingArea |  |  | Area; FixedLtgPowerProposed; IESNAIllCat; LtgAltType; LtgPowerBudget; LtgPowerProposed; PortLtgPowerProposed; PrimaryFunc; RCR
[6 empty] | LightingControls |  | LtgCtrlDevice; LtgCtrlScheme; PAF
[6 empty] | LightingAllowance |  | LtgAllowAmt; LtgAllowType; MountHgtMult
[6 empty] | LightingFixture |  | AreaFixtureType; BallastEff; BallastPow; BallastRemote; Dimmable; FixturePowBudget; FixturePowProp; HighEffLED; Portable; RSE; TailoredFixtureType
|  |  |  | PolyLoop |  |  |  | CartesianPoint[varies]
|  |  |  | Roof |  |  |  | Area; Name; RoofConstructType; SkylightRoofRatio; Status; TotalSkylightArea | ConstructAssembly
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
[5 empty] | Skylight |  |  | Name; SkylightCurbType; Status | FenestrationConstruction
[6 empty] | ExternalShadingObject |  | ShadingCoefficient; ShadingType | ConstructAssembly
[7 empty] | PolyLoop | CartesianPoint[varies]
[6 empty] | InternalShadingDevice |  |  |  | RHi: 1. Need material/construction?, control?, schedule? DP: 2013 NR ACM Internal Shading Devices descriptor does not mention construction properties. It does state that solar gain greater than x, should activate closing blinds. RHi: E+ supports extensive inside/between layers/outside shade/blind/screen alternatives with a variety of controls (schedule, solar gain, interior illuminance, glare, temperatures, etc.). We can't support everything without a lot of effort. We should only support what the codes care about. But that could still be tricky. Are shades assumed to be opaque pure reflectors?
[6 empty] | PolyLoop |  | CartesianPoint[varies]
|  |  |  | UndergroundFloor |  |  |  | Name; Status | ConstructAssembly
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
|  |  |  | UndergroundWall |  |  |  | Name; Status | ConstructAssembly
[5 empty] | PolyLoop |  |  | CartesianPoint[varies]
|  | ExternalShadingObject | [5 empty] | ShadingCoefficient; ShadingType | ConstructAssembly
|  |  | PolyLoop |  |  |  |  | CartesianPoint[varies]
|  | LoadSchedules | [7 empty] | RHi: 1. Is this just a container for all schedules? We don't have containers for elements like ConstructAssembly or Boiler or ... DP: This is a BESM term and should probably be excluded. Now that we have array objects we can handle schedules that way.
|  |  | LoadScheduleWeekly |  |  |  |  | LdSchedOccup; LdSchedType |  | RHi: 1.. I don't understand how these weekly schedules are referenced by different loads (people, lights, etc.) for different OccupancyArea(s). DP: I haven't messed with mapping space occupancy types to schedule occupancy tpes yet as there appeared to still be discussion on what to use for schedules. If it has been settled, we can map space occupancies to schedule occupancies and that would relate a schedule to an OccupancyArea (I think) RHi: 2. Also, I don't see something like Start/End dates supporting different weekly schedules over the course of a year.
|  |  |  | LoadScheduleHoliday |  |  |  | LoadPercentageHourly[24]
|  |  |  | LoadScheduleSaturday |  |  |  | LoadPercentageHourly[24]
|  |  |  | LoadScheduleSunday |  |  |  | LoadPercentageHourly[24]
|  |  |  | LoadScheduleWeekday |  |  |  | LoadPercentageHourly[24] |  | RHi: 1. What about a restaurant that's closed on Monday? DP: Not sure what the difference is between the weekend day schedules and the holiday schedule. Do they all represent when the place is closed? SAC: This partly gets back to how detailed we get - simulation vs. standards. To date, schedules are dictated by the code and I am not aware of any situations where there was variation between week days. However, w/ the potential for schedule changes and the value to user input simulation, perhaps we should allow for individual (M-F) week day schedules??
|  | AirSystem | [5 empty] | CoolControl; CoolingCapacity; CoolResetSch; HeatControl; HeatingCapacity; HeatResetSch; VentControl; OptimumStart; Type; UnmetCoolLoadHours; UnmetHeatLoadHours; Name
|  |  | AirSegment |  |  |  |  | DuctConductionLoss; DuctLeakage; DuctLeakageFactor; DuctSurfaceArea; DuctSurfaceAreaCoeff; DuctThermalRes; Path; Source; Type; MakeUpAirSystem; MakeUpThermalZone; Name
|  |  |  | CoilCooling |  |  |  | CondFlowType; CondType; CoilCoolingBF_fAirFlowCurveCoefficient; CoilCoolingBF_fPLRCurveCoefficient; CoilCoolingBF_fTempCurveCoefficient; CBFDesign; CBFRated; CapAdj; CoilCoolingCap_fTempCurveCoefficient; CapSensAdj; CapSensRated; CapTotRated; DesignClgTemp; DxEER; EIRFactorAirflowVerified; CoilCoolingDxEIR_fPLRCurveCoefficient; CoilCoolingDxEIR_fTempCurveCoefficient; DxEIR; DxFDDFactor; DxRefrgChrgFactor; DxSEER; UnloadRatioMin; FuelSource; SizingRatio; Type; WaterEconoCWSTempMax; WaterEconoCWSTempSetpoint; WaterEconoDBTempMax; WaterEconoHXEff; WaterEconoType; CrankcaseCtrlTemp; CoilFluidFlowIn; CoilFluidFlowOut; Name; Status
[5 empty] | CoilCoolingCapfTempCurveCoefficients |  |  | CoilCoolingCap_fTempCurveCoefficient[6]
[5 empty] | CoilCoolingDxEIRfPLRCurveCoefficients |  |  | CoilCoolingDxEIR_fPLRCurveCoefficient[6]
[5 empty] | CoilCoolingDxEIRfTempCurveCoefficients |  |  | CoilCoolingDxEIR_fTempCurveCoefficient[4]
|  |  |  | CoilHeating |  |  |  | CondFlowType; CondType; CoilFluidFlowIn; CoilFluidFlowOut; DesignHtgTemp; FuelSource; FuelFullLoad; CoilHeatingFurnaceHIR_fPLRCurveCoefficent; IgnitionType; PilotFuelInput; ThermalEff; CoilHeatingHpCap_fTempCurveCoefficient; HpCOP; CoilHeatingHpCOPAdjusted; DefrostCtrl; DefrostHeatSrc; CoilHeatingHpEIR_fPLRFactor; CoilHeatingHpEIR_fTempFactor; CoilHeatingHpEIR_fTempCurveCoefficient; EIR; HSPF; CoilHeatingHpSupplementalOATemp; SizingRatio; Type
[5 empty] | CoilHeatingFurnaceHIRfPLRCurveCoefficients |  |  | CoilHeatingFurnaceHIR_fPLRCurveCoefficent[3]
[5 empty] | CoilHeatingHpCapfTempCurveCoefficients |  |  | CoilHeatingHpCap_fTempCurveCoefficient[4]
[5 empty] | CoilHeatingHpEIRfPLRCurveCoefficients |  |  | CoilHeatingHpEIR_fPLRCurveCoefficient[4]
[5 empty] | CoilHeatingHpEIRfTempCurveCoefficients |  |  | CoilHeatingHpEIR_fTempCurveCoefficient[4]
|  |  |  | Fan |  |  |  | FanAxialType; FanCentrifugalType; ControlMethod; FanDriveEfficiency; FanOverallEfficiency; FlowCap; FanFlowMin; FanFlowPLRFactor; ModelingMethod; MotorBHP; MotorEff; MotorHP; MotorPoleCount; MotorPosition; MototRPM; MotorType; PLPowerCurve; Power; FanPowerIndex; PowerMin; PowerPerFlow; FanPower_fPLRCurveCoefficient; TotalSP; FanType; Name
|  | FluidSystem | [5 empty] | CoolCtrl; CoolResetSch; Description; EquipCtrl; HeatCtrl; HeatResetSch; Type; UnmetCoolLoadHours; UnmetHeatLoadHours; Name
|  |  | FluidSegment |  |  |  |  | FluidSegmentConductionLoss; FluidSegmentPipeDiameter; FluidSegmentPipeInsulationThk; PrimarySegment; Source; Type; Name
|  |  |  | Pump |  |  |  | Name; Count; FlowCap; FlowMin; MinSpeed; MinSpeedRatio; ModelingMethod; MotorBHP; MotorEff; MotorHP; OperationCtrl; Power; PowerPerFlow; PumpPowerfPLRCurveCoefficient; SpeedCtrl; Type |  | JG: 1. Not sure if pump service from ACM is needed or not. JG: 2. Does not support power per unit flow input from ACM JG: 3. Add impeller efficiency, motore efficiency, design pump head JG: 4. Add whether flow is variable speed or not. JG: 5. Add pump operation
|  | ThermalZone | [5 empty] | Name; CoolingSystem; CoolTStatSch; Description; ThermalZoneExhaustSystem; HeatingSystem; HeatTStatSch; SuppCoolingSystem; SuppHeatingSystem; ThrottlingRange; Type; VentCtrlMethod; VentilationSystem; VentRateDesign; VentRateMin; ThrottlingRangeLowerTemp; ThrottlingRangeUpperTemp |  | RHi: 1. Can a ThermalZone include spaces that are not contiguous? Rob will lead work to resolve this issue and work with Jason, John and Dan (NREL)
|  | IndoorLightingSystem | [5 empty] | ComplianceApproach; ComplianceApproval; LtgPowerBudget; LtgPowerProposed; LtgPrescripMeth
| Boiler | [6 empty] | AFUE; CapRated; CombustionEff; Count; DesignEntTemp; DesignLvgTemp; DraftType; BoilerHIRfPLRCurveCoefficent; EIR; FluidFlowIn; FluidFlowOut; Fuel; FuelFullLoad; BoilerFuelPartLoad; HeatLoss; BoilerHIRfPLRCurveFactor; ThermalEff; Type; UnloadRatioMin; Name; Status |  | JG: 1. Add inputs for equipment staging. DP: Is this different than the BoilerUnloadRatioMinimum? DR: Equipment staging controls are currently defined under 'FluidSystemEquipmentControl', which will reference a yet to be defined object that will have equipment stating properties.
|  | BoilerHIRfPLRCurveCoefficents | [5 empty] | BoilerHIRfPLRCurveCoefficent[3]
| Chiller | [6 empty] | ChillerCapAvailable; ChillerCapfTempFactor; CapRated; CondenserIn; CondenserOut; CoolEffMin; ChillerCoolingHourlyLoad; COP; Count; ChillerDBOutdoorTemp; ChillerDesignEnteringTemp; ChillerDesignLeavingTemp; ChillerEIRfPLRCurveCoefficient; ChillerEIRfTempCurveCoefficient; ChillerEIRfTempFactor; EIR; EngineSpeedMin; EvapIn; EvapOut; ChillerFIRfPLRCurveCoefficient; ChillerFIRfTempCurveCoefficient; Fuel; ChillerFuelOperating; ChillerFuelRated; ChillerLeavingTemp; ChillerPowerRated; Type; UnloadRatioMin; Name; Status |  | JG: 1. Need kW/ton DP: Ton as in 12,000 Btu/hr? DR: What?? JG: 2. Need EfficiencyType DP: We have ChillerCOP which is what 2013 NR ACM defines as chiller efficiency. JG: 3. Need air cooled condenser power from 5.8.2 DP: Will this require a condenser object, or can we define it as a property of a Chiller? JG: 4. DBEntering does not make sense for chiler unless this is for the condenser? DP: Resolved - it isn't a property of Chiller now. JG: 5. Add inputs for equipment staging. DP: Is this different from ChillerUnloadRationMinimum? DR: Equipment staging controls are currently defined under 'FluidSystemEquipmentControl', which will reference a yet to be defined object that will have equipment stating properties. KB: 6. New issue RESOLUTION (KB): solved
|  | ChillerCapfTempCurveCoefficients | [5 empty] | ChillerCapfTempCurveCoefficient[6]
|  | ChillerEIRfPLRCurveCoefficients | [5 empty] | ChillerEIRfPLRCurveCoefficient[4]
|  | ChillerEIRfTempCurveCoefficients | [5 empty] | ChillerEIRfTempCurveCoefficient[6]
|  | ChillerFIRfPLRCurveCoefficients | [5 empty] | ChillerFIRfPLRCurveCoefficient[4]
|  | ChillerFIRfTempCoefficients | [5 empty] | ChillerFIRfTempCurveCoefficient[6]
| EnergyRecovery | [6 empty] | ExhaustFlow; FluidFlowIn; FluidFlowOut; SupplyFlow; Type; Name
| EvapCooler | [6 empty] | AirFlowPrimaryDesign; AirFlowPrimaryOperating; Effectiveness; EnteringDBT; EnteringWBTemp; LeavingDBT; PerformanceCoeff; Type
| HeatExchanger | [6 empty] | HeatExchangerFluidDemandIn; HeatExchangerFluidDemandOut; HeatExchangerFluidSupplyn; HeatExchangerFluidSupplyOut; Type; Name |  | JG: 1. Is this for support of water side economizer? If so need to add terms and details and definitions. DR: Yes, will add terms in future.
| HeatRejection | [6 empty] | HeatRejectionCapfTempCurveCoefficient; HeatRejectionCapRated; CellCount; DesignEntTemp; DesignLvgTemp; DesignWBTemp; FanType; HeatRejectionFluidFlowIn; HeatRejectionFluidFlowOut; ModCtrl; TotalFanHP; Type; Name |  | JG: 1. Add ElectricInputRatio to be consistent with ACM 5.8.3 or gpm/hp to be consistent with other efficiency metrics for towers. JG: 2. Add capacity adjustment curve, JG: 3 Add cooling tower set point control options, JG: 4. Add terms needed for exception to cooling tower capacity control. JG: 5. Add low-speed airflow ratio and low speed kW ratio. JG: 6. Add power adjustment curve coefficients. Add cooling tower minimum speed.
|  | HeatRejectionCapfTempCoefficients | [5 empty] | HeatRejectionCapfTempCurveCoefficient[6]
| HVACSystems | [6 empty] | CoolOversizingRatio; HeatOversizingRatio; UnmetCoolLoadHours; UnmetHeatLoadHours; UnmetLoadHoursDeltaLimit; UnmetLoadHoursLimit |  | DR: 1. This is a proposed object that may be parent to all HVAC components in Project. Right now, it holds high level sizing terms.
| OAControl | [6 empty] | Name; EconoControlMethod; EconoHighEnthalpyLockout; EconoHighTempLockout; OutsideAirRatio; ReturnFlow; SupplyFlow; Type
| PreheatCoil | [6 empty] | Name; Type
| ProcessLoad | [6 empty] | EnergyLoad; Flow; Name; Type
| StorageTank | [6 empty] | Name; Capacity; FluidFlowIn; FluidFlowOut; RValue |  | JG: 1. need to add attributes related to how to operate thermal storage system. DR: Yes. Currently, this object was intended to represent an unfired SHW tank. For thermal storage, we will may decide to add another object…
| TerminalUnit | [6 empty] | AirFlowPrimary; HotDuctFlowSegment; Name; PrimaryFlowSegment; InducedAirZone; InductionRatio; Type; ZoneServed |  | DR: 1. Need to discuss pros/cons of TerminalUnit fan and coil properties are components or properties of TerminalUnit
| WaterHeater | [6 empty] | Name; Status; EF; FluidFlowIn; FluidFlowOut; MakeUp; StandByLoss; StorageCapacity; ThermalEff; Type
|  | WaterHeaterHIRfPLRCurveCoefficents | [5 empty] | WaterHeaterFIRfPLRCurveCoefficent[3]
PerfomanceCurve | [9 empty] | DR: 1. We need to define this object and link it to the appropratie HVAC equipment. David will lead work to complete this object definition, including making sure that this fits with what is being defined in the 2013 NR ACM for performance curves
CoolingThermostatSchedule
HeatingThermostatSchedule

## Objects
Term | Term Short Form | SDD Parent | Properties | Referenced Objects | Referenced HVAC Object | ObjectType | Array Count | ArrayObject | ArrayProperty | Definition | Standards Reference | Constraints | Set By | Issues | Resolved Issues | Critical Path Issue | Collapsed From
AdjacentSpace |  | Ceiling |  | Space |  | Heterogeneous |  |  |  | The Space on the other side of the InteriorPartition.
CeilingBelowAttic
InteriorFloor
InteriorWall
Building | Bldg | Project | AboveGradeStoryCount |  |  | Heterogeneous |  |  |  | The root element of the building description file, Building is a structure representing a complete building for energy analysis purposes. | The Standards refer to any construction project as a building. Entire Building is the term used to represent a stand alone structure and the ensemble of all enclosed spaces including the space for which a permit is sought, plus all existing conditioned and unconditioned space within the structure. | [5 empty] | BuildingOccupancyProperties
BuildingTotalFloorArea
Name
Status
CBCOccupancyGroup
RelocatablePublicSchoolBuilding
TopLevelOccupancy
WholeBuildingOccupancy
BuildingStory | BldgStry | Building | Name |  |  | Heterogeneous |  |  |  | The portion of a building included between the upper surface of a floor and the upper surface of the floor or roof next above. It is measured as the vertical distance from top to top of two successive tiers of beams or finished floor surfaces. ( Source: definition in CBC) | T24: No definition, but the number of stories is used to differentiate between low rise residential and high rise residential which uses the nonresidential standards for the most part.
Status
CartesianPoint |  | PolyLoop |  |  |  | Property Array | 3 |  | Coordinate | The cartesian triple (x, y and z) locating a three-dimensional point relative to some specified origin of coordinates. | NA
Ceiling |  | Space | CeilingConstructionType | ConstructAssembly |  | Heterogeneous |  |  |  | A building partition forming the interior, overhead boundary of a space. | 2013 NR ACM: Not a Building Descriptor. Used only as a general term in text with the same meaning as Ceiling. JA1: Ceiling is the interior upper surface of a space separating it from an attic, plenum, indirectly or directly conditioned space or the roof assembly, which has a slope less than 60 degrees from horizontal. | [5 empty] | InteriorPartition Partition SurfaceGeometry
FloorToCeilingHeight
Status
Name
CeilingBelowAttic |  | Space | CeilingConstructionType | ConstructAssembly |  | Heterogeneous |  |  |  | A Ceiling partition that is placed below an Attic | [6 empty] | InteriorPartition Partition SurfaceGeometry
Status
Name
ConstructAssembly |  | Project |  |  |  | Object Array | 10 | Material |  | An array of up to 10 Material layers. |  |  |  | RHi: 1. From Scott's XML Sample Documentation: 8. There is an inconsistency between the SDD spreadsheet/SharePoint site (SDD sprd) and the XML file when it comes to object type names and references to objects (attributes) scattered throughout the SDD. In the XML file, ConstructAssembly is the name of the object type (as specified in the SDD sprd) and each surface object that references a ConstructAssembly uses an attribute called ConstructionReference. Likewise, the Material object type (from SDD sprd) is referenced by an attribute array called MaterialReference. This was a last minute change without full SDD working group consultation and may therefore be subject to change down the road. DP: The definition of ConstructAssembly as an array can be done in the Schema as a sequence of the same type, but the XML generated without a schema doesn't. Not sure where the attributes ConstructionReference and MaterialReference come from. There is a Referenced Object column and the idea is that it would return the object name, which is what is represented in the XML ConstructAssembly elements. SAC: I had to add some stuff here immediately prior to wrapping up the SDD XML for NREL, in part due to commetns from Rob & Jason. Changing names of properties should not be a problem, but I think Jason raised the concern that the name of a property in one object (Material[10] here) should not be identical to the name of anothe property or object elsewhere in the schema, and I tend to agree (though the ruleset database CAN handle non-unique names fine if need be).
CoolingThermostatSchedule | CoolingTstatSch |  |  |  |  | Heterogeneous
DaylitZone |  | OccupancyArea | DaylitZoneType | Skylight |  | Heterogeneous | [8 empty] | RHi: 1. Is this consistent with new Daylighting code language? Probably incomplete at this point. DP: Yes, it is now called Daylit zone in the standards. RHi: Resolution - Leave as placeholder pending Daylighting code. DP: Resolved - this is what it is called in 45 day language
Window
Door |  | ExteriorWall | DoorType | ConstructAssembly |  | Heterogeneous |  |  |  | An opening in the building envelope or an internal wall, which is opaque or has less than 50% glazing. and provides passage to and from an interior space. | 2013 NR ACM: Section 5.5.6 Doors (no longer called Exterior Doors). Table 30 – Baseline Building U-factor Criteria for Doors. |  |  | SAC 2: ALSO - what about Glass Doors? Are they Doors or Windows? If Doors, then we need to add Opaque vs. Glass and if glass we need to include a FenestrationConstruction. DR: T24Sec101 definition for 'Door' indicates that if more the 50% area of door is glass, it is considered a glazed fenestration product. The 2008 NResComp (p3-29) manual has further guidance on how to deal with door that are <50% glazing: When a door has glazing of less than one-half the door area, the portion of the door with fenestration must be treated as part of the envelope fenestration independent of the remainder of the (opaque) door area. RHi: Proposed resolution - Divide opaque and glazed portions into opaque Door and glazed Window. | RHi: 1. Need referenced ConstructAssembly DP: 2013 NR ACM section 5.5.6 Doors unlike Fenestration or partitions, does not have a construction descriptor. It has only Door Type, Door Geometry and UFactor properties. Is this going to change? SAC: need to either come up w/ default constructions tied to a more simulation-oriented DoorType property or add a Construction reference. RHi: Proposed resolution - For consistency, reference a ConstructAssembly. DP: Partially Resolved: Added reference to ConstructAssembly in Door object. |  | OpeningGeometry
|  | InteriorWall | Name
Status
ExteriorFloor |  | Space | ExtFloorConstructType | ConstructAssembly |  | Heterogeneous |  |  |  | A Floor that separates the Space from surface ground | [6 empty] | ExteriorPartition Partition SurfaceGeometry
Status
Name
ExteriorWall |  | Space | ExtWallConstructType | ConstructAssembly |  | Heterogeneous |  |  |  | A Wall that separated the Space from outdoors | [6 empty] | ExteriorPartition Partition SurfaceGeometry
Status
Name
ExternalShadingObject |  | Building | ShadingCoefficient | ConstructAssembly |  | Heterogeneous | [8 empty] | RHi: 1. Need geometry; reflectance?, transmittance?, construction reference? DP: Added all shading terms as a place holder - from your last feedback. 2013 NR ACM 5.11.5 Opening Shade mentions that the "data structure describes the dimensions and position of external shading devices ... in terms of the projection distance, height above the opening, and extension distance on each side of the opening." But no mention of construction or other properties. RHi: Proposed resolutions - For ExternalShadingObject add PolyLoop and ConstructAssembly reference. Note that ConstructAssembly is opaque, so this will not support Transmittance with Schedule, which E+ supports. DP: Resolved: Added PolyLoop and reference to ConstructAssembly. DR: 2. How does E+ simulate window shades? DOE-2 has two options: one is part of window specification, the other is to use a BUILDING-SHADE object, which has the same properties that RJH indicates. Are we going to allow both specification methods? If so, there is often not a parent/child relationshipe between the ExternalShadingObject and a Window... RHI: E+ supports a variety of detached and attached shades, but for simplicity we should target one specification. I suggest Shading:Zone:Detailed. Also Add Building ShadingType enumerated value. DP: Resolved Building is now a possible parent as well as Window so we don't need a separate Building Shading Type. |  | SurfaceGeometry
|  | Skylight | ShadingType
Window
FenestrationConstruction |  | Project | AirInfiltrationRate |  |  | Heterogeneous |  |  |  | A structure specifying the construction attributes and associated thermal and optical properties that apply to all fenestration products. | 2013 NR ACM: A property building descriptor of Fenestration. Also, Section 5.11.7 Fenestration Construction common data structure for this property. T24: Fenestration construction is defined in the Fenestration Product which is any transparent or translucent material plus any sash, frame, mullions and dividers, that fills an open space in the envelope of a building, such as a window, sliding glass door, French door, skylight, curtain wall, garden window, or an open space in a door where the opening is more than one half of the door area. |  |  | RHi: 1. I still have concerns about no layered representation of fenestration constructions. DP: We can create a fenestration construction assembly that consists of material layers, but currently the Standards do not define acceptable materials for fenestration in their construction assembly tables.
DividerMinimalSpacing
DividerThroughPanes
FenestrationFraming
FenestrationFramingThermalBreak
FenestrationOperability
GlazingForm
GlazingMaterial
GlazingTint
PanesDivider
PanesPerLite
RelativeSolarHeatGain
SolarHeatGainCoefficient
SolarReflectance
UFactor
VisibleTransmittance
FloorAboveCrawlSpace |  | Space | Name | ConstructAssembly |  | Heterogeneous |  |  |  | A Floor that is placed above a CrawlSpace | [6 empty] | ExteriorPartition Partition SurfaceGeometry
Status
HeatingThermostatSchedule | HeatingTstatSch |  |  |  |  | Heterogeneous
InteriorFloor |  | Space | Name | ConstructAssembly |  | Heterogeneous |  |  |  | A Floor that separates the Space from another interior Space | [6 empty] | InteriorPartition Partition SurfaceGeometry
Status
InteriorWall |  | Space | Name | ConstructAssembly |  | Heterogeneous |  |  |  | A Wall that separates the Space from another interior Space |  |  |  |  | NREL: We can handle interior surfaces that are entirely inside a space. We can also handle surfaces that bound a space, but are not actually there in the real design (air walls). |  | InteriorPartition Partition SurfaceGeometry
Status
InternalShadingDevice |  | Skylight |  |  |  | Heterogeneous |  |  |  |  | 2013 T24 does not regulate interior shading devices. 2013 NR ACM has a bldg desc, Internal Shading Devices with rules regarding the shading schedule |  |  | RHi: 1. Need material/construction?, control?, schedule? DP: 2013 NR ACM Internal Shading Devices descriptor does not mention construction properties. It does state that solar gain greater than x, should activate closing blinds. RHi: E+ supports extensive inside/between layers/outside shade/blind/screen alternatives with a variety of controls (schedule, solar gain, interior illuminance, glare, temperatures, etc.). We can't support everything without a lot of effort. We should only support what the codes care about. But that could still be tricky. Are shades assumed to be opaque pure reflectors?
Window
LoadScheduleHoliday | LdSchedHDay | LoadScheduleWeekly |  |  |  | Property Array | 24 |  | LoadPercentageHourly | Contains an array of 24 LoadPercentageHourly element for each hour of a day designated as a holiday. | 2008 NR ACM Found in Schedule tables N2-8 through N2-12 2013 NR ACM Found in appendix for schedules
LoadSchedules | LdSched | Building |  |  |  | Heterogeneous |  |  |  | A collection of Load Schedule Weekly elements. All load schedules required for a building energy analysis will be found in this collection | 2008 NR ACM Load Schedules are all found in tables N2-8 through N2-12 2013 NR ACM LoadSchedules are found in appendix C |  |  | RHi: 1. Is this just a container for all schedules? We don't have containers for elements like ConstructAssembly or Boiler or ... DP: This is a BESM term and should probably be excluded. Now that we have array objects we can handle schedules that way.
LoadScheduleSaturday | LdSchedSatDay | LoadScheduleWeekly |  |  |  | Property Array | 24 |  | LoadPercentageHourly | Contains an array of 24 LoadPercentageHourly element for each hour of a Saturday. | 2008 NR ACM Found in Schedule tables N2-8 through N2-12 2013 NR ACM Found in appendix for schedules
LoadScheduleSunday | LdSchedSunDay | LoadScheduleWeekly |  |  |  | Property Array | 24 |  | LoadPercentageHourly | Contains an array of 24 LoadPercentageHourly element for each hour of a Sunday. | 2008 NR ACM Found in Schedule tables N2-8 through N2-12 2013 NR ACM Found in appendix for schedules
LoadScheduleWeekday | LdSchedWkDay | LoadScheduleWeekly |  |  |  | Property Array | 24 |  | LoadPercentageHourly | Contains an array of 24 LoadPercentageHourly element for each hour of a week day. | 2008 NR ACM Found in Schedule tables N2-8 through N2-12 2013 NR ACM Found in appendix for schedules |  |  | RHi: 1. What about a restaurant that's closed on Monday? DP: Not sure what the difference is between the weekend day schedules and the holiday schedule. Do they all represent when the place is closed? SAC: This partly gets back to how detailed we get - simulation vs. standards. To date, schedules are dictated by the code and I am not aware of any situations where there was variation between week days. However, w/ the potential for schedule changes and the value to user input simulation, perhaps we should allow for individual (M-F) week day schedules??
LoadScheduleWeekly | LdSchedWeek | LoadSchedules | LoadScheduleOccupancy |  |  | Heterogeneous |  |  |  | Contains the LoadScheduleWeekday, LoadScheduleSaturday, LoadScheduleSunday, and LoadScheduleHoliday for a specific Load Schedule Occupancy and Load Schedule Type | Found in N2-8 through N2-12 Schedule tables |  |  | RHi: 1.. I don't understand how these weekly schedules are referenced by different loads (people, lights, etc.) for different OccupancyArea(s). DP: I haven't messed with mapping space occupancy types to schedule occupancy tpes yet as there appeared to still be discussion on what to use for schedules. If it has been settled, we can map space occupancies to schedule occupancies and that would relate a schedule to an OccupancyArea (I think) RHi: 2. Also, I don't see something like Start/End dates supporting different weekly schedules over the course of a year. |  |  | LoadScheduleIdentifier
LoadScheduleType
Material |  | Project | Density |  |  | Heterogeneous |  |  |  | Used in layers in a Construction Assembly and records the type of material and it's characteristics that effect heat transfer such as specific heat capacity, density, thickness. | The 2008 Standards do not use a layer by layer approach to construction assemblies although JA 4 does describe underlying layer calculations used in the construction assembly tables that assign values for U-Factor and other thermal measurements. 2013 JA4 may replace defined construction assemblies with the layer approach |  |  | NREL: 1. Thickness plus ThermalConductivity is sufficient to calculate RValue. Should we check that these two calculation methods are equivalent to some tolerance?
Roughness
RValue
SolarAbsorbance
SpecificHeat
ThermalAbsorptance
ThermalConductivity
Thickness
VisibleAbsorptance
OccupancyArea | OccupArea | Space | Area |  |  | Heterogeneous |  |  |  | A subdivision of a Space. It may have a unique occupancy type and has known space uses such as occupant loads, interior lighting and receptacle and process loads. | There are a number of times when a Space is subdivided into OccupancyAreas usually for lighting regulations. 2013 NR ACM Space function is the equivalent to OccupancyArea and is defined as a sub-component of a thermal zone that has specific baseline lighting requirements and for which there are associated defaults for outside air ventilation, occupancy, receptacle loads, and hot water consumption. An HVAC zone may contain more than one space function. |  |  | RHi: 2. Do we need Area? PolyLoop?. SAC: Seems like we would want an Area here, since most of the occupancy and load properties are defined in code (and various source materials as occup or load densities. Including an area allows these properties to remain in this native (density/intensity) form and allows users to easily scale up/down all loads via Area adjustments. This will probably add something to the ruleset list - to check sums of OccupancyArea Areas vs. parent Space Area...I had not invisioned PolyLoop here, but interested in the discussion... RHi: OK with Area, pending Daylighting code need for PolyLoop. DP: Area Resolution - Area property added to OccupancyArea. | RHi: 1. Are there potentially multiple OccupancyArea(s) in a Space, or is this handled by SpaceOccupancyAncillary? We should discuss the relationship between OccupancyArea, SpaceOccupancy, and SpaceOccupancyAncillary; and their associated loads. DP: Resolved: Space can have more than one OccupancyArea. Each OccupancyArea has only one SpaceOccupancy. Ancillary space types have been removed. |  | SpaceLoads
Name
SpaceOccupancy
InfiltrationLoad
LightingLoad
LoadScheduleOccupancy
LoadScheduleType
OccupantDensity
OccupantLatentHeatRate
OccupantSensibleHeatRate
ReceptacleLoad
VentilationLoad
WaterHeatingLoad
PolyLoop |  | Door |  |  |  | Object Array | varies | CartesianPoint |  | A list of coordinates that make up a polygon in three-dimensional space. All coordinates must lie on the same plane. The right-hand rule applies for defining the outward normal of a surface: For every surface, points must be defined in order, such that the direction of (the average cross-product between (any point, the centroid of the surface, and the next point)) points in the direction of the outward normal, which is a vector pointing away from the associated/parent zone/space. Includes a number of child CartesianPoint objects, with a maximum allowed based on the default quantity of polygon vertices allowed in EnergyPlus (this is 120 in DOE-2.2). | NA |  |  |  | NREL: Unless we receive other direction, we plan to ignore the PolyLoop item under Space, per Scott’s description of that object. RHi: Agreed
Skylight
Window
ExternalShadingObject
ExteriorFloor
ExteriorWall
FloorAboveCrawlSpace
Roof
Ceiling
CeilingBelowAttic
InteriorFloor
InteriorWall
UndergroundFloor
UndergroundWall
Space
Project | Proj |  | PermitScope |  |  | Heterogeneous |  |  |  | The root structure and contains all information about the construction or remodeling project. | Projects are defined in terms of the applied building permit coverage. Much of the project level information is recorded on the compliance forms, e.g. CF-1R, that are filed for the permitted construction project |  |  |  | JG: 1: Add "LightingPlansSumbitted" from 5.4.2 ACM. DP: Resolved: Added PermitScope which defines the scope of plans submitted for the project |  | ComplianceChoices GeographicAndClimateData
BuildingClassificationMethod
ClimateZone
Elevation
Latitude
Longitude
ClimateZoneCity
ClimateZoneCounty
Roof |  | Space | Area | ConstructAssembly |  | Heterogeneous |  |  |  | Makes up the top exterior boundary of the building envelope. It is generally horizontal or sloped less than 60 degrees from horizontal. | T24: Roof is the outside cover of a building or structure including the structural supports, decking, and top layer that is exposed to the outside with a slope less than 60 degrees from the horizontal. 2013 NR ACM 5.5.3 Roofs Maps to Roof, which is a building descriptor | [5 empty] | ExteriorPartition Partition SurfaceGeometry
Name
RoofConstructType
SkylightRoofRatio
Status
TotalSkylightArea
Skylight |  | Roof | Name | FenestrationConstruction |  | Heterogeneous |  |  |  | A fenestration skylight product installed in a roof and includes all construction and thermal properties required for applying the Standards. | T24: Skylight is fenestration installed on a roof less than 60 degrees from the horizontal. NR ACM 2.3.5.6 Fenestration Thermal Properties 2013 NR ACM Maps to Skylight Fenestration. In the building description Fenestration, skylight is defined as fenestration that has a tilt of less than 60° from horizontal. | [5 empty] | OpeningGeometry
SkylightCurbType
Status
Space |  | BuildingStory | SpaceConditioningType |  | ThermalZone | Heterogeneous |  |  |  | The fundamental unit of space conditioning based on the occupancy type | Title 24 Part 6 Section 101 definitions: ZONE, SPACE-CONDITIONING, is a space or group of spaces within a building with sufficiently similar comfort conditioning requirements so that comfort conditions, as specified in Section 144(b)3 or 150(h), as applicable, can be maintained throughout the zone by a single controlling device. 2013 NR ACM Space maps to HVAC Zone which is defined as follows: HVAC zone is a physical space within the building that has its own thermostat and zonal system for maintaining thermal comfort. It isn't clear how this differs from Thermal Block |  |  | 2. JG: Need Classification from 5.4.1 ACM. Is this a small enough unit of area? DP: Subareas: We have OccupancyArea which allows more than one to be defined for a Space. 3. JG: Subareas are referenced as part of 5.4.2 ACM. ACM 5.4.6 Commercial Refrigeration Equipment is shown at space level, where is it supported in SDD? How about support for Elevators, Escaltors and Moving Walkways as appear in 5.4.7 of the ACM or Processs Gas equipment 5.4.8. DP: Refrig.equipment: just added to the SDD SP lists, so not in this spreadsheet, We will have to associate it with the space as floor area is used in its rules. Elevators and escalators & Process gas equip: we need to check with John Arendt if they will be in the final ACM? They are not regulated in T24 part 6 or the previous ACM. 4. RJH: SDD Working Group discussed simplifying ThermalZone-Space-OccupancyArea structure. After email thread with NREL I propose the following: A) Keep Project-Building-BuildingStory-Space hierarchy to minimize impact on current structure; B) Keep surface geometry at Space object (need not be closed volume if representing portion of actual room for lighting area purposes); C) Restrict Space to 1-and-only-1 OccupancyArea; D) Restrict Space/OccupancyArea to 1-and-only-1 SpaceType and 0-1 LightingArea/DaylightingArea; E) Keep ThermalZone as group of 1-N Spaces, but restrict to contiguous Spaces; F) Support Mulitplier on ThermalZone for simulation efficiency (would this lose BuildingStory information required by Title24?); G) Consider renaming Space to OccupancyArea or other term more consistent with T24/COMNET/2013ACM. | 1. NREL: Are SpaceVolume and SpaceArea intended to override the energy model geometry in the heat transfer model? Are the EnergyPlus Zone fields volume and floor area sufficient for this purpose? RESOLUTION: Yes, floor area and volume for space will override energy model geometry. This should be documented with these properties and in the schema |  | SpaceGeometry
FloorArea
Volume
UndergroundFloor |  | Space | Name | ConstructAssembly |  | Heterogeneous |  |  |  | A Floor that separates the Space from underground environment | [6 empty] | Partition SurfaceGeometry UndergroundPartition
Status
UndergroundWall |  | Space | Name | ConstructAssembly |  | Heterogeneous |  |  |  | A Wall that separates the Space from underground environment | [6 empty] | Partition SurfaceGeometry UndergroundPartition
Status
Window |  | ExteriorWall | Name | FenestrationConstruction |  | Heterogeneous |  |  |  | Vertical fenestration installed an opening in an exterior wall. It may be a window, curtain wall, garden window and a door with 50% or more glazing. | From the glossary definition: WINDOW is fenestration that is not a skylight. | [5 empty] | OpeningGeometry
Status
WindowStyle

## Properties
Term | Term Short Form | DataType | Units | Enumerations | Definition | Standards Reference | Constraints | Set By | Issues | Resolved Issues | Critical Path Issue
AboveGradeStoryCount |  | integer | none |  | An attribute of the Building object for recording the number of above grade stories in the building which is used in several rules. | T24/CBC/Nonres Compliance Manual: The total number of stories in the building that have the finished floor surface entirely above the plane of grade or 50% of its volume above grade. Table N2-13 Standard Design HVAC System Selection tests if building has 3 or fewer stories above grade.
AboveWaterProofMembraneRValueFactor |  | decimal | none |  | Applied to the RValue of some roofs in climate zones 1 and 16 if the continuous insulation is installed above the roof's waterproof membrane. | Table 4.2.1, Table 4.2.2, Table 4.2.3, Table 4.2.4, Table 4.2.5, Table 4.2.6, and Table 4.2.7
AirInfiltrationRate |  | decimal | ft3 per min ft2 |  | Uncontrolled inward air leakage from outside a building or unconditioned space, including leakage through cracks and interstices, around windows and doors, and through any other exterior or demising partition or pipe or duct penetration. | T24 Definition: Infiltration is uncontrolled inward air leakage from outside a building or unconditioned space, including leakage through cracks and interstices, around windows and doors, and through any other exterior or demising partition or pipe or duct penetration. Section 116 defines mandatory air infiltration rates for fenestration products. 2013 NR ACM Maps to Infiltration which means the same thing. However, infiltration is an attribute of Thermal Block.
Area |  | decimal | ft2 |  | The two dimensional extent of a surface. For horizontal rectangular areas, such as most floor areas, it is calculated by multiplying the linear extent of each dimension, usually referred to as Width and Length. For vertical rectangular surfaces such as walls, the vertical linear dimension is usually referred to as Height and the horizontal may be called Width or Length. | There is no formal defintion of the measurement of area in Title 24 Part 6. There is a definition for conditioned floor area which states that it is the floor area (in square feet) The dimensions of rectangular surfaces such as walls, windows, floors needs to be calculated to get the area of the surface.
AssemblyContext |  | enumerated list | none | FieldFabricated | The context in which a building element was assembled for installation. | An example of how Assembly Context affects how rule targets are assigned: Title 24 Part 6 Section 116 – Mandatory Requirements For Fenestration Products And Exterior Doors are different for fenestration that os site built, manufactured or field fabricated.
Manufactured
SiteBuilt
Azimuth |  | decimal | deg arc |  | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | T24 Part 6 never mentions azimuth even in its definition of cardinal orientations. JA has one table that depends on the azimuth: Table NA4-1. However, the Res ACM and the NR ACM use azimuth extensively. e.g. Res ACM: 3.5.5-Reporting requirements on CF-1R; 3.7.7-Fenestration Calculations; Appendix B-Algorithms and Procedures for Calculating PV Production; NR ACM: 2.3.3.3 Surface Azimuth and Tilt of Exterior Partitions
BuildingClassificationMethod | BldgClassifyMethod | enumerated list | none | SpaceBySpace | One of two methods of assigning building occupancy for the project - either whole building or at the space level. This is dependent on whether the user have submitted lighting plans for the whole building or not. | 2013 NR ACM building classification method assigns whole building or space by space occupancy type. 2008 Title 24 Part 6) Tables 146E and 146F) and 2008 NR ACM Tables N2-5, N2-6 and N2-7 - in lighting compliance there are two levels that are similar: the complete buildng or area occupancy.
WholeBuilding
BuildingTotalFloorArea | BldgTotlFloorArea | decimal | ft2 |  | Derived by summing Total Conditioned Floor Area and Total Unconditioned Floor Area. | Title 24 Section 146 (c) Complete Building Method. The Complete Building Method involves the entire building which is defined as including all conditioned and unconditioned space which a building permit is sought plus any conditioned and unconditioned space of the existing structure when applying lighting compliance to the complete building. In the NR ACM this is applied when using Table N2-5
CBCOccupancyGroup | CBCOccup | enumerated list | none | GroupAAssembly | One of the occupancy categories defined by the California Building Code (CBC). | Title 24 Part 6 uses the CBC Occupancy Group infrequently. It is evaluated to limit the use of display perimeter in calculating window wall ratio.
GroupBBusiness
GroupEEducational
GroupFFactory
GroupMMercantile
GroupR1Residential
GroupR2Residential
GroupSStorage
CeilingConstructionType |  | enumerated list | none | Suspended | One of several general types of ceiling construction. | Title 24 Part 6 Tables 143A/B/C use the same construction types for Roof and Ceiling JA 4 has several tables of Roof and Ceiling construction assemblies.
TBar
CFactor |  | decimal | Btu per h ft2 F |  | A measurement of thermal conductivity of a material and is used in the JA 4 tables for masonry and concrete walls | JA 1 glossary defines C-VALUE (ALSO KNOWN AS C-FACTOR): the time rate of heat flow through unit area of a body induced by a unit temperature difference between the body surfaces, in Btu (hr. x ft.2 x °F). The JA IV tables all refer to C-Factor and never mention C-Value
ClimateZone |  | enumerated list | none | 1 | One of the geographic areas defined in Title 24 that cover the state of California which are numbered 1-16. | T24: CLIMATE ZONES are the 16 geographic areas of California for which the Commission has established typical weather data, prescriptive packages and energy budgets. Climate zone boundary descriptions are in the document "California Climate Zone Descriptions" (July 1995), incorporated herein by reference. FIGURE 101-A is an approximate map of the 16 climate zones.
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
ClimateZoneCity |  | enumerated list | none
ClimateZoneCounty |  | enumerated list | none
ConcreteWebPercentage |  | decimal | none |  | An attribute of concrete sandwich panel wall construction assembly and affects the assignment of building performance metrics like UFactor | Joint Appendix 4 Table 4.3.7 – Properties of Concrete Sandwich Panels: assigned values are dependent on the percentage of wall that is solid concrete and ties together two concrete layers, which is the Concrete Web Percentage.
Coordinate |  | decimal | ft |  | The x, y or z length measured from an origin. |  |  |  | NREL: 1. A more formal/programmatic mechanism in the XML/XSD for specifying units would be appreciated RHi: Units = ft? DP: Resolved? - I assigned ft as ft - does everyone agree?
DaylitZoneType |  | enumerated list | none | PrimarySidelit | Defines whether the DaylitZone is under a skylight or next to a window or some distance from a window |  |  |  |  | RHi: 1 Check 45 day language for Daylighting DP: Resolved: This was taken from 45 day language.
SecondarySidelit
SkylitDaylit
Density |  | decimal | lb per ft3 |  | An attribute of a material and is the measure of how much mass is contained in a given unit volume. This is the classical definition of density: mass/volume. | When used with material, Density is expressed as mass/area. For example the Density of roofing products is expressed in lb/ft2 but in JA 4 it is used as mass/volume. However, elsewhere in JA 4 the density of materials is expressed as lb/ft3 |  |  | NREL: 1. A more formal/programmatic mechanism in the XML/XSD for specifying units would be appreciated
DisplayPerimeter |  | decimal | ft |  | The length of an exterior wall in a building of CBC Occupancy Group B; F Div1, or M, that immediately abuts a public sidewalk, measured at the sidewalk level for each story that abuts a public sidewalk. It can be derived using the CBC Occupancy type and the Width dimension of the Exterior Wall. | T24 definition: DISPLAY PERIMETER is the length of an exterior wall in a building of CBC Occupancy Group B; F Div1, or M, that immediately abuts a public sidewalk, measured at the sidewalk level for each story that abuts a public sidewalk.
DividerMinimalSpacing |  | decimal | in |  | The measurement of the width of the spacer between double panes in inches. If it is less than 7/16 in, 0.05 is added to the UFactor. | T24: Section 116 Table 116-A Note 1a instructs that if Divider Minimal Spacing is less than 7/16 inch wide, 0.05 should be added to the fenestration U-Factor.
DividerThroughPanes |  | boolean | none |  | A Boolean and if True, indicates that the divider goes through the fenestration pane and this causes the fenestration product U-Factor to be adjusted. | T24: Section 116 table 116-A Note 1 adjusts fenestration product U-Factors if they have dividers through the double pane. Rule from T24: Section 116 Table 116-A Note 1a See DividerMinimalSpacing term.
DoorNumber |  | enumerated list | none | DoubleDoor | The number of doors in a door unit which is either single or double and usually applies to DoorType swinging. | T24: Used in assigning air leakage rate in Section 116 (a)
SingleDoor
DoorType |  | enumerated list | none | NonSwinging | An enumeration with values of swinging and non-swinging. Non-swinging would include sliding doors and roll-up doors. | Title 24 Table 143-A/B and C assign U-Factor based on whether the door is swinging or non swinging. 2013 NR ACM Maps to Door Type with same two values of swinging and non-swinging.
Swinging
Electric Equipment Power |  | decimal | W |  |  |  |  | User
Electric Equipment Power Density |  | decimal | W per ft2 |  |  |  |  | User
ElectricalPower |  | decimal | W |  | Electrical power expressed in the SI unit of a watt which is the power dissipated by a current of 1 ampere flowing across a resistance of 1 ohm in 1 second. 1,000 watts is called a kilowatt. 1 watt equals 1 joule (J) of energy per second | The most common usage in the Standards is for expressing lighting electrical energy in watts. There are also a number of energy efficiency rating systems for HVAC equipment that are used in the Standards that use electrical energy expressed in SI units of watts or kilowatts in the calculations including EER, HSPF and SEER
Elevation |  | decimal | ft |  | The height of a land surface above sea level | Joint Appendix 2 defines climate data and includes latitude, longitude and elevation for the selected representative city in each of the 16 climate zones.
EnergyPerArea |  | decimal | Btu per ft2 |  | An amount of energy normalized by an area, typically the floor area of a building or zone. | In Title 24 Section 141 (a) Energy Budget defines the units "expressed in Btu per square foot of conditioned floor area per year" Conflict: Section 141 (a)1. Space-conditioning budget states that the space-conditioning budget is the TDV energy which are different units, specifically: kBtu/therm for gas and propane, and kBtu/kWh for electricity.
EnergyPerPerson |  | decimal | Btu per person |  |  |  |  | User
EnergyUse |  | decimal | Btu |  |  |  |  | User
EnergyUseIntensity |  | decimal | Btu per ft2 |  |  |  |  | User
ExtFloorConstructType |  | enumerated list |  | MassHeavyFloor | A general category of floor construction which is used in prescriptive and performance compliance for assigning UFactor. | Title 24 Part 6 Table 143A assigns UFactor to floors depending on the FloorConstructionType which has two values: metal building; wood framed and other. 2008 NR ACM Table N2-1 – Standard Design Construction Assemblies from Reference Joint Appendix JA4 also refers to FloorConstructionType values which it calls "Class." 2013 NR ACM 5.5.5 Exterior Floors Maps to Floor Type which defines these types: mass floor, metal joist floor, and wood and other floors.
MassMediumFloor
MetalFramingFloor
WoodFramingAndOtherFloor
ExtWallConstructType |  | enumerated list | none | MassHeavyWall | A general category of wall construction which is used in prescriptive and performance compliance for assigning UFactor | Title 24 Part 6 Table 143A assigns UFactor for walls based on the WallConstructionType. 2008 NR ACM Table N2-1 – Standard Design Construction Assemblies from Reference Joint Appendix JA4 also uses WallConstructionType values which it calls "Class." 2013 NR ACM 5.5.4 Exterior Walls Maps to Wall Type.
MassLightWall
MassMediumWall
MetalBuildingWall
MetalFramingWall
WoodFramingAndOtherWall
FenestrationFraming |  | enumerated list | none | MetalFramingCurtainWall | The type of frame used for a fenestration product which may be a window, door or curtain wall. | Title 24: Section 116 Fenestration Framing in Tables 116A/B are defined as metal or nonmetal and metal is further broken into frames with thermal break and those with no thermal break. The absorbance and conductance values which are dependent on the Fenestration Frame characteristics, are used in calculating thermal properties for fenestration products. 2013 NR ACM Vertical Fenestration Type defines the type of frame but the values are a little different: nonmetal framing, metal framing for curtain wall/storefront, metal framing for entrance door, and metal framing all other.
MetalFramingDoor
MetalFramingOther
NonMetalFraming
FenestrationFramingThermalBreak |  | enumerated list | none | NoThermalBreak | An attribute that is used to assign mandatory default U Factors and SHGC for fenestration products. Values are: Thermal Break and No Thermal Break. | Section 116 Tables 116-A/B assign U Factor and SHGC depending on the fenestration frame type which may or may not have a thermal break.
ThermalBreaK
FenestrationOperability |  | enumerated list | none | Fixed | The operation capability, if any, of a fenestration product. | Fenestration Operability evaluates in assigning default Solar Heat Gain Coefficient and U Factor values in tables 116-A & B. 2013 NR ACM Used in Table 50 – Baseline Building Criteria for Vertical Glazing for 90.1 2001.
Operable
FFactor |  | decimal | Btu per h ft F |  | The quantity of heat that will flow through a unit area of the material when the temperature difference through the material is 1 degree F. | This is referred to as F-Factor and is defined in a measurement of heat transfer in Btu/(hr x ft x F). It is used mainly for floor slabs, because heat loss is more closely proportional to the length of the perimeter of the slab than to its area, F-factor is represented by heat over a distance rather than heat over an area. Essentially, the only difference between F-factor and U-factor is that U-factor is over an area whereas F-factor is over just length (ft2 vs. ft).
FloorArea |  | decimal | ft2 |  | Used as the measurement of conditioned and unconditioned floor area for Envelope and Zone and is calculated by measuring the length dimensions starting at the outside surface of the walls that enclose the space. | 2008 NR ACM states that Conditioned Floor Area as the floor area (in square feet) of enclosed conditioned space on all floors of a building, as measured at the floor level of the exterior surfaces of exterior walls enclosing conditioned space. Where areas are bounded or separated by interior partitions, the floor space occupied by those interior partitions shall not be included in any area. 2013 NR ACM In 6.4 Space Uses: Area shall be measured to the outside of exterior walls and to the center line of partitions. |  |  | NREL: 1. A more formal/programmatic mechanism in the XML/XSD for specifying units would be appreciated
FloorSlabHeating |  | enumerated list | none | Heated | Defines if the slab floor is heated or not and is used to assign F Factor | JA tables 4.47 and 4.4.8
Unheated
FloorToCeilingHeight |  | decimal | ft |  | The measurement of height from the top surface of the floor to the bottom surface of the ceiling in an enclosed space. | Floor to Ceiling Height measurement is used in several places in the Standards e.g. in Section Section 131 – Indoor Lighting Controls That Shall Be Installed, Floor to Ceiling Height is used in calculating skylit daylight areas. |  |  |  | RHi: 1 Units = ft? DP: Resolution - defined units as ft
FramingSize |  | enumerated list | none | 2x10 | The nominal size of construction framing members and is evaluated in some Joint Appendix 4 tables to assign UFactor to the ConstructionAssembly. | In Joint Appendix 4 many tables include Framing Size defines the size of the framing members and is one of the following values: 2x4, 2x6, 2x8, 2x10, 2x12, 2x14. Joint Appendices section 4.1: Framing size along with framing type and framing spacing defines the framing-factor which then allows the selection of a construction assembly as defined by ASHRAE 2005 Fundamentals Handbook. 2013 NR ACM Appendix of construction materials Framing/Insulation Material type does not define the framing size.
2x4
2x6
2x8
2x12
2x14
FramingSpacing |  | enumerated list | none | 16InchesOC | The distance between framing members and is evaluated in some Joint Appendix 4 tables to assign UFactor to the ConstructionAssembly. | In Joint Appendix 4 many tables include Assembly Framing Spacing as an attribute with values such as 16 inch OC (on center), 24 inches OC, and 48 inches OC. Joint Appendices section 4.1: Framing size along with framing type and framing spacing defines the framing-factor which then allows the selection of a construction assembly as defined by ASHRAE 2005 Fundamentals Handbook. 2013 NR ACM Maps to Framing/Insulation material type that has some entries for wall wood and metal framing including spacing for 16 " OC and 24" OC. These are part of the building descriptor Materials.
24InchesOC
48InchesOC
96InchesOC
Fuel Type |  | enumerated list | none |  |  |  |  | User
Gas Equipment Power |  | decimal | Btu per h |  |  |  |  | User
Gas Equipment Power Density |  | decimal | W per ft2 |  |  |  |  | User
Generated Energy |  | decimal | Btu |  |  |  |  | User
Generated Energy Intensity |  | decimal | Btu per ft2 |  |  |  |  | User
Generated Energy per Person |  | decimal | Btu per person |  |  |  |  | User
GlazingForm |  | enumerated list | none | GlazingBlock | Currently defines whether the fenestration glazing is a pane, block or panel. All GlazingForm types are either transparent or translucent. This reference data is used in assigning mandatory default U Factor and SHGC. | Section 116 Tables 116 - A/B use the glazing form to assign U Factor and SHGC values.
GlazingPanel
GlazingPane
GlazingMaterial |  | enumerated list | none | GlassGlazing | An enumeration that currently has two values: Glass and Plastic. | Tables 143-A/B assign U Factor depending on the Skylight Glazing Material which is either glass or plastic. 2013 NR ACM Fenestration Type includes material of either glass or plastic..
PlasticGlazing
GlazingTint |  | enumerated list | none | ClearGlazing | Has values of clear and tinted and is used in assigning mandatory default SHGC values. | Glazing Tint is used to establish Solar Heat Gain Coefficient of fenestration products. Specifically Table 116-B assigns SHGC dependent on Glazing Tint value. 2013 NR ACM Glazing Tint is only mentioned in section on Switchable glazing which describes a technology of applying an electric current to liquid crystal windows to darken the window simulating a tint.
TintedGlazing
GrossArea |  | decimal | ft2 |  | The total area of an exterior partition such as a wall, floor or roof including any installed fenestration products or doors. | T24 definitions only cover exterior walls and exterior roofs: GROSS EXTERIOR WALL AREA is the sum of the window area, door area, and exterior wall area. GROSS EXTERIOR ROOF AREA is the sum of the skylight area and the exterior roof/ceiling. 2008 NR ACM 2.3.1.3 Enclosed Unconditioned uses GrossArea in calculating AirInfiltrationRate. 2013 NR ACM Uses Surface Geometry to calculate the gross area of a wall, floor or roof.
HeatCapacity |  | decimal | Btu per ft2 F |  | Used in rules derived from the JA IV tables that assign Heat Capacity, the amount of heat necessary to raise the temperature in unit area of all the components of a construction assembly by 1°F. | Title 24 and JA II both define Heat Capacity as the amount of heat necessary to raise the temperature of all the components of a unit area in an assembly by 1°F. In JA IV Heat capacity (HC) values are provided in Tables 4.3.5 to Table 4.3.12 and HC units are defined in Table 4.6.2 New 2013 NR ACM states: ... use volume, density, and specific heat of the component wall materials to calculate the heat capacity
HeatingRate |  | decimal | Btu per h person
Height |  | decimal | ft |  | Measures the vertical extent of a vertical rectangular surface such as a wall or door or a space. Units: feet. | Height is used in the Standards to measure the vertical extent of a building component e.g. Wall, or the vertical distance between two building components e.g. between the ceiling and the roof.
Horsepower |  | decimal | hp |  | A measure of a motor’s mechanical ability to deliver the torque required for the load at the motor's rated speed. There are several different measurements of a motor's Horsepower, including nominal horsepower and brake horsepower.
InfiltrationLoad |  | decimal | ft3 per min ft2 |  | Leakage or flow of outdoor air into the building or space through openings in the building or space envelope, whether intentional or unintentional. The driving force for infiltration is a negative pressure in a space or building relative to the exterior of the building envelope. | 2008 NR ACM 2.4.1.6 Infiltration |  |  |  | RHi: 1. No units? Definition? DP: Resolved - assigned units and provided definition.
InsulationForm |  | enumerated list | none | Batt | One of several descriptors defining whether the insulation is rigid board, foam or batt. | In Joint Appendix 4 some tables for roofs and walls assign different U Factors for cavity insulation depending on two forms of insulation: batt or foamed plastic or cellulose. Rigid board is the form used for continuous insulation. Thermal blocks are used on some metal building roofs. 2013 NR ACM Qualities of Insulation are defined in Materials library Appendix . There are over 60 different entries for Insulation which include in the name a description of the form..
Foam
RigidBoard
ThermalBlock
InsulationLayer |  | enumerated list | none | InsideLayer | Defines if wall insulation layer is on the inside or outside. This is used in calculating UFactor when there are insulation layers on both the inside and outside of a mass wall. | JA 4 4.1.4 Insulating Layers on Mass and Other Walls
OutsideLayer
InsulationPlacement |  | enumerated list | none | CavityAttic | An enumeration of possible placements of insulation in a construction assembly. | JA 4 tables specify RValues specific to the placement of the insulation in the construction assembly.
ContinuousAboveDeckSleepers
ContinuousBelowDeck
CavityFraming
CavityFurring
OverSuspendedCeiling
SlabFullyInsulated
SlabHorizontal
SlabVertical
ContinuousAboveWaterproofMembrane
ContinuousAboveDeckNoSleepers
InsulationRValue |  | decimal | h ft2 F per Btu |  | A measure of thermal resistance of an insulating material used in a pre-defined ConstructionAssembly or individual construction layer or used to insulate ducts or equipment like a water heater. It is usually expressed in whole number units of (hr x ft² x ºF)/Btu but can be a decimal value e.g. JA IV 4.1.5 Wood Based Sheathing R-values | JA 4 tables list InsulationRValue for different types of roof, wall and floor constructions 2013 NR ACM R-Value is defined in the construction assemblies for different envelope components (roof, wall, floor).
InsulationType |  | enumerated list | none | Cellulose | One of several defined types used in the Joint Appendix 4 construction assembly tables. | Joint Appendix 4: A number of tables assign UFactor that depend on the type of insulating material in the construction.
Fiberglass
MineralWool
PlasticPolystyrene
UreaFormaldehyde
PlasticPolyisocyanurate
LatentHeatRatePer Occupant |  | decimal | Btu per h person |  | The rate of latent heat released per person which is a function of activity | NR ACM Table Table N2-5 and N2-6 assign values for Latent Heat per person 2013 NR ACM Latent and sensible heat generated by occupants are called the Occupant Heat Rate.
Latitude |  | decimal | deg arc |  | The angular distance of a place north or south of the earth's equator, usually expressed in degrees and minutes. | Joint Appendix 2 defines climate data and includes latitude, longitude and elevation for the selected representative city in each of the 16 climate zones. |  |  |  | RHi: 1. Units = degrees? DP: Resolved - assigned units, degree arc
Length |  | decimal | ft |  | The longer of the two dimensions of a horizontal rectangular surface. Units: feet. | The Standards use length and width interchangeably. For example the Display Perimeter which is the horizontal dimension of a vertical surface is defined as the length of an exterior wall, but the horizontal dimension for window which is also a vertical surface is referred to as width. Length measures the longest extent from one end to the other of a building component that lies in the horizontal place such as a floor or ceiling, or the longest extent of a building material. The shortest extent is the Width
LightingLoad |  | decimal | W per ft2 |  | The usage of lighting devices plugged into receptacles in a space based on the occupancy type. | 2008 NR ACM Table N2-5 and N2-6 assign values for Lighting and receptacle electric loads for a space
LoadPercentageHourly | LdPercentHr | decimal |  |  | The percentage of a full load to be applied for a specified hour of the day. | Load Percentage Hourly is the value used in the schedule tables N2-8 through N2-12 |  |  | RHi: 1 Units = fraction? As opposed to percent? DP: It would be nice to always use fraction instead of percentage, so the issue of decimal places doesn't result in numerical errors. Can we decide that anything called a percentage is expressed as a fraction?
LoadScheduleOccupancy | LdSchedOccup | enumerated list | none | Assembly | A type specifying occupancy categories used to determine load schedules. | 2008 NR ACM tables N2-8 through N2-12 are defined by these Load Schedule Occupancy types 2013 NR ACM Appendix C schedules in tables C12 - C16 use the same occupancy types |  |  | DP 1. What is the final list of occupancy types for load schedules? Currenlty listing 2008 NR ACM values, but when the list is finalized, we need to map the finer grained space occupancy types to the broader schedule occupancy types. Waiting on material from Roger on this.
DataCenter
Health
Lab
LightManufacturing
Office
Parking
Restaurant
Retail
School
Warehouse
LoadScheduleType | LdSchedType | enumerated list | none | Cooling | A list of types that specify the kind loads used to determine load schedules. Types are taken from the NR ACM Schedules in tables N2-8 through N2-12 | NR ACM has schedules for Cooling, Equipment, Fans, Heating, HotWater, Infiltration, Lights, and People in tables N2-8 through N2-12. Some are broken into finer levels such as lighting. |  |  | RHi: 1.Do we need "Ventilation" enumerated value? DP: 2008 NR ACM has an infiltration schedule but no ventialtion schedule in tables N2-8 through 12. 2013 NR ACM section 5.3.6 Natural Ventilation does have a schedule for natural ventilation for proposed buildings. So maybe the term should be NaturalVentilation? Or is this required for simulation purposes regardless of whether it is regulated? | JG: 2. Need schedules for recepticle DP Resolved: Added receptacle to enumerations
Equipment
Fans
Heating
HotWater
Infiltration
Lights
People
Receptacle
LogThickness |  | decimal | in |  | The diameter in inches of logs used in walls of log homes and is evaluated in order to assign UFactor. | JA 4 Table 4.3.11 Thermal Properties of Log Home Walls.
Longitude |  | decimal | deg arc |  | The angular distance of a place east or west of the meridian at Greenwich, England. | Joint Appendix 2 defines climate data and includes latitude, longitude and elevation for the selected representative city in each of the 16 climate zones. |  |  |  | RHi: 1. Units = degrees? DP: Resolved by assigning units
MasonryGrout |  | enumerated list | none | PartialGrout | Describes how the grout is applied in hollow masonry walls. Values include solid (every cell is grouted), partial (some cells are grouted) and partial insulated (cells not grouted are filled with insulation). | Masonry Grout value effects thermal factors assigned to hollow unit masonry walls in Joint Appendix 4
PartialInsulatedGrout
SolidGrout
MasonryHollowUnitThickness |  | decimal | in |  | Evaluated in order to assign UFactor to masonry walls. | JA4 Table 4.3.5 – Properties of Hollow Unit Masonry Walls Thickness Type.
MasonryType |  | enumerated list | none | ClayBrick | Will be an attribute of some types of Construction Assembly for walls. The values cover solid and hollow units. | In Joint Appendix 4 some tables include Masonry Type defined as Hollow Masonry Units: lightweight concrete masonry units (CMU), medium weight CMU, normal weight CMU, and hollow clay masonry units. (defined by ASTM C-90) NR ACM Table N2-1 includes masonry type Solid Unit Masonry: light weight CMU, medium weight CMU, normal weight CMU, clay brick and concrete
Concrete
ConcreteMasonryUnitLightWeight
ConcreteMasonryUnitMediumWeight
ConcreteMasonryUnitNormalWeight
ClayHollowUnit
MassPerUnitArea |  | decimal | lb per ft2 |  | The amount of material per unit of surface area. | In Title 24 Part 6 there are references to lb/ft2 which are called "weight". For example Section 143(a)1 has exceptions that refer to the weight of the roofing product as so many pounds per square foot. This measurement is also called "density" in various places in the Standards Unfortunately in JA IV weight is used with units of lb/ft3 which should be density e.g. Table 4.3.5 – Properties of Hollow Unit Masonry Walls has several weight classifiers and the text defines them as lb/ft3
MetalPanelThickness |  | decimal | in |  | Thickness of a metal panel roof or ceiling. Evaluated in order to assign UFactor. | Joint Appendix JA4 – U-Factor, C-Factor, and Thermal Mass Data Table 4.2.9 – U-factors of Insulated Metal Panel Roofs and Ceilings.
Name |  | string | none |  | A string that uniquely defines an object in the data model and is assigned in other objects as a reference to the object similar to a foreign key in relational database tables.
Net Energy Use |  | decimal | Btu |  |  |  |  | User
Net Energy Use Intensity |  | decimal | Btu per ft2 |  |  |  |  | User
Net Energy Use per Person |  | decimal | Btu per person |  |  |  |  | User
OccupantDensity |  | integer | person per thousand ft2 |  | The areal density of people associated with a space expressed in people per 1000 square feet. | 2008 NR ACM assigns occupancy loads in units of people per 1000 square feet in tables N2-5 and N2-6 |  |  | JG: 1. According to 5.4.2 ACM the input can also be absolute number of people or square feet per person. DP: We need to use one or the other. The latest 2013 Occupancy Tables received from Roger show # people per 1000 ft2
OccupantLatentHeatRate | OccuptLatHeat | decimal | Btu per h person |  | The rate of latent heat released per person which is a function of activity | 2008 NR ACM Table Table N2-5 and N2-6 assign values for Latent Heat per person 2013 NR ACM Latent and sensible heat generated by occupants are one descriptor, "Occupant Heat Rate".
OccupantSensibleHeatRate | OccuptSensHeat | decimal | Btu per h person |  | The rate of sensible heat released per person which is a function of activity | 2008 NR ACM Table Table N2-5 and N2-6 assign values for Sensible Heat per person 2013 NR ACM Latent and sensible heat generated by occupants are one descriptor, "Occupant Heat Rate".
PanesDivider |  | enumerated list | none | Divider | Indicates if a double paned fenestration product has a divider. If so this adjusts the mandatory U-Factor. | T24: Section 116 Table 166-A Note 1 gives adjustments for fenestration U-Factor based on divider characteristics.
NoDivider
PanesPerLite |  | enumerated list | none | DoublePane | An attribute of Fenestration Construction that tracks how many panes are in the fenestration product. Values are single, double and triple. | Section 116 Tables 116 - A/B use the number of panes per lite to assign U Factor and SHGC values.
SinglePane
TriplePane
PartitionThermalType |  | enumerated list | none | Adiabatic | A means of specifying the gross thermodynamic behavior of a Partition (Wall, Roof, Ceiling, Window, Floor, Fenestration) due to its relationship with other building elements or to the outside environment. | The Standards define exterior, demising and adiabatic thermal types of Partitions. 2013 NR ACM Defines exterior and interior walls, but does not mention demising or adiabatic terms.
Demising
Exterior
Interzone
Underground
PermitScope |  | enumerated list | none | PermitNRAll | Defines what compliance the project covers and depends on what plans will be submitted for a permit. | 2013 NR ACM 1.6.2 Scope of Compliance Calculations
PermitNREnv
PermitNREnvMech
PermitNRLight
PermitNRLightMech
PermitNRMech
PowerDensityArea |  | decimal | W per ft2 |  | The power in watts per unit area in square feet. | Power Density Area is used for calculating lighting power density and receptacle loads
PowerDensityFlow |  | decimal | kW per ft3 per min |  |  | NR ACM: 2.5.3.5 Fan Power has fan power index which is power per cfm
ProcessLoadLatent |  | decimal | W per ft2 |  | The latent internal energy of a building resulting from an activity or treatment not related to the space conditioning, lighting, service water heating, or ventilating of a building as it relates to human occupancy. | 2008 NR ACM 2.4.1.5 Process Loads |  | User
ProcessLoadSensible |  | decimal | W per ft2 |  | The internal energy of a building resulting from an activity or treatment not related to the space conditioning, lighting, service water heating, or ventilating of a building as it relates to human occupancy. | 2008 NR ACM 2.4.1.5 Process Loads |  |  |  | RHi: 1. Units? DP: Resolved by assigning units from standards JG: 2. Do process loads get included into receptacle? 5.4.5 lumps them together. DP: Resolved: John added Process Load text from 2008 NR ACM into section 5.4.5 JG: 3. Process loads can be both sensible and latent. Should separate these even if using ReceptacleLoad. DP Resolved: Now have two values, one for sensible and one for latent
PumpFlowRate |  | decimal | gal per min |  | The volume of fluid a pump can move through a given surface per unit time and is expressed in gallons per minute
ReceptacleLoad |  | decimal | W per ft2 |  | The usage of electrical devices plugged into receptacles in a space based on the occupancy type. | 2008 NR ACM Table N2-5 and N2-6 assign values for receptacle loads for a space
RelativeSolarHeatGain |  | decimal | none |  | The ratio of the solar heat gain entering a space, through the subject fenestration product, (corrected for external shading) to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation which is then re-radiated, conducted or convected into the space. referred to as RSGH. | From Section 143 (a)5.C The relative solar heat gain of windows is: i. The solar heat gain coefficient of the windows; or ii. Relative solar heat gain as calculated by EQUATION 143-A, if an overhang extends beyond both sides of the window jamb a distance equal to the overhang projection.
RelocatablePublicSchoolBuilding |  | boolean | none |  | A flag that indicates what tables to use for applying standards, in particular prescriptive envelope U Factors. This will be derived from the whole building occupancy type School-Public-K-12 and an Relocatable attribute of Building. | RELOCATABLE PUBLIC SCHOOL BUILDING is a relocatable building as defined by Title 24, Part 1, Section 4-314, which is subject to Title 24, Part 1, Chapter 4, Group 1. Application of prescriptive envelope standards is dependent on whether the building is a Relocatable Public School Building and whether it can be located in any climate zone.
RoofConcreteThickness |  | decimal | in |  | Thickness of concrete topping on metal deck roofs or reinforced concrete roofs. Evaluated in order to assign UFactor. | JA4 Table 4.2.6 –U-factors for Span Deck and Concrete Roofs.
RoofConstructType |  | enumerated list | none | WoodFramingAndOtherRoof | A general category of roof construction which is used in prescriptive and performance compliance for assigning UFactor. | Title 24 Part 6 Table 143A assigns UFactor to roofs depending on the RoofConstructionType which has two values: metal building; wood framed and other. 2008 NR ACM Table N2-1 – Standard Design Construction Assemblies from Reference Joint Appendix JA4 also refers to RoofConstructionType values which it calls "Class." 2013 NR ACM 5.5.3 Roofs Maps to Roof Type.
MetalBuildingRoof
RoofFireProofing |  | enumerated list | none |  | Defines the type of fireproofing installed in the Roof. This attribute is used in assigning UFactor for span deck and concrete roofs. | JA4 Table 4.2.6 –U-factors for Span Deck and Concrete Roofs
RoofingProductType |  | enumerated list | none | Asphalt Shingles | An enumeration of types of roofing products that are evaluated when assigning a rule target in the Standards. | In Title 24 EXCEPTION to Section 118(i), aged reflectance and emittance values are assigned based on whether the roofing product type is asphalt shingles or not.
Clay
ClayRoofingTiles
RoofingProductWeight |  | decimal | lb per ft2 |  | The weight of the roofing product covering 1 square foot. | In Title 24 Table 143-A/B/C Roofing product weight expressed as less than pounds per square foot is used to assign prescriptive limits on roof reflectance and emittance. 2013 NR ACM Table 44 – Baseline Building Roof Construction Assemblies has a column for Density (lb/ft2).
RotationalSpeed |  | decimal | rpm |  | The number of complete rotations (i.e. revolutions or cycles) there are per time unit and is a measurement of how fast a motor is running.
Roughness |  | enumerated list | none | MediumRough | The relative roughness of a material layer, specifically an exterior facing layer. | 2013 NR ACM Roughness has same meaning |  |  |  | RHi: 1. I thought we added "Rough" as another value in the list. DP: Resolved by adding Rough.
MediumSmooth
Rough
Smooth
VeryRough
VerySmooth
RValue |  | decimal | h ft2 F per Btu |  | A measure of thermal resistance of a type of Material found in construction layers or Insulation in a pre-defined ConstructionAssembly. It is usually expressed in whole number units of (hr x ft² x ºF)/Btu but can be a decimal value e.g. JA IV 4.1.5 Wood Based Sheathing R-values | T24 Definition: THERMAL RESISTANCE (R) is the resistance of a material or building component to the passage of heat in (hr x ft² x ºF)/Btu. Usuage: T24 Table 126-A Refrigerated Warehouse Insulation; Table 149-A Insulation Requirements For Roof Alterations Joint Appendix 4 Tables evaluate insulation RValues in order to assign UFactor
SensibleHeatRatePerOccupant |  | decimal | Btu per h person |  | The rate of sensible heat released per person which is a function of activity | NR ACM Table Table N2-5 and N2-6 assign values for Sensible Heat per person
ShadingCoefficient |  | decimal | none |  | The ratio of the solar heat gain through a fenestration product to the solar heat gain through an unshaded 1/8-inch-thick clear double strength glass under the same set of conditions. Used in calculating envelope loads in prescriptive standards. | 2013 T24 Definitions; Section 140.4 – Prescriptive Requirements For Space Conditioning Systems (b) Calculations 6. Envelope
ShadingType |  | enumerated list | none | Overhang
VerticalFin
SIPSSpacerType |  | enumerated list | none | SpacerOSBSpline | Defines the type of spacer in structurally insulated panels used in roof and wall construction. | In Joint Appendix 4 some tables include structurally insulated wall panels (SIPS) and defines whether the spacer is wood or oriented strand board. Values include OSB splines, wood spacers, (new types to be added) This is used in assigning thermal factors in the Joint Appendix 4 for performance compliance 2008 JA4 SIPS panel tables for Wall, Table 4.3.2 and Roof Table 4.2.3 evaluates these characteristics of the SIPS construction.
SpacerWood
SpacerSteelFraming
SIPThickness |  | decimal | in |  | The measurement from one side of the SIP panel to the other side | In Joint Appendix 4 Table 4.4.3 requires evaluation of the panel thickness of structurally insulated wall panels (SIPS) in order to assign UFactor.
SkylightCurbType |  | enumerated list | none | Curb | Curb or No Curb. | Tables 143 A/B assign U Factor dependent on whether the skylight is mounted on a curb or directly on the roof. 2013 NR ACM Fenestration Type (Skylights) includes whether the skylight has a curb or not.
NoCurb
SkylightRoofRatio |  | decimal | none |  | The ratio of the rough opening area of the skylights in a parent surface to the total parent surface area. This can either be a local ratio (for a single roof section) or a global ratio (for the entire roof area in the building or project). referred to as SRR. | Skylight-Roof-Ratio is mentioned in Section 143 (b) Overall Envelope TDV Energy ApproachAlso in Appendix NA5 – Overall Envelope TDV Energy Approach (Envelope Tradeoff Procedure):Calculate the proposed skylight-roof-ratio (SRRpd) by dividing the proposed design skylight area by the gross exterior roof area.
SolarAbsorbance |  | decimal | none |  | The fraction of incident solar radiation that is absorbed by the material. Solar radiation includes the visible spectrum as well as infrared and ultraviolet wavelengths. | NR ACM uses solar absorbance and describes it as follows: Absorbance is the fraction of the incident solar radiation absorbed as heat on the construction assembly’s opaque exterior surface.· Reflectance is the fraction of incident solar radiation that is reflected. Reflectance plus absorbance equal one. 2008 NR ACM 2.3.2.3 Solar Reflectance and Thermal Emittance: This section describes assigning default values for solar reflectance but states: "The reference method accepts absorptance, but not reflectance." Both can be derived from the other's value.
SolarHeatGainCoefficient |  | decimal | none |  | The ratio of the solar heat gain entering a space, through the subject fenestration product, to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation which is then re-radiated, conducted or convected into the space. often referred to as SHGC. | SOLAR HEAT GAIN COEFFICIENT (SHGC) is the ratio of the solar heat gain entering the space through the fenestration area to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation, which is then re-radiated, conducted, or convected into the space. 2013 NR ACM Fenestration Construction includes Solar Heat Gain Coefficient as an attribute.
SolarReflectance |  | decimal | none |  | The fraction of incident solar radiation that is reflected by the material. Solar radiation includes the visible spectrum as well as infrared and ultraviolet wavelengths. NOTE: For roofs, differentiate between the initial Solar Reflectance value and the three year aged value established by the Cool Roof Rating Council (CRRC). The aged value is use in Table 143A | From Title 24 Section 101 Defintions SOLAR REFLECTANCE is the ratio of the reflected solar flux to the incident solar flux. This is measured for roofing products and the three years aged reflectance value is assigned in Table 143A 2008 NR ACM .3.2.3 Solar Reflectance and Thermal Emittance Equation N2-2 SolarReflectanceAged = 0.06 + 0.70 x SolarRefectance 2013 NR ACM Maps to Reflectivity part of the exterior surface properties data structure and is applied to Roof or Exterior Wall.
SolarReflectanceAged |  | decimal | none |  | The three year aged value for Solar Reflectance established by the Cool Roof Rating Council (CRRC). Assigned a prescriptive value in Table 143A. | Assigned prescriptive value in table 143-A Rule from Table 143-AIF Roof.SurfaceGeometry.SpatialAttitude.Tilt > 9.5 deg arc AND Roof.RoofingProductWeight => 5lb per ft2 THEN Roof.ExteriorSurfaceProperties.SolarReflectanceAged = 0.15
SpaceConditioningType | SpaceCondType | enumerated list | none | IndirectlyConditioned | One of a list of categories which characterize the type of conditioning for a space. | There are definitions for the following types of space conditioning in the Standards: Conditioned Space, DirectlyConditioned Space, IndirectlyProcess SpaceRefrigerated SpaceUnconditioned Space Plenum in T24 is handled as conditioned space. Ref: NR ACM 2.3.1.1 Directly Conditioned Space Return Air Plenums 2013 NR ACM This maps to Thermal Block Type an attribute of building descriptor, Thermal Block which has the value of directly conditioned, indirectly conditioned, unconditioned or plenum. |  |  |  | JG: 1. Add DirectlyConditioned to list of enumerations DP: Resolved - It is there
ProcessEnvironmentConditioning
RefrigeratedConditioning
Unconditioned
SpaceOccupancy | SpaceOccup | enumerated list | none |  | One of a list of occupancies assigned to the OccupancyArea The terms have been derived from mapping types from Title 24 Part 6 and NR ACM definitions and tables that occupancy types, to COMNET's space by space terms. | Title 24 Part 6 has definitions for occupancy types listed in the definitions in Section 101 under Nonresidential Function Area Or Type Of Use. Many of these types are used in lighting tables to assign values to rule targets such as lighting power adjustment factor. 2008 NR ACM has Tables N2-5 and N2-6 that use occupancy types for loads and schedules. 2013 NR ACM Appendix A has space-by-space occupancy types. |  |  | RHi: 1. Does the list of SpaceOccupancy types include assigned loads? Do we want those loads to be children of SpaceOccupancy rather than OccupancyArea to avoid duplication for each Space with this SpaceOccupancy type?
SpaceVolume | Volume | decimal | ft3 |  | Measures the volume of a Space using the 3D coordinates supplied in the space geometry attributes
SpecificHeat |  | decimal | Btu per lb F |  | The quantity of heat that must be supplied to a unit mass of a material to increase its temperature by 1 degree F. | There is no formal definition of Specific Heat JA 4 in Table 4.6.2 – Rules for Calculating Mass Thermal Properties From Published Values Specific Heat (SH) units are defined as Btu/ºF-lb
StateBuilding | StateBldg | boolean | none |  | A qualifier that can be applied to any whole building occupancy type. | Suggested definition for T24: Any newly constructed building, including new addition, constructed or whose construction is managed by the State of California or existing building owned, operated and/or leased by the State of California undergoing an alteration or renovation subject to the requirements of the Standards. State Buildings must meet the Standard's requirements for service water heating and solar DHW.References: Section 113 (c) Installation.6. Service water heaters in state buildings
Status |  | enumerated list | none | ExistingAlteration | Defines if a construction or equipment is new, existing, modified, removed. Standards such as efficiency standards may not apply if a construction or equipment in a project is existing. equipment may be moved and reinstalled in the project.
New
Removed
SteelThroughInsulation |  | boolean | none |  | A Boolean attribute of concrete sandwich panel wall construction assembly and affects the assignment of building performance metrics like UFactor. | Joint Appendix 4 Table 4.3.7 evaluates Steel Through Insulation to assign UFactor, CFactor and Heat Capacity.
ThermalAbsorptance |  | decimal | none |  | The fraction of incident long wavelength radiation that is absorbed by the material. This parameter is used when calculating the long wavelength radiant exchange between various surfaces and affects the surface heat balances (both inside and outside as appropriate). Units: none | 2008 NR ACM 2.3.2.3 Solar Reflectance and Thermal Emittance, defines absorptance as the fraction of the incident solar radiation absorbed as heat on the construction assembly’s opaque exterior surface and absorptance is equal to 1 minus reflectance.
ThermalCapacity |  | decimal | Btu per h |  | The rate of thermal energy transfer expressed in unit of energy per unit of time. | Title 24 Part 6 and NR ACM use the unit Btu/h to express the capacity or size of different HVAC equipment e.g. Tables 112A,B and E.
ThermalConductivity |  | decimal | Btu per h ft F |  | The thermal conductivity of a material of unit thickness is the quantity of heat that will flow through a unit area of the material when the temperature difference through the material is 1 degree F. | This is referred to as F-Factor and is defined in a measurement of heat transfer in Btu/(hr x ft x F). It is used mainly for floor slabs, because heat loss is more closely proportional to the length of the perimeter of the slab than to its area, F-factor is represented by heat over a distance rather than heat over an area. Essentially, the only difference between F-factor and U-factor is that U-factor is over an area whereas F-factor is over just length (ft2 vs. ft). PB
ThermalMassCapacitance |  | decimal | lb per ft2 |  | The thermal capacitance of the building contents are typically specified in terms of the composite weight of the building contents in lb/ft² | 2013 NR ACM 5.3.7 Thermal Mass |  | User
Thickness |  | decimal | in |  | Measures between two surfaces of an object, which is the dimension through an object as opposed to its length or width | Thickness is the measure of the distance between inner and outer surfaces of a building component or material. It is always given in inches which can be converted to feet
Tilt |  | decimal | deg arc |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards
Time Dependent Valuation |  | decimal | Btu |  |  |  |  | User
Time Dependent Valuation Intensity |  | decimal | Btu per ft2 |  |  |  |  | User
Time Dependent Valuation per Person |  | decimal | Btu per person |  |  |  |  | User
TimeDependentValuationElectricity |  | decimal | kBtu per kW h |  | The time varying electrical energy used by the building to provide space conditioning and water heating and for specified buildings lighting. Time Dependent Valuation (TDV) Electricity energy is calculated by multiplying the site energy use of electricity kWh, times the applicable TDV multiplier. TDV multipliers vary for each hour of the year and by energy type (electricity, natural gas or propane), by climate zone and by building type (low-rise residential or nonresidential, high-rise residential or hotel/motel). | Title 24 Section 101 – Definitions and Rules of Construction and Appendix JA3 – Time Dependent Valuation (TDV)JA3.1 Scope and Purpose: The currency used to compare energy performance
TimeDependentValuationGasPropane |  | decimal | kBtu per thm |  | The time varying gas and propane energy used by the building to provide space conditioning and water heating. Time Dependent Valuation (TDV) Gas Propane energy is calculated by multiplying the site energy use (in natural gas therms, or fuel oil or LPG gallons) for each energy type times the applicable TDV multiplier. TDV multipliers vary for each hour of the year and by natural gas or propane energy type, by climate zone and by building type (low-rise residential or nonresidential, high-rise residential or hotel/motel). | Title 24 Section 101 – Definitions and Rules of Construction and Appendix JA3 – Time Dependent Valuation (TDV)JA3.1 Scope and Purpose: The currency used to compare energy performance
TopLevelOccupancy |  | enumerated list | none | Nonresidential | The highest-level definition of building occupancy with a value of either Residential or Nonresidential. The value for TopLevelOccupancy is dependent on whether the building is used for residential or nonresidential purposes and also for residential whether the building is single or multi-family, and how many stories there are in the building. | T24 Section 100 Scope (a) Buildings Covered
Residential
TotalConditionedFloorArea |  | decimal | ft2 |  | All conditioned floor area in the Building project. It can be derived from all conditioned area in the Zones | T24: Conditioned Floor Area(CFA) is the floor area (in square feet) of enclosed conditioned space on all floors of a building, as measured at the floor level of the exterior surfaces of exterior walls enclosing the conditioned space. Many of the energy requirements of the Standards are based on conditioned floor area. In the performance approach final energy budgets are listed in kbtu/square foot.
TotalSkylightArea |  | decimal | ft2 |  | The sum of all skylights in a building. Total Skylight Area can be derived from the Fenestration Skylight object which contains all skylights in the building. | Total Skylight Area combines areas of smaller skylights into one large square skylight having an area weighted average U-factor, SHGC and visible light transmittance. T24: Skylight Area is the rough opening for the skylight. 2008 NR ACM uses Total Skylight Area for calculating various optical effects from skylights. References: NR ACM 2-47 Skylighting. 2013 NR ACM Fenestration Geometry describes the gross area of skylights in the building which is the same thing.
TotalStoryCount |  | integer | none |  | The total number of stories in a building and includes both above grade stories and any below grade stories. | 2013 NR ACM
TotalUnconditionedFloorArea |  | decimal | ft2 |  | All unconditioned floor area in the Building project. It can be derived by summing Zone Floor Area of all Zones with Space Conditioning Type set to Unconditioned | 2008 NR ACM 5.7.1.1: The total floor area of enclosed unconditioned space in the building. Used to describe compliance documentation necessary for additions when meeting the indoor lighting requirements of the Nonresidential Standards.
UFactor |  | decimal | Btu per h ft2 F |  | The overall coefficient of thermal transmittance through a layer or construction assembly. It includes air film resistance at both surfaces. | T24 Part 6 definition: U-FACTOR is the overall coefficient of thermal transmittance of a construction assembly, in Btu/(hr x ft² x ºF). Used in table 143 and JA 4 tables of construction assemblies
VentilationLoad |  | decimal | ft3 per min ft2 |  | The amount of outside air provided to a space during occupied hours divided by the floor area of that space. | 2008 Title 24 Part 6 Section 121 2008 NR ACM Table N2-5 2013 NR ACM 5.6.5.4 Outdoor Air Ventilation
VisibleAbsorptance |  | decimal | none |  | The fraction of incident visible radiation that is absorbed by the material. Visible radiation includes only a sub-range of solar radiation and excludes infrared and ultraviolet wavelengths. Units: none.
VisibleTransmittance |  | decimal | none |  | The fraction of incident visible radiation that is transmitted by the material. Visible radiation includes only a sub-range of solar radiation and excludes infrared and ultraviolet wavelengths. | 2088 NR ACM only refers to VT in the section5, Reference Method Comparison Tests. Title 24 part 6 has only a definition for the term but never explicitly applies it. 2013 NR ACM Table 50 – Baseline Building Criteria for Vertical Glazing for 90.1 2001 referred to as VT.
Volume |  | decimal | ft3 |  | The measurement of space or object calculated by multiplying the three dimensions of the space: length, width, and height. | Title 24 and JA II have a definition for conditioned volume as follows: CONDITIONED VOLUME is the total volume (in cubic feet) of the conditioned space within a building
VolumetricFlowratePerArea |  | decimal | ft3 per min ft2
WaterHeatingLoad |  | decimal | Btu per h person |  | The amount of energy required in providing hot water for each person in a space during occupied hours | 2013 NR ACM 5.9.1.2 Water Heaters 2008 NR ACM: 2.6.1 Nonresidential Service Water Heating 2.6.1.1 Algorithms and Assumptions Equation N2-95. Derived from values in Table N2-5 or Table N2-6
Weight |  | decimal | lb |  | The mass of an object or material expressed in pounds. | NR ACM uses the weight of materials and furniture and expresses it is pounds per square foot. Joint Appendix 4 Table 4.6.2 assigns Weight property the units of lb/ft2 Appendix RA3 uses weight to mean mass and uses the phrase weight-per-square-foot to express the areal density
WholeBuildingOccupancy | WholeBldgOccup | enumerated list | none |  | One of the occupancy types applied to the whole building. | Title 24 part 6 Lighting table 146E and NR ACM Table N2-5 use whole building occupancy types 2013 NR ACM Maps to Building Classification which is one of the whole building categories listed in Appendix B
Width |  | decimal | ft |  | The shorter of the two dimensions of a horizontal rectangular surface or the horizontal extent of a vertical rectangular surface Units: feet | The Standards use length and width interchangeably. For example the Display Perimeter which is the horizontal dimension of a vertical surface is defined as the length of an exterior wall, but the horizontal dimension for window which is also a vertical surface is referred to as width.
WidthInch |  | decimal | in |  | Used for measurements of lengths that are always less than a foot and could be error prone if expressed in feet. These measured are designated in Title 24 to be measured in inches. | There are a few measurements in inches for short lengths that would be difficult for inspectors to use when checking for compliance Example: Table 116-A Note 1a instructs users to adjust UFactor if the width of a spacer in a double pane window is less than 7/16 in
WindowStyle |  | enumerated list | none | GardenWindow | Defines whether the fenestration construction is a garden window, glazed door, window or other type of vertical fenestration. | Table 116-A Default Fenestration Product U-Factors requires differentiating between Greenhouse/Garden Window and other windows defined as fixed or operable.
GlazedDoor
WindowOther
WindowWallRatio |  | decimal | none |  | The ratio of the rough opening area of the window in a parent Wall to the total Wall surface area. This can either be a local ratio (for a single wall) or a global ratio (for all walls in the building or project). | T24: Window Wall Ratio is the ratio of the window area to the gross exterior wall area. Prescriptive compliance requires that the Window Wall Ratio is not greater than 40%. In Performance compliance the Window Wall Ratio of the proposed wall can be greater than 40% but the standard building will have the wall and fenestration adjusted to maintain the cap of 40% Window Wall Ratio.

## Enumerations
|  | Term | Property | Definition | Schedule Occupancy Type | CBCOccupancyGroup | Group | Top Level Occupancy Type | Term Order
Non-Occupancy Type Enumerations
AssemblyContext
|  | FieldFabricated | AssemblyContext
|  | Manufactured | AssemblyContext
|  | SiteBuilt | AssemblyContext
BuildingClassificationMethod
|  | SpaceBySpace | BuildingClassificationMethod
|  | WholeBuilding | BuildingClassificationMethod
CeilingConstructionType
|  | Suspended | CeilingConstructionType | One type of Ceiling construction.
|  | TBar | CeilingConstructionType | One type of Ceiling construction.
ClimateZone
|  | 1 | ClimateZone | CEC Climate Zone 1 |  |  |  |  | 1
|  | 2 | ClimateZone | CEC Climate Zone 2 |  |  |  |  | 2
|  | 3 | ClimateZone | CEC Climate Zone 3 |  |  |  |  | 3
|  | 4 | ClimateZone | CEC Climate Zone 4 |  |  |  |  | 4
|  | 5 | ClimateZone | CEC Climate Zone 5 |  |  |  |  | 5
|  | 6 | ClimateZone | CEC Climate Zone 6 |  |  |  |  | 6
|  | 7 | ClimateZone | CEC Climate Zone 7 |  |  |  |  | 7
|  | 8 | ClimateZone | CEC Climate Zone 8 |  |  |  |  | 8
|  | 9 | ClimateZone | CEC Climate Zone 9 |  |  |  |  | 9
|  | 10 | ClimateZone | CEC Climate Zone 10 |  |  |  |  | 10
|  | 11 | ClimateZone | CEC Climate Zone 11 |  |  |  |  | 11
|  | 12 | ClimateZone | CEC Climate Zone 12 |  |  |  |  | 12
|  | 13 | ClimateZone | CEC Climate Zone 13 |  |  |  |  | 13
|  | 14 | ClimateZone | CEC Climate Zone 14 |  |  |  |  | 14
|  | 15 | ClimateZone | CEC Climate Zone 15 |  |  |  |  | 15
|  | 16 | ClimateZone | CEC Climate Zone 16 |  |  |  |  | 16
ClimateZoneCounty
|  | Alameda | ClimateZoneCounty
|  | Alpine | ClimateZoneCounty
|  | Amador | ClimateZoneCounty
|  | Butte | ClimateZoneCounty
|  | Calaveras | ClimateZoneCounty
|  | Colusa | ClimateZoneCounty
|  | ContraCosta | ClimateZoneCounty
|  | DelNorte | ClimateZoneCounty
|  | ElDorado | ClimateZoneCounty
|  | Fresno | ClimateZoneCounty
|  | Glenn | ClimateZoneCounty
|  | Humboldt | ClimateZoneCounty
|  | Imperial | ClimateZoneCounty
|  | Inyo | ClimateZoneCounty
|  | Kern | ClimateZoneCounty
|  | Kings | ClimateZoneCounty
|  | Lake | ClimateZoneCounty
|  | Lassen | ClimateZoneCounty
|  | Los Angeles | ClimateZoneCounty
|  | Madera | ClimateZoneCounty
|  | Marin | ClimateZoneCounty
|  | Mariposa | ClimateZoneCounty
|  | Mendocino | ClimateZoneCounty
|  | Merced | ClimateZoneCounty
|  | Modoc | ClimateZoneCounty
|  | Mono | ClimateZoneCounty
|  | Monterey | ClimateZoneCounty
|  | Napa | ClimateZoneCounty
|  | Nevada | ClimateZoneCounty
|  | Orange | ClimateZoneCounty
|  | Placer | ClimateZoneCounty
|  | Plumas | ClimateZoneCounty
|  | Riverside | ClimateZoneCounty
|  | Sacramento | ClimateZoneCounty
|  | SanBenito | ClimateZoneCounty
|  | SanBernardino | ClimateZoneCounty
|  | SanDiego | ClimateZoneCounty
|  | SanFrancisco | ClimateZoneCounty
|  | SanJoaquin | ClimateZoneCounty
|  | SanLuisObispo | ClimateZoneCounty
|  | SanMateo | ClimateZoneCounty
|  | SantaBarbara | ClimateZoneCounty
|  | SantaClara | ClimateZoneCounty
|  | SantaCruz | ClimateZoneCounty
|  | Shasta | ClimateZoneCounty
|  | Sierra | ClimateZoneCounty
|  | Siskiyou | ClimateZoneCounty
|  | Solano | ClimateZoneCounty
|  | Sonoma | ClimateZoneCounty
|  | Stanislaus | ClimateZoneCounty
|  | Sutter | ClimateZoneCounty
|  | Tehama | ClimateZoneCounty
|  | Trinity | ClimateZoneCounty
|  | Tulare | ClimateZoneCounty
|  | Tuolumne | ClimateZoneCounty
|  | Ventura | ClimateZoneCounty
|  | Yolo | ClimateZoneCounty
|  | Yuba | ClimateZoneCounty
DaylitZoneType
|  | PrimarySidelit | DaylitZoneType | The area on plan directly adjacent to each vertical glazing, one window head height deep into the area, and window width plus 0.5 times window head height wide on each side of the rough opening of the window, minus any area on plan beyond a permanent obstruction that is 6 feet or taller as measured from the floor.
|  | SecondarySidelit | DaylitZoneType | The area on plan directly adjacent to each vertical glazing, two
|  | SkylitDaylit | DaylitZoneType | The area on plan under each skylight, 0.7 times ceiling height in each direction from the edge of the rough opening of the skylight, minus any area on plan beyond a permanent obstruction that is taller than the following: A permanent obstruction that is taller than one-half the distance from the floor to the bottom of the skylight.
DoorNumber
|  | DoubleDoor | DoorNumber
|  | SingleDoor | DoorNumber
DoorType
|  | NonSwinging | DoorType
|  | Swinging | DoorType | An attribute of a door and defines how the door opens.
ExtFloorConstructType
|  | MassHeavyFloor | ExtFloorConstructType
|  | MassMediumFloor | ExtFloorConstructType
|  | MetalFramingFloor | ExtFloorConstructType
|  | WoodFramingAndOtherFloor | ExtFloorConstructType
ExtWallConstructType
|  | MassHeavyWall | ExtWallConstructType | A construction assembly with a heat capacity >= 15.0 Btu/ft2-F used in walls.
|  | MassLightWall | ExtWallConstructType | A concrete assembly with a heat capacity of < 7.0 Btu/ft2-F used in wall construction.
|  | MassMediumWall | ExtWallConstructType | A construction assembly with a heat capacity >= to 7.0 Btu/ft2-F and < 15.0 Btu/ft2-F used in wall construction.
|  | MetalBuildingWall | ExtWallConstructType | Defines a type of construction used in walls. It is used in prescriptive envelope rules in table 143. For performance compliance, rules for this type of wall construction are found in Joint Appendix 4 table 4.3.9 U-Factors for Metal Building Walls.
|  | MetalFramingWall | ExtWallConstructType
|  | WoodFramingAndOtherWall | ExtWallConstructType
FenestrationFraming
|  | MetalFramingCurtainWall | FenestrationFraming
|  | MetalFramingDoor | FenestrationFraming
|  | MetalFramingOther | FenestrationFraming
|  | NonMetalFraming | FenestrationFraming
FenestrationFramingThermalBreak
|  | NoThermalBreak | FenestrationFramingThermalBreak | Means that the framing of a window or other vertical fenestration is not constructed to provide a thermal break in the flow of energy.
|  | ThermalBreaK | FenestrationFramingThermalBreak | An element of low thermal conductivity placed in an assembly to reduce or prevent the flow of thermal energy between conductive materials. In fenestration framing, it varies depending on the fenestration framing material. Aluminum window frames create a thermal break with a strip of rubber or plastic, placed between the inner and outer frame. For vinyl window frames, thermal break is usually created by an internal metal network.
FenestrationOperability
|  | Fixed | FenestrationOperability | Fenestration that does not open.
|  | Operable | FenestrationOperability | Fenestration that can open.
FloorSlabHeating
|  | Heated | FloorSlabHeating | Defines a slab floor that is heated.
|  | Unheated | FloorSlabHeating | Defines a slab floor that is not heated.
FramingSize
|  | 2x10 | FramingSize | One of the acceptable sizes for framing members. It defines a framing member with a nominal Thickness of 2 inches and a nominal Width of 10 inches.
|  | 2x12 | FramingSize | One of the acceptable sizes for framing members. It defines a framing member with a nominal Thickness of 2 inches and a nominal Width of 12 inches.
|  | 2x14 | FramingSize | One of the acceptable sizes for framing members. It defines a framing member with a nominal Thickness of 2 inches and a nominal Width of 14 inches.
|  | 2x4 | FramingSize | One of the acceptable sizes for framing members. It defines a framing member with a nominal Thickness of 2 inches and a nominal Width of 4 inches.
|  | 2x6 | FramingSize | One of the acceptable sizes for framing members. It defines a framing member with a nominal Thickness of 2 inches and a nominal Width of 6 inches.
|  | 2x8 | FramingSize | One of the acceptable sizes for framing members. It defines a framing member with a nominal Thickness of 2 inches and a nominal Width of 8 inches.
FramingSpacing
|  | 16InchesOC | FramingSpacing | One possible value for the spacing between framing members and is 16 inches measured from the center of a framing member to the center of the next framing member.
|  | 24InchesOC | FramingSpacing | One possible value for the spacing between framing members and is 24 inches measured from the center of a framing member to the center of the next framing member.
|  | 48InchesOC | FramingSpacing | One possible value for AssemblyFramingSpacing for Structurally Insulated Panels used in Roofs or Walls.
|  | 96InchesOC | FramingSpacing | One possible value for AssemblyFramingSpacing for Structurally Insulated Panels used in Roofs or Walls.
GlazingForm
|  | GlazingBlock | GlazingForm | One of the types of Glazing Geometry.
|  | GlazingPane | GlazingForm | A type of glazing geometry.
|  | GlazingPanel | GlazingForm
GlazingMaterial
|  | GlassGlazing | GlazingMaterial
|  | PlasticGlazing | GlazingMaterial
GlazingTint
|  | ClearGlazing | GlazingTint | A value for Glazing Tint indicating that the glazing is clear and has no tint.
|  | TintedGlazing | GlazingTint | A value for Glazing Tint, indicates the glazing in a Fenestration Product is not clear and is tinted.
InsulationForm
|  | Batt | InsulationForm
|  | Foam | InsulationForm
|  | RigidBoard | InsulationForm
|  | ThermalBlock | InsulationForm
InsulationPlacement
|  | CavityAttic | InsulationPlacement
|  | CavityFraming | InsulationPlacement
|  | CavityFurring | InsulationPlacement
|  | ContinuousAboveDeckNoSleepers | InsulationPlacement
|  | ContinuousAboveDeckSleepers | InsulationPlacement
|  | ContinuousAboveWaterproofMembrane | InsulationPlacement | If Roof.Insulation is placed AboveWaterproofMembrane in ClimateZone 1 or 16, the Insulation.RValue is multiplied by 0.8 before applying the rule that assigns the UFactor.
|  | ContinuousBelowDeck | InsulationPlacement
|  | InsideLayer | InsulationPlacement
|  | OutsideLayer | InsulationPlacement
|  | OverSuspendedCeiling | InsulationPlacement
|  | SlabFullyInsulated | InsulationPlacement
|  | SlabHorizontal | InsulationPlacement
|  | SlabVertical | InsulationPlacement
InsulationType
|  | Cellulose | InsulationType | Cellulose is one of the materials used in cavity insulation.
|  | Fiberglass | InsulationType | Fiberglass material used in insulation.
|  | MineralWool | InsulationType | Mineral Wool Insulation is one of the materials used in cavity insulation.
|  | PlasticPolyisocyanurate | InsulationType | Plastic Polyisocyanurate is a type of plastic used in cavity insulation and its RValue is evaluated to assign UFactor in some Joint Appendix 4 tables.
|  | PlasticPolystyrene | InsulationType | PlasticPolystyrene is is a type of plastic used in cavity insulation and its RValue is evaluated to assign UFactor in some Joint Appendix 4 tables.
|  | UreaFormaldehyde | InsulationType | Urea Formaldehyde is a type of plastic or resin used as an insulating material in some construction assemblies, and its RValue is evaluated in order to assign UFactor in some tables in Joint Appendix 4.
LoadScheduleOccupancy
|  | Assembly | LoadScheduleOccupancy
|  | DataCenter | LoadScheduleOccupancy
|  | Health | LoadScheduleOccupancy
|  | HotelFunction | LoadScheduleOccupancy
|  | Lab | LoadScheduleOccupancy
|  | LightManufacturing | LoadScheduleOccupancy
|  | Nonresidential | LoadScheduleOccupancy
|  | Office | LoadScheduleOccupancy
|  | Parking | LoadScheduleOccupancy
|  | Residential | LoadScheduleOccupancy
|  | Restaurant | LoadScheduleOccupancy
|  | Retail | LoadScheduleOccupancy
|  | Retail | LoadScheduleOccupancy
|  | School | LoadScheduleOccupancy
|  | Warehouse | LoadScheduleOccupancy
LoadScheduleType
|  | Cooling | LoadScheduleType
|  | Equipment | LoadScheduleType
|  | Fans | LoadScheduleType
|  | Heating | LoadScheduleType
|  | HotWater | LoadScheduleType
|  | Infiltration | LoadScheduleType
|  | Lights | LoadScheduleType
|  | People | LoadScheduleType
|  | Receptacle | LoadScheduleType
MasonryGrout
|  | PartialGrout | MasonryGrout | PartialGrout is one type of MasonryGrout which indicates that only some cells in a hollow masonry wall are grouted.
|  | PartialInsulatedGrout | MasonryGrout | PartialinsulatedGrout is one type of MasonryGrout which indicates that only some cells in a hollow masonry wall are grouted and cells not grouted are filled with insulation.
|  | SolidGrout | MasonryGrout | SolidGrout is one type of MasonryGrout which indicates that every cell in a hollow masonry wall is grouted.
MasonryType
|  | ClayBrick | MasonryType
|  | ClayHollowUnit | MasonryType | Used in masonry walls and its thickness and grout characteristics are evaluated in order to assign UFactor.
|  | Concrete | MasonryType
|  | ConcreteMasonryUnitLightWeight | MasonryType | A type of masonry unit used for mass walls with a density of 105 lb/ft^3.
|  | ConcreteMasonryUnitMediumWeight | MasonryType | A type of masonry unit used for mass walls with a density of 115 lb/ft^3.
|  | ConcreteMasonryUnitNormalWeight | MasonryType | A type of masonry unit used for mass walls with a density of 125 lb/ft^3.
PanesDivider
|  | Divider | PanesDivider
|  | NoDivider | PanesDivider
PanesPerLite
|  | DoublePane | PanesPerLite | One of the values for Panes Per Lite.
|  | SinglePane | PanesPerLite | One of the possible values for Panes Per Lite.
|  | TriplePane | PanesPerLite | One of the values for Panes Per Lite.
PartitionThermalType
|  | Adiabatic | PartitionThermalType | Adiabatic partitions are internal walls, floors or ceilings that separate two spaces and are treated as if there is no heat is transferred through the wall.
|  | Demising | PartitionThermalType | Demising partition is a wall, ceiling or floor that separates conditioned from unconditioned space.
|  | Exterior | PartitionThermalType | Defines partition such as a wall, floor or roof that separates conditioned space from the outdoors.
|  | Interzone | PartitionThermalType | Identifies a partition that separates two zones.
|  | Underground | PartitionThermalType | Identifies a Partition that is 50% or more below ground level.
PermitScope
|  | PermitNRAll | PermitScope | Permit scope for nonresidential envelope, lighting and mechanical
|  | PermitNREnv | PermitScope | Permit scope for nonresidential envelope only
|  | PermitNREnvLight | PermitScope | Permit scope for nonresidential envelope and lighting
|  | PermitNREnvMech | PermitScope | Permit scope for nonresidential envelope and mechanical
|  | PermitNRLight | PermitScope | Permit scope for nonresidential lighting only
|  | PermitNRLightMech | PermitScope | Permit scope for nonresidential lighting and mechanical
|  | PermitNRMech | PermitScope | Permit scope for nonresidential mechanical only
RoofConstructType
|  | MetalBuildingRoof | RoofConstructType
|  | WoodFramingAndOtherRoof | RoofConstructType
RoofFireProofing
|  | FireProofingSpray | RoofFireProofing | A method of providing fire protection for metal deck roofs.
|  | NoFireProofing | RoofFireProofing | Indicates that no fire proofing has been installed.
RoofingProductType
|  | Asphalt Shingles | RoofingProductType | Asphalt Shingles
|  | Clay | RoofingProductType | A type of masonry unit used for for hollow or solid walls.
|  | ClayRoofingTiles | RoofingProductType | Clay Roofing Tiles
|  | MetalRoofing | RoofingProductType
Roughness
|  | VeryRough | Roughness | [5 empty] | 1
|  | Rough | Roughness | [5 empty] | 2
|  | MediumRough | Roughness | [5 empty] | 3
|  | MediumSmooth | Roughness | [5 empty] | 4
|  | Smooth | Roughness | [5 empty] | 5
|  | VerySmooth | Roughness | [5 empty] | 6
ShadingType
|  | Overhang | ShadingType
|  | VerticalFin | ShadingType
SIPSSpacerType
|  | SpacerOSBSpline | SIPSSpacerType | A type of spacer used with structurally insulated wall panels (SIPS).
|  | SpacerSteelFraming | SIPSSpacerType | A type of spacer used with structurally insulated wall panels (SIPS).
|  | SpacerWood | SIPSSpacerType | SpacerWood is a type of spacer used with structurally insulated wall panels (SIPS).
SkylightCurbType
|  | Curb | SkylightCurbType
|  | NoCurb | SkylightCurbType
SpaceConditioningType
|  | IndirectlyConditioned | SpaceConditioningType | Describes an enclosed space, including, but not limited to, unconditioned volume in atria, that (1) is not directly conditioned space; and (2) either (a) has a thermal transmittance area product (UA) to directly conditioned space exceeding that to the outdoors or to unconditioned space ... or (b) is a space through which air from directly conditioned spaces is transferred at a rate exceeding three air changes per hour. Reference: 2008 NR ACM 2.3.1.2
|  | ProcessEnvironmentConditioning | SpaceConditioningType | (from Standards 101 definiions) PROCESS SPACE is a space that is thermostatically controlled to maintain a process environment temperature less than 55º F or to maintain a process environment temperature greater than 90º F for the whole space that the system serves, orthat is a space with a space -conditioning system designed and controlled to be incapable of operating at temperaturesabove 55º F or incapable of operating at temperatures below 90º F at design conditions. Reference Standards Table 100-A =>>sections 143(c) and 146
|  | RefrigeratedConditioning | SpaceConditioningType | REFRIGERATED SPACE is a building or a space that is a refrigerated warehouse, walk-in cooler, or a freezer. REFRIGERATED WAREHOUSE is a building or a space constructed for storage of products, where mechanicalrefrigeration is used to maintain the space temperature at 55o F or less.
|  | Unconditioned | SpaceConditioningType | Defines an enclosed space within a building that is not directly conditioned, or indirectly conditioned. Reference: NR ACM 2.3.1.3 Enclosed Unconditioned: Compliance software shall require the user to explicitly model any enclosed unconditioned spaces such as stairways, warehouses, unoccupied adjacent tenant spaces, attached sunspaces, attics and crawl spaces if and only if they are part of the permitted space.
Status
|  | ExistingAlteration | Status
|  | ExistingUnchanged | Status
|  | Modified | Status
|  | New | Status
|  | Removed | Status
WindowStyle
|  | GardenWindow | WindowStyle | The equivalent of greenhouse/garden window style used in Title 24 Part 6 Table 116A.
|  | GlazedDoor | WindowStyle | A door that has 50% or more glazing and is considered fenestration.
|  | WindowOther | WindowStyle | All windows that are not glazed doors or garden windows.
(no property)
CriticalProcess
|  | Hourly |  | Individual values (8760) reported for each hour of the design year.
IsolationArea
PerimeterSystem
Turnstiles
NonResBuildingOccupancyType |  |  | WholeBuildingOccupancy | The whole building occupancy type for a building defined as nonresidential which includes hotels, motels and high-rise residential. |  |  |  | NonResidential (includes Hotel, Motel and High-rise Residential)
| GroupAAssembly |  | CBCOccupancyGroup | Group A Assembly includes places of assembly with fixed seating like auditoriums and theatres, places with food and drink, places of worship and places of assembly for indoor sports
|  | Auditorium | WholeBuildingOccupancy | Part of a public building where an audience sits in fixed seating, or a room, area, with fixed seats used for public meetings or gatherings not specifically for the viewing of dramatic performances. | Assembly | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ConventionCenter | WholeBuildingOccupancy | A building that is used for meetings, conventions and multiple purposes, including, but not limited to, dramatic performances, and that has neither fixed seating nor fixed staging. | Assembly | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | DiningFastfood | WholeBuildingOccupancy | A building that is a food establishment as defined in Section 27520 of the Health andSafety Code | Restaurant | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | DiningRestaurant | WholeBuildingOccupancy | A building that is a food establishment as defined in Section 27520 of the Health andSafety Code. | Restaurant | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ExerciseFacility | WholeBuildingOccupancy | Exercise center/gymnasium: a room or building equipped for gymnastics, exercise equipment, or indoor athletic activities. |  | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Library | WholeBuildingOccupancy | A building that contains repository for literary materials, such as books, periodicals, newspapers, pamphlets and prints, and provides areas for reading and stacks as well as amenities for the library patrons. | Assembly | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Museum | WholeBuildingOccupancy | A space in which the primary function is the care or exhibit of works of artistic, historical, or scientific value. A museum does not include a gallery or other place where art is for sale. A museum does not include a lobby, conference room, or other occupancies where the primary function is not the care or exhibit of works of artistic, historical, or scientific value. | Assembly | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ReligiousFacility | WholeBuildingOccupancy | A building in which the primary function is for an assembly of people to worship, Religious facilities do not include classroom, housing, or gymnasium buildings. | Assembly | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | TheaterMotionPicture | WholeBuildingOccupancy | From Title 24 Part 6 Section 101 Definitions, an assembly room, a hall, or a building with tiers of rising seats or steps for the showing of motion pictures. | Assembly | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | TheaterPerformance | WholeBuildingOccupancy | An assembly room, a hall, with tiers of rising seats or steps for the viewing ofdramatic performances, lectures, musical events and similar live performances. | Assembly | GroupAAssembly | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
| GroupBBusiness |  | CBCOccupancyGroup | Group B Business includes service oriented businesses including offices, beauty shops, medical offices, public buildings, fire stations, banks
|  | BeautyBarberShop | WholeBuildingOccupancy | A building in which the primary activity is manicures, pedicures, facials, or the cutting or stylingof hair. Also known as beauty shop or beauty parlor. |  | GroupBBusiness | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | CivicFacility | WholeBuildingOccupancy | Civic meeting place: a city council or board of supervisors meeting chamber, courtroom, or other official meetingspace accessible to the public. | Assembly | GroupBBusiness | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | FinancialFacility | WholeBuildingOccupancy | Financial institution: a public establishment used for conducting financial transactions including the custody, loan, exchange, or issue of money, for the extension of credit, and for facilitating the transmission of funds. Financial transactions is the teller, work stations, and customers waiting areas to complete financial transactions. Financial transaction areas do not include private offices, hallways, restrooms, or other support areas. | Office | GroupBBusiness | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | FireStation | WholeBuildingOccupancy |  |  | GroupBBusiness | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | MedicalOutpatientFacility | WholeBuildingOccupancy | Medical buildings and clinics: a building where medical and clinical care is provided and does not provide overnight patient care. | Health | GroupBBusiness | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | OfficeBuilding | WholeBuildingOccupancy | Office: a room, area, or building of CBC Group B Occupancy | Office | GroupBBusiness | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | PoliceStation | WholeBuildingOccupancy |  |  | GroupBBusiness | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | TransportationFacility | WholeBuildingOccupancy | The ticketing area, waiting area, baggage handling areas, concourse, or other areas notcovered by primary functions in Table 146-C in an airport terminal, bus or rail terminal or station, subway or transitstation, or a marine terminal. |  | GroupBBusiness | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
| GroupEEducational |  | CBCOccupancyGroup | Group E Educational includes school facilities for K-12th grade.
|  | ClassroomBuilding | WholeBuildingOccupancy | A building or group of buildings that is predominately classrooms used by an organization that provides instruction to students. A classroom building does not include auditorium, gymnasium, kitchen, library, multi-purpose, dining and cafeteria, student union, maintenance staff workroom, or storage buildings. | School | GroupEEducational | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | EducationCollegeUniversity | WholeBuildingOccupancy | A building or group of buildings that is used by an organization that provides instruction to students, which is predominately classroom buildings but may also include auditorium, gymnasium, kitchen, library, multi-purposerooms, dining and cafeteria, student union, maintenance staff workroom, and small storage spaces. | School | GroupEEducational | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | EducationKto12 | WholeBuildingOccupancy | A building or group of buildings that is used by an organization that provides instruction to students, whichis predominately classroom buildings but may also include auditorium, gymnasium, kitchen, library, multi-purposerooms, dining and cafeteria, student union, maintenance staff workroom, and small storage spaces. | School | GroupEEducational | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
| GroupFFactory |  | CBCOccupancyGroup | Group F Factory/Industrial includes light to moderate hazard manufacturing as well as processing industries like dry cleaning and laundries, and bakeries and food processing
|  | LaundryFacility | WholeBuildingOccupancy | A building where laundering activities occur |  | GroupFFactory | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ManufacturingHighBay | WholeBuildingOccupancy | A room, area, or building in which an art, craft, assembly or manufacturing operation is performed and the luminaires 25 feet or more above the floor. | LightManufacturing | GroupFFactory | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ManufacturingLowBay | WholeBuildingOccupancy | A room, area, or building in which an art, craft, assembly or manufacturing operation is performed and the luminaires less than 25 feet above the floor. | LightManufacturing | GroupFFactory | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ManufacturingPrecision | WholeBuildingOccupancy | A room, area, or building in which an art, craft, assembly or manufacturing operation is performed involving visual tasks of small size or fine detail | LightManufacturing | GroupFFactory | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
| GroupMMercantile |  | CBCOccupancyGroup | Group M Mercantile covers all types of buinesses that provide display and sale of merchandise
|  | Grocery | WholeBuildingOccupancy | A building that has as its primary purpose the sale of foodstuffs requiring additional preparation priorto consumption | Retail | GroupMMercantile | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | RetailBuilding | WholeBuildingOccupancy | A building in which the primary activity is the sale of merchandise. | Retail | GroupMMercantile | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ShoppingMall | WholeBuildingOccupancy |  | Retail | GroupMMercantile | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
| GroupR1Residential |  | CBCOccupancyGroup | Group R Residential: R-1 includes hotels and motels which are considered nonresidential in the Standards
|  | HotelMotel | WholeBuildingOccupancy | A building or buildings incorporating six or more guest rooms and all conditioned spaces within the same building envelope |  | GroupR1Residential | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
| GroupR2Residential |  | CBCOccupancyGroup | Group R Residential: R-2 covers multi-family housing of three or more units and therefore may be considered residential or nonresidential depending on the number of building stories.
|  | Dormitory | WholeBuildingOccupancy | A building where group sleeping accommodations are provided in one room, or in a series of closely associated rooms, for persons not members of the same family group, under joint occupancy and single management, as in college dormitories or fraternity houses. |  | GroupR2Residential | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | HighRiseResidential | WholeBuildingOccupancy | A building, other than a hotel/motel, of Occupancy Group R, Division 1 with four or more habitable stories. |  | GroupR2Residential | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | MultiFamilyHousing | WholeBuildingOccupancy | Multi-family: A multi-family building contains multiple dwelling units that share common walls and may also share common floors or ceilings (apartments). |  | GroupR2Residential | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | SeniorHousing | WholeBuildingOccupancy | Senior housing: Is specifically for habitation by seniors, including but not limited to independent living quarters, and assisted living quarters. |  | GroupR2Residential | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
| GroupSStorage |  | CBCOccupancyGroup | Group S Storage covers low and moderate hazardous storage and includes auto repair businesses and parking facilities
|  | AutoRepair | WholeBuildingOccupancy | The portion of a building used to repair automotive equipment and/or vehicles, exchange parts, and may include work using an open flame or welding equipment. |  | GroupSStorage | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ParkingFacility | WholeBuildingOccupancy | A covered building or structure for the purpose of parking vehicles | Parking | GroupSStorage | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | RefrigeratedWarehouse | WholeBuildingOccupancy |  | Warehouse | GroupSStorage | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | StorageFacility | WholeBuildingOccupancy | Commercial and industrial storage is a room, area, or building used for storing items. | Warehouse | GroupSStorage | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | UtilityFacility | WholeBuildingOccupancy | Electrical/mechanical/telephone room: a room in which the building's electrical switchbox or control panels, telephone switchbox, and/or HVAC controls or equipment is located. |  | GroupSStorage | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
| AllOthersBldg |  | WholeBuildingOccupancy | In most tables that evaluate occupancy in order to assign a rule target value, there is a catch all category of All Others |  |  | NonResBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
(SpaceOccupancyType)
|  | AllOthersSpace | SpaceOccupancy | In most tables that evaluate occupancy in order to assign a rule target value, there is a catch all category of All Others |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Atrium | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | AuditoriumSpace | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | AutoRepairSpace | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | BarCocktailLounge | SpaceOccupancy |  | Restaurant |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | BeautyBarberShopSpace | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ButcherShop | SpaceOccupancy |  | Restaurant |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Cafeteria | SpaceOccupancy |  | Restaurant |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Classroom | SpaceOccupancy |  | School |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ConferenceExhibit | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ConferenceMeeting | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ConfinementCell | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Corridor | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Courtroom | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | DiningArea | SpaceOccupancy |  | Restaurant |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | DressingRoom | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | DryCleanFullService | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | DryCleanSelfService | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | DwellingUnits | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Entrance Lobby | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | FinancialTransactions | SpaceOccupancy |  | Office |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | FoodPreparation | SpaceOccupancy |  | Restaurant |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | GrocerySales | SpaceOccupancy | A room or area, in a building that has as its primary purpose the sale of foodstuffs requiring additional preparation prior to consumption. | Retail |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Gymnasium | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | HotelMotelFunctionArea | SpaceOccupancy | A hotel room or area such as a hotel ballroom, meeting room, exhibit hall or conference room,together with pre-function areas and other spaces ancillary to its function. | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | HotelMotelGuestRoom | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | HousingCommonArea | SpaceOccupancy | May include dining, reading, study, library or other community spaces and/or medical treatment or hospicefacilities. | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | JudgeChambers | SpaceOccupancy |  | Office |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | LaundrySpace | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | LectureHall | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | LibraryReading | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | LibrarySpace | SpaceOccupancy | A room or area in a building hat contains repository for literary materials, such as books, periodicals, newspapers, pamphlets and prints, and provides areas for reading | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | LibraryStacks | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Lounge | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ManufacturingHighBaySpace | SpaceOccupancy |  | LightManufacturing |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ManufacturingLowBaySpace | SpaceOccupancy |  | LightManufacturing |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ManufacturingPrecisionSpace | SpaceOccupancy |  | LightManufacturing |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | MechElectTeleControlRoom | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | MedicalOutpatientSpace | SpaceOccupancy | A room or area in a building that does not provide overnight patient care and that is used to provide physical and mental care through medical, dental, or psychological examination and treatment, including, but not limited to, laboratories and treatment spaces. | Health |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | MuseumExhibit | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | MuseumRestoration | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | OfficeeEnclosed | SpaceOccupancy |  | Office |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | OfficeOpenPlan | SpaceOccupancy |  | Office |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ParkingArea | SpaceOccupancy |  | Parking |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ParkingRampEntrance | SpaceOccupancy |  | Parking |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Restroom | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | RetailSales | SpaceOccupancy | A room or area in which the primary activity is the sale of merchandise. This includes wholesale showroom is a room where samples of merchandise are displayed | Retail |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | ScienceLab | SpaceOccupancy |  | Lab |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Stairs | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | StorageActiveLargeItems | SpaceOccupancy |  | Warehouse |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | StorageActiveSmallItems | SpaceOccupancy |  | Warehouse |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | StorageCommercialIndustrial | SpaceOccupancy |  | Warehouse |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | StorageCooler | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | StorageFreezer | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | StorageInactive | SpaceOccupancy |  | Warehouse |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | TheaterMotionPictureSpace | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | TheaterPerformanceSpace | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Utility Area (Mechanical Electrical Telephone) | SpaceOccupancy |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | VocationalTraining | SpaceOccupancy |  | School |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | Waiting Area | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | WholesaleShowroom | SpaceOccupancy |  | Retail |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | WorshipArea | SpaceOccupancy |  | Assembly |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)

## HvacObjects
Term | Term Short Form | SDD Building Parent | SDD Parent | Service | Properties | Referenced Objects | ObjectType | Array Count | ArrayObject | ArrayProperty | Definition | Standards Reference | Constraints | Set By | Critical Path Issue | Issues | Resolved Issues | Collapsed From
AirSegment |  |  | AirSystem | AirSystem | AirSegmentDuctConductionLoss |  | Heterogeneous |  |  |  | A duct that carries supply, return, makeup, relief or exhaust air in an AirSystem. |  |  |  | NO
AirSegmentDuctLeakage
AirSegmentDuctLeakageFactor
AirSegmentDuctSurfaceArea
AirSegmentDuctSurfaceAreaCoefficient
AirSegmentDuctThermalResistance
AirSegmentPath
AirSegmentSource
AirSegmentType
AirSegmentMakeupAirSystem
AirSegmentMakeupThermalZone
Name
AirSystem |  | Building |  |  | AirSystemCoolControl |  | Heterogeneous |  |  |  | Provides conditioned air or ventilation to one or more thermal zones in a building. |  |  |  | NO
AirSystemCoolingCapacity
AirSystemCoolResetSchedule
AirSystemHeatControl
AirSystemHeatingCapacity
AirSystemHeatResetSchedule
AirSystemVentilationControl
AirSystemOptimumStart
AirSystemType
AirSystemUnmetCoolLoadHours
AirSystemUnmetHeatLoadHours
Name
Boiler |  | Project |  |  | BoilerAFUE |  | Heterogeneous |  |  |  | A device for generating steam or hot water, which consists of a source of heat and a chamber that holds water which absorbs the heat. The steam or hot water is then recirculated out of the boiler for use in FluidSystem | 2013 NR ACM: 5.8.1 Boilers; |  |  | NO | JG: 1. Add inputs for equipment staging. DP: Is this different than the BoilerUnloadRatioMinimum? DR: Equipment staging controls are currently defined under 'FluidSystemEquipmentControl', which will reference a yet to be defined object that will have equipment stating properties.
BoilerCapRated
BoilerCombustionEff
BoilerCount
BoilerDesignEnteringTemp
BoilerDesignLeavingTemp
BoilerDraftType
BoilerHIRfPLRCurveCoefficent
BoilerEnergyInputRatio
BoilerFluidFlowIn
BoilerFluidFlowOut
BoilerFuel
BoilerFuelFullLoad
BoilerFuelPartLoad
BoilerHeatLoss
BoilerHIRfPLRCurveFactor
BoilerThermalEff
BoilerType
BoilerUnloadRatioMinimum
Name
Status
BoilerHIRfPLRCurveCoefficents |  |  | Boiler |  |  |  | Property Array | 3 |  | BoilerHIRfPLRCurveCoefficent | An array of three values used tto calculate HeatingPLEffCurveFactor for Boilers and Furnaces | 2013 NR ACM 5.7.6.4 Furnace, Table 59, equation 43 5.8.1 Boilers equation 60 |  |  | NO
Chiller |  | Project |  |  | ChillerCapAvailable |  | Heterogeneous |  |  |  | Cooling equipment that produces chilled water for cooling systems. A chiller plant consists one or more chillers, evaporator and condenser pumps, and cooling towers. | 2013 NR ACM: 5.8.2 Chillers |  |  | NO | JG: 1. Need kW/ton DP: Ton as in 12,000 Btu/hr? DR: What?? JG: 2. Need EfficiencyType DP: We have ChillerCOP which is what 2013 NR ACM defines as chiller efficiency. JG: 3. Need air cooled condenser power from 5.8.2 DP: Will this require a condenser object, or can we define it as a property of a Chiller? JG: 4. DBEntering does not make sense for chiler unless this is for the condenser? DP: Resolved - it isn't a property of Chiller now. JG: 5. Add inputs for equipment staging. DP: Is this different from ChillerUnloadRationMinimum? DR: Equipment staging controls are currently defined under 'FluidSystemEquipmentControl', which will reference a yet to be defined object that will have equipment stating properties. KB: 6. New issue RESOLUTION (KB): solved
ChillerCapfTempFactor
ChillerCapRated
ChillerCondenserIn
ChillerCondenserOut
ChillerCoolingEfficiencyMin
ChillerCoolingHourlyLoad
ChillerCOP
ChillerCount
ChillerDBOutdoorTemp
ChillerDesignEnteringTemp
ChillerDesignLeavingTemp
ChillerEIRfPLRCurveCoefficient
ChillerEIRfTempCurveCoefficient
ChillerEIRfTempFactor
ChillerEnergyInputRatio
ChillerEngineSpeedMin
ChillerEvaporatorIn
ChillerEvaporatorOut
ChillerFIRfPLRCurveCoefficient
ChillerFIRfTempCurveCoefficient
ChillerFuel
ChillerFuelOperating
ChillerFuelRated
ChillerLeavingTemp
ChillerPowerRated
ChillerType
ChillerUnloadRatioMinimum
Name
Status
ChillerCapfTempCurveCoefficients |  |  | Chiller |  |  |  | Property Array | 6 |  | ChillerCapfTempCurveCoefficient | An array of 6 values, a-f used in calculating the available chiller cooling capacity. The value is dependent on the chiller fuel, Coolant (air or water), compressor type for ChillerDx and stages and fuel for ChillerAbsorp | 2013 NR ACM Tables 67-69 Default Capacity Coefficients; 2008 NR ACM: 2.5.3.16 Performance Curves for Gas Absorption and Electric Chillers Table N2-22 - N2-27 |  |  | NO
ChillerEIRfPLRCurveCoefficients |  |  | Chiller |  |  |  | Property Array | 4 |  | ChillerEIRfPLRCurveCoefficient | An array of 4 values are used in calculating EIRFactorPLR | 2013 NR ACM 5.8.2 Chillers Electric Chiller Cooling Efficiency Adjustment Curves Tables 72 and 73 and 64 equations |  |  | NO
ChillerEIRfTempCurveCoefficients |  |  | Chiller |  |  |  | Property Array | 6 |  | ChillerEIRfTempCurveCoefficient | An array 6 values a-f used in calculating EIRFactorTemp | 2013 NR ACM 5.8.2 Chillers Electric Chiller Cooling Efficiency Adjustment Curves Tables 70 and 71 and 64 equations |  |  | NO
ChillerFIRfPLRCurveCoefficients |  |  | Chiller |  |  |  | Property Array | 4 |  | ChillerFIRfPLRCurveCoefficient | An array of 4 values used in calculating FIRFactorPLR for chillers that are fueled by steam or gas rather then electricity. This includes all absorption chillers. | 2013 NR ACM 5.8.2 Chillers Fuel and Steam Chiller Cooling Efficiency Adjustment Curves Tables 74 and 75 Note table 74 categories are not orthogonal |  |  | NO
ChillerFIRfTempCoefficients |  |  | Chiller |  |  |  | Property Array | 6 |  | ChillerFIRfTempCurveCoefficient | An array of 6 values used in calculating FIRFactorTemp for chillers that are fueled by steam or gas rather then electricity. This includes all absorption chillers. | 2013 NR ACM 5.8.2 Chillers Fuel and Steam Chiller Cooling Efficiency Adjustment Curves Tables 76 and 77 Note table 76 categories are not orthogonal |  |  | NO
CoilCooling |  |  | AirSegment | AirSegment | CoilCondenserFlowType |  | Heterogeneous |  |  |  | An arrangement of pipe or tubing used in heating, cooling and refrigeration systems. Coils carry a heated or cooled medium and air or water surrounds the coil to absorb heat from the medium or reject heat into the medium. |  |  |  | NO
|  |  |  | TerminalUnit | CoilCondenserType
CoilCoolingBF_fAirFlowCurveCoefficient
CoilCoolingBF_fPLRCurveCoefficient
CoilCoolingBF_fTempCurveCoefficient
CoilCoolingBFDesign
CoilCoolingBFRated
CoilCoolingCapTotalAdjusted
CoilCoolingCap_fTempCurveCoefficient
CoilCoolingCapSensibleAdjusted
CoilCoolingCapSensibleRated
CoilCoolingCapTotalRated
CoilCoolingDesignCoolingTemp
CoilCoolingDxEER
CoilCoolingDxEIRFactorAirflowVerified
CoilCoolingDxEIR_fPLRCurveCoefficient
CoilCoolingDxEIR_fTempCurveCoefficient
CoilCoolingDxEnergyInputRatio
CoilCoolingDxFDDFactor
CoilCoolingDxRefrigerantChargeFactor
CoilCoolingDxSEER
CoilCoolingDxUnloadRatioMinimum
CoilCoolingFuelSource
CoilCoolingSizingRatio
CoilCoolingType
CoilCoolingWaterEconoCWSTempMax
CoilCoolingWaterEconoCWSTempSetpoint
CoilCoolingWaterEconoDBTempMax
CoilCoolingWaterEconoHXEff
CoilCoolingWaterEconoType
CoilHeatingCrankcaseControlTemp
CoilFluidFlowIn
CoilFluidFlowOut
Name
Status
CoilCoolingCapfTempCurveCoefficients |  |  | CoilCooling |  |  |  | Property Array | 6 |  | CoilCoolingCap_fTempCurveCoefficient |  |  |  | User | NO
CoilCoolingDxEIRfPLRCurveCoefficients |  |  | CoilCooling |  |  |  | Property Array | 6 |  | CoilCoolingDxEIR_fPLRCurveCoefficient |  |  |  | User | NO
CoilCoolingDxEIRfTempCurveCoefficients |  |  | CoilCooling |  |  |  | Property Array | 4 |  | CoilCoolingDxEIR_fTempCurveCoefficient |  |  |  | User | NO
CoilHeating |  |  | AirSegment |  | CoilCondenserFlowType |  | Heterogeneous | [6 empty] | User | NO
CoilCondenserType
CoilFluidFlowIn
CoilFluidFlowOut
CoilHeatingDesignHeatingTemp
CoilHeatingFuelSource
CoilHeatingFurnaceFuelFullLoad
CoilHeatingFurnaceHIR_fPLRCurveCoefficent
CoilHeatingFurnaceIgnitionType
CoilHeatingFurnacePilotFuelInput
CoilHeatingFurnaceThermalEff
CoilHeatingHpCap_fTempCurveCoefficient
CoilHeatingHpCOP
CoilHeatingHpCOPAdjusted
CoilHeatingHpDefrostControl
CoilHeatingHpDefrostHeatSource
CoilHeatingHpEIR_fPLRFactor
CoilHeatingHpEIR_fTempFactor
CoilHeatingHpEIR_fTempCurveCoefficient
CoilHeatingHpEnergyInputRatio
CoilHeatingHpHSPF
CoilHeatingHpSupplementalOATemp
CoilHeatingSizingRatio
CoilHeatingType
CoilHeatingFurnaceHIRfPLRCurveCoefficients |  |  | CoilHeating |  |  |  | Property Array | 3 |  | CoilHeatingFurnaceHIR_fPLRCurveCoefficent | An array of four values used to calculate EIR- FPLR and EIR-FT for heat pumpts | 2013 NR ACM 5.7.6.5 Electric Heat Pump Table 61 |  |  | NO
CoilHeatingHpCapfTempCurveCoefficients |  |  | CoilHeating |  |  |  | Property Array | 4 |  | CoilHeatingHpCap_fTempCurveCoefficient | An array of four values used in calculating the available heating capacity of heat pumps | 2013 NR ACM 5.7.6.5 Electric Heat Pump Table 60 |  |  | NO
CoilHeatingHpEIRfPLRCurveCoefficients |  |  | CoilHeating |  |  |  | Property Array | 4 |  | CoilHeatingHpEIR_fPLRCurveCoefficient |  |  |  | User | NO
CoilHeatingHpEIRfTempCurveCoefficients |  |  | CoilHeating |  |  |  | Property Array | 4 |  | CoilHeatingHpEIR_fTempCurveCoefficient | An array of four values used to calculate EIR- FPLR and EIR-FT for heat pumpts | 2013 NR ACM 5.7.6.5 Electric Heat Pump Table 61 |  |  | NO
EnergyRecovery |  | Project |  |  | EnergyRecoveryExhaustFlow |  | Heterogeneous | [7 empty] | NO
EnergyRecoveryFluidFlowIn
EnergyRecoveryFluidFlowOut
EnergyRecoverySupplyFlow
EnergyRecoveryType
Name
EvapCooler |  | Project |  |  | EvapCoolerAirFlowPrimaryDesign |  | Heterogeneous |  |  |  | Equipment that pre-cools the outside air that is brought into the building. It may be used with any type of cooling system that brings in outside air. | 2013 NR ACM 5.7.5.3 Evaporative Cooler |  |  | NO
EvapCoolerAirFlowPrimaryOperating
EvapCoolerEffectiveness
EvapCoolerEnteringDBTemp
EvapCoolerEnteringWBTemp
EvapCoolerLeavingDBTemp
EvapCoolerPerformanceCoefficient
EvapCoolerType
Fan |  |  | AirSegment | AirSegment | FanAxialType |  | Heterogeneous | [7 empty] | NO
|  |  |  | TerminalUnit | FanCentrifugalType
FanControlMethod
FanDriveEfficiency
FanOverallEfficiency
FanFlowCapacity
FanFlowMinimum
FanFlowPLRFactor
FanModelingMethod
FanMotorBHP
FanMotorEfficiency
FanMotorHP
FanMotorPoleCount
FanMotorPosition
FanMotorRotationalSpeed
FanMotorType
FanPartLoadPowerCurve
FanPower
FanPowerIndex
FanPowerMinimum
FanPowerPerFlow
FanPower_fPLRCurveCoefficient
FanTotalStaticPressure
HeatRejectionFanType
Name
FluidSegment |  |  | FluidSystem | FluidSystem | FluidSegmentConductionLoss |  | Heterogeneous |  |  |  | A pipe that carries supply, return, makeup, or discharge fluid in an FluidSystem. |  |  |  | NO
FluidSegmentPipeDiameter
FluidSegmentPipeInsulationThk
FluidSegmentPrimarySegment
FluidSegmentSource
FluidSegmentType
Name
FluidSystem |  | Building |  |  | FluidSystemCoolControl |  | Heterogeneous |  |  |  | Provides conditioned fluid for a heating or cooling system, or service water heating system. |  |  |  | NO
FluidSystemCoolResetSchedule
FluidSystemDescription
FluidSystemEquipmentControl
FluidSystemHeatControl
FluidSystemHeatlResetSchedule
FluidSystemType
FluidSystemUnmetCoolLoadHours
FluidSystemUnmetHeatLoadHours
Name
HeatExchanger |  | Project |  |  | HeatExchangerFluidDemandIn |  | Heterogeneous | [7 empty] | NO | JG: 1. Is this for support of water side economizer? If so need to add terms and details and definitions. DR: Yes, will add terms in future.
HeatExchangerFluidDemandOut
HeatExchangerFluidSupplyn
HeatExchangerFluidSupplyOut
HeatExchangerType
Name
HeatRejection |  | Project |  |  | HeatRejectionCapfTempCurveCoefficient |  | Heterogeneous | [7 empty] | NO | JG: 1. Add ElectricInputRatio to be consistent with ACM 5.8.3 or gpm/hp to be consistent with other efficiency metrics for towers. JG: 2. Add capacity adjustment curve, JG: 3 Add cooling tower set point control options, JG: 4. Add terms needed for exception to cooling tower capacity control. JG: 5. Add low-speed airflow ratio and low speed kW ratio. JG: 6. Add power adjustment curve coefficients. Add cooling tower minimum speed.
HeatRejectionCapRated
HeatRejectionCellCount
HeatRejectionDesignEnteringTemp
HeatRejectionDesignLeavingTemp
HeatRejectionDesignWBTemp
HeatRejectionFanType
HeatRejectionFluidFlowIn
HeatRejectionFluidFlowOut
HeatRejectionModulationControl
HeatRejectionTotalFanHP
HeatRejectionType
Name
HeatRejectionCapfTempCoefficients |  |  | HeatRejection |  |  |  | Property Array | 6 |  | HeatRejectionCapfTempCurveCoefficient | An array of 6 values a-f used in calculating the available cooling capacity of the cooling tower heat rejection | 2013 NR ACM Table 78 Default Capacity Coefficients - Cooling Towers |  |  | NO
HVACSystems |  | Project |  |  | HVACSystemsCoolingOversizingRatio |  | Heterogeneous | [6 empty] | User | NO | DR: 1. This is a proposed object that may be parent to all HVAC components in Project. Right now, it holds high level sizing terms.
HVACSystemsHeatingOversizingRatio
HVACSystemsUnmetCoolLoadHours
HVACSystemsUnmetHeatLoadHours
HVACSystemsUnmetLoadHoursDeltaLimit
HVACSystemsUnmetLoadHoursLimit
OAControl |  | Project |  |  | Name |  | Heterogeneous | [7 empty] | NO
OAControlEconoControlMethod
OAControlEconoHighEnthalpyLockout
OAControlEconoHighTempLockout
OAControlOutsideAirRatio
OAControlReturnFlow
OAControlSupplyFlow
OAControlType
PerfomanceCurve | [6 empty] | Heterogeneous | 1 | [5 empty] | User | NO | DR: 1. We need to define this object and link it to the appropratie HVAC equipment. David will lead work to complete this object definition, including making sure that this fits with what is being defined in the 2013 NR ACM for performance curves
PreheatCoil |  | Project |  | OAControl | Name |  | Heterogeneous | [7 empty] | NO
PreheatCoilType
ProcessLoad |  | Project |  | FluidSegment | ProcessLoadEnergyLoad |  | Heterogeneous | [7 empty] | NO
ProcessLoadFlow
Name
ProcessLoadType
Pump |  |  | FluidSegment | Boiler | Name |  | Heterogeneous | [7 empty] | NO | JG: 1. Not sure if pump service from ACM is needed or not. JG: 2. Does not support power per unit flow input from ACM JG: 3. Add impeller efficiency, motore efficiency, design pump head JG: 4. Add whether flow is variable speed or not. JG: 5. Add pump operation
|  |  |  | Chiller | PumpCount
|  |  |  | HeatRejection | PumpFlowCapacity
PumpFlowMin
PumpMinimumSpeed
PumpMinimumSpeedRatio
PumpModelingMethod
PumpMotorBHP
PumpMotorEfficiency
PumpMotorHP
PumpOperationControl
PumpPower
PumpPowerPerFlow
PumpPowerfPLRCurveCoefficient
PumpSpeedControl
PumpType
StorageTank |  | Project |  |  | Name |  | Heterogeneous | [7 empty] | NO | JG: 1. need to add attributes related to how to operate thermal storage system. DR: Yes. Currently, this object was intended to represent an unfired SHW tank. For thermal storage, we will may decide to add another object…
StorageTankCapacity
StorageTankFluidFlowIn
StorageTankFluidFlowOut
StorageTankRValue
TerminalUnit |  | Project |  |  | TerminalUnitPrimaryAirFlow |  | Heterogeneous | [7 empty] | NO | DR: 1. Need to discuss pros/cons of TerminalUnit fan and coil properties are components or properties of TerminalUnit
TerminalUnitHotDuctAirSegment
Name
TerminalUnitPrimaryAirSegment
TerminalUnitInducedAirZone
TerminalUnitInductionRatio
TerminalUnitType
TerminalUnitZoneServed
ThermalZone |  | Building |  |  | Name |  | Heterogeneous | 1 |  |  | A collection of spaces within a building having sufficiently similar space conditioning requirements so that those conditions could be maintained with a single thermal controlling device. | Zone is a space or group of spaces that have the same space conditioning requirements and are controlled by a single thermostat. 2013 NR ACM Uses Thermal Block for this object but same definition. |  | User | NO | RHi: 1. Can a ThermalZone include spaces that are not contiguous? Rob will lead work to resolve this issue and work with Jason, John and Dan (NREL)
ThermalZoneCoolingSystem
ThermalZoneCoolingTStatSchedule
ThermalZoneDescription
ThermalZoneExhaustSystem
ThermalZoneHeatingSystem
ThermalZoneHeatingTStatSchedule
ThermalZoneSupplementalCoolingSystem
ThermalZoneSupplementalHeatingSystem
ThermalZoneThrottlingRange
ThermalZoneType
ThermalZoneVentControlMethod
ThermalZoneVentilationSystem
ThermalZoneVentRateDesign
ThermalZoneVentRateMin
ThrottlingRangeLowerTemp
ThrottlingRangeUpperTemp
WaterHeater |  | Project |  |  | Name |  | Heterogeneous | [7 empty] | NO
Status
WaterHeaterEnergyFactor
WaterHeaterFluidFlowIn
WaterHeaterFluidFlowOut
WaterHeaterMakeUp
WaterHeaterStandByLoss
WaterHeaterStorageCapacity
WaterHeaterThermalEff
WaterHeaterType
WaterHeaterHIRfPLRCurveCoefficents |  |  | WaterHeater |  |  |  | Property Array | 3 |  | WaterHeaterFIRfPLRCurveCoefficent | An array of three values used in calculating the part load curve for the water heater | 2013 NR ACM 5.9.1.2 Water Heaters Fuel Water Heater Part Load Efficiency Curve equation 76 |  |  | NO

## HvacProperties
Term | Term Short form | DataType | Units | HvacEnumerations | Referenced Objects | Definition | Standards Reference | Constraints | Set By | Issues | Resolved Issues | Critical Path Issue
AirSegmentDuctConductionLoss | DuctConductionLoss | decimal | Btu per h F |  |  | The heat loss rate of ducts which varies depending on duct length and surrounding environment. | ??? |  |  | 1. DR: Not sure if this is still used in NACM. Need NACM Appendix D. |  | NO
AirSegmentDuctLeakage | DuctLeakage | decimal | none |  |  | A percentage of acceptable leakage in air distribution systems. The default is a maximum of 6% of fan flow in the air distribution system, but it is affected by the type of installation (new, existing) and by a duct leakage factor which varies depending on if the was a leakage test performed or not. | 2008 Title 24: section 144 (k) Air Distribution System Duct Leakage Sealing. 2008 Appendix NA2 Table NA2-1 Duct Leakage Factors, Table NA2-2 Duct Leakage Tests. |  |  | 1. DR: Not sure if this is still used in NACM. Need NACM Appendix D. |  | NO
AirSegmentDuctLeakageFactor | DuctLeakageFactor | decimal | none |  |  | Aconstant used to calculate distribution efficiency | CoolingSystems: 5.7.5 Cooling Systems - Distribution System Efficiency includes duct leakage factor, |  |  | 1. DR: Not sure if this is still used in NACM. Need NACM Appendix D. |  | NO
AirSegmentDuctSurfaceArea | DuctSurfaceArea | decimal | ft2 |  |  | Required in order to calculate the efficiency of the distribution system. It is also used in applying duct leakage requirements. | 2013 NR ACM 5.7.5 Cooling Systems - Distribution System Efficiency requires SurfaceArea for calculating efficiency |  |  | 1. DR: Not sure if this is still used in NACM. Need NACM Appendix D. |  | NO
AirSegmentDuctSurfaceAreaCoefficient | DuctSurfaceAreaCoeff | decimal | none |  |  | Used in the default equations for calculating duct SurfaceArea. SurfaceAreaCoefficient are unique depending on if the DistributionSystem.Function is supply or return. | 2008 Appendix NA2.3.3.1 Default Duct Surface Area |  |  | 1. DR: Not sure if this is still used in NACM. Need NACM Appendix D. |  | NO
AirSegmentDuctThermalResistance | DuctThermalRes | decimal | h ft2 F per Btu |  |  | The R-value of ducts used in calculating distribution efficiency. The requirement is different for new and existing ducts in a project. | 2013 NR ACM 5.7.5 Cooling Systems - Distribution System Efficiency includes R-values for the supply duct and the return duct. 2008 NA2.3.5 Duct Wall Thermal Resistance |  |  | 1. DR: Not sure if this is still used in NACM. Need NACM Appendix D. |  | NO
AirSegmentMakeupAirSystem | MakeUpAirSystem | reference | none |  | AirSystem | The Name of AirSystem from which makeup air is supplied | [5 empty] | NO
AirSegmentMakeupThermalZone | MakeUpThermalZone | reference | none |  | ThermalZone | The Name of ThermalZone from which makeup air is drawn |  |  |  | 1. DSP: If we have MakeupAirSystem defined and that AirSystem is referenced by a ThermalZone, do we need this too? |  | NO
AirSegmentPath | Path | enumerated list | none | Direct |  |  |  |  | User |  |  | NO
Ducted
PlenumZones
AirSegmentSource | Source | enumerated list | none | AirSystem |  | Defined for Makeup AirFlowSegments |  | AirFlowSegmentType = MakeUp only | User |  |  | NO
None
OutdoorAir
ZoneAir
AirSegmentType | Type | enumerated list | none | ExhaustSegment |  | dsp |  |  | User;#Rule |  |  | NO
MakeupAir
DualDuctSplitter
Relief
Return
Supply
AirSystemCoolControl | CoolControl | enumerated list | none | ColdestReset |  | Defines the cooling supply air temperature control method used for systems with cooling coils | 2013 NR ACM: 5.7.2.2 Cooling Control |  | User;#Rule |  |  | NO
FixedAirCool
OAResetAirCool
ScheduledAirCool
AirSystemCoolingCapacity | CoolingCapacity | decimal | Btu per h |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems also has Total Cooling Capacity units: cooling tons (12,000 BTU/h per ton) defined as the total cooling capacity (both sensible and latent) of a cooling coil or packaged DX system. |  | User | 1. DR: Need to discuss if this is a necessary term, or if it should be at AirSystem, Building or Project level. |  | NO
AirSystemCoolResetSchedule | CoolResetSch | reference | none |  |  | The name of the reset schedule object that defines outdoor and supply air temperature control points during cooling. |  |  | User |  |  | NO
AirSystemHeatControl | HeatControl | enumerated list | none | FixedAirHeat |  | Defines the control method for heating supply air temperature for systems with heating coils. | 2013 NR ACM: 5.7.2.3 Heating Control |  | User;#Rule |  |  | NO
OAResetAirHeat
ScheduledAirHeat
WarmestReset
AirSystemHeatingCapacity | HeatingCapacity | decimal | Btu per h | [5 empty] | User | 1. DR: Need to discuss if this is a necessary term, or if it should be at AirSystem, Building or Project level. |  | NO
AirSystemHeatResetSchedule | HeatResetSch | reference | none |  |  | This is the name of the reset schedule object that defines outdoor and supply air temperature control points during heating. |  |  | User |  |  | NO
AirSystemOptimumStart | OptimumStart | boolean | none |  |  |  | 2013 NR ACM: 5.7.2.1 Schedules |  | User;#Rule |  |  | NO
AirSystemPeakCoincidentCoolingLoad | PeakCoincidentCoolLoad | decimal | Btu per h |  |  | The cooling required to maintain thermal comfort and is dependent on occupancy type and schedules | 2013 NR ACM: 2.5 HVAC Capacity Requirements and Sizing, 3.1.10 Loads Calculation |  | User |  |  | NO
AirSystemPeakCoincidentHeatingLoad | PeakCoincidentHeatLoad | decimal | none |  |  | The heatng required to maintain thermal comfort and is dependent on occupancy type and schedules | 2013 NR ACM: 2.5 HVAC Capacity Requirements and Sizing, 3.1.10 Loads Calculation |  | User |  |  | NO
AirSystemType | Type | enumerated list | none | BuiltUp |  |  | 2013 NR ACM: 5.7.1 Basic System Information |  | User;#Rule | 1. DR: NACM 'System Type' has a number of system definitions. Need to discuss in SDD group how we want to describe systems. |  | NO
Unitary
AirSystemUnmetCoolLoadHours | UnmetCoolLoadHours | decimal | h |  |  | The number of hours during the year when the space temperature is below the heating set point temperature or greater than the cooling set point temperature. UnmetLoadHours are used to determine if resizing is required. If greater than 300 there are rules for adjusting the baseline model to decrease the UnmetLoadHours | 2013 NR ACM 2.5 HVAC Capacity Requirements and Sizing; |  | User |  |  | NO
AirSystemUnmetHeatLoadHours | UnmetHeatLoadHours | decimal | h |  |  | The number of hours during the year when the space temperature is below the heating set point temperature or greater than the cooling set point temperature. UnmetLoadHours are used to determine if resizing is required. If greater than 300 there are rules for adjusting the baseline model to decrease the UnmetLoadHours | 2013 NR ACM 2.5 HVAC Capacity Requirements and Sizing; |  | User |  |  | NO
AirSystemVentilationControl | VentControl | enumerated list | none | AverageFlow |  |  | 2013 NR ACM: 5.7.4.1 Outside Air Controls |  | User |  |  | NO
CriticalZone
FixedAirVent
BoilerAFUE | AFUE | decimal | none |  |  | The full load efficiency of a boiler or furnace at AFUE rated conditions | 2013 NR ACM: 5.7.6.4 Furnace equation 41 5.8.1 Boilers equation 59 | Appliance Stds, for boilers <300kBtu/hr only | User;#Rule |  |  | NO
BoilerCapRated | CapRated | decimal | Btu per h |  |  | The rated measure of energy ouput of Boilers. | 2013 NR ACM: 5.8.1 Boilers Boiler Design Capacity; |  | User |  |  | NO
BoilerCombustionEff | CombustionEff | decimal | none |  |  | The measure of how much energy is extracted from the fuel and is the ratio of heat transferred to the combustion air divided by the heat input of the fuel. | 2013 NR ACM: 5.8.1 Boilers Boiler Efficiency Type | Appliance Stds, for boilers >=300kBtu/hr only | User;#Rule |  |  | NO
BoilerCount | Count | integer | none |  |  | The number of Boilers that are identical. Because all the features are the same in each unit, the Count can be used as a multiplier for calculating values like capacity of all the units | 2013 NR ACM: 5.8.1 Boilers Number of Identical Boiler Units; |  | User;#Rule |  |  | NO
BoilerDesignEnteringTemp | DesignEntTemp | decimal | F |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63 |  | User | 1. DR: Need to discuss how SDD and NACM will support design vs. rated conditions |  | NO
BoilerDesignLeavingTemp | DesignLvgTemp | decimal | F |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63 |  | User | 1. DR: Need to discuss how SDD and NACM will support design vs. rated conditions |  | NO
BoilerDraftType | DraftType | enumerated list | none | Atmospheric | [5 empty] | 1. DR: Need to add MechanicalBalanced? 2. JG: Remove NaturalGas and add NaturalDraft. DP: Is Atmospheric OK? NaturalGas removed. |  | NO
MechanicalForced
MechanicalInduced
BoilerEnergyInputRatio | EIR | decimal | none |  |  | The ratio of energy used by the system to the cooling or heating capacity in the same units. EIR is used in calculating a performance curve for cooling and heating equipment. It is the reciprocal of the coefficient of performance (COP) Represented as EIR | 2013 NR ACM: 5.8.1 Boilers Boiler Part-Load Performance Curve; |  |  | 1. DR: Not sure if this term is needed except to describe the energy input of fan used for forced draft boilers. Suggest we come up with as set of additional terms used to describe draft fans. |  | NO
BoilerFluidFlowIn | FluidFlowIn | reference | none |  | FluidSegment |  |  |  | User |  |  | NO
BoilerFluidFlowOut | FluidFlowOut | reference | none |  | FluidSegment |  |  |  | User |  |  | NO
BoilerFuel | Fuel | enumerated list | none | Electric |  | Defines the type of energy used to run the equipment or provide heat. Values: electricity, natural gas, propane, fuel oil, hot water, steam, solar thermal. | 2013 NR ACM: 5.8.1 Boiler fuel |  |  |  |  | NO
HotWaterSys
NaturalGasBoiler
Oil
SteamSys
BoilerFuelFullLoad | FuelFullLoad | decimal | Btu per h |  |  | The fuel consumption at design conditions | 2013 NR ACM 5.7.6.4 Furnace, equation 42 5.8.1 Boilers equation 60; 5.9.1.2 Water Heaters equation 76 |  |  |  |  | NO
BoilerFuelPartLoad |  | decimal | Btu per h |  |  | The fuel consumption of Boilers and Furnaces at part load conditions | 2013 NR ACM 5.7.6.4 Furnace, equation 42 5.8.1 Boilers equation 60; 5.9.1.2 Water Heaters equation 76 |  |  | 1. DR: This is a property that is calculated at each timestep by the simulation program. |  | NO
BoilerHeatLoss | HeatLoss | decimal | none |  |  | The heat lost when the Boiler is firing and is expressed as a percentage of full load output capacity. The default is 2% for electric boilers and heat-exchangers and 0% for fuel-fired boilers | 2013 NR ACM: 5.8.1 Boilers Boiler Heat Loss |  |  |  |  | NO
BoilerHIRfPLRCurveCoefficent |  | decimal | none |  |  | Coefficent used tto calculate HeatingPLEffCurveFactor for Boilers. There are three HeatingPLEffCurveCoefficent values required for the calculations. | 2013 NR ACM 5.8.1 Boilers equation 60 |  |  | 1. DR: Revise NACM boiler part-load curve equation to be in terms of HIR not Eff |  | NO
BoilerHIRfPLRCurveFactor |  | decimal | none |  |  | Derived from HeatingCapRated and HeatingCapPartLoad. Expressed as FHeatPLC in equations | 2013 NR ACM 5.7.6.4 Furnace, equation 42, 43 5.8.1 Boilers equation 60 |  |  | 1. DR: This is a property that is calculated at each timestep by the simulation program. 2. DR: Revise NACM boiler part-load curve equation to be in terms of HIR not Eff |  | NO
BoilerThermalEff | ThermalEff | decimal | none |  |  | The full load of a boiler or water heater or heating coil efficiency calculated as the ratio of heat transferred to the water divided by the heat input of the fuel. | 2013 NR ACM 5.8.1 Boilers equation 59 |  |  | 1. DR: Appliance Stds are in terms of combustion eff; NACM needs equations to convert combustion eff to thermal eff. 2. DR: Need to decide if efficiencies are described as a ratio or decimal |  | NO
BoilerType | Type | enumerated list | none | HotWaterSys |  |  | 2013 NR ACM: 5.8.1 Boilers Boiler Type; |  |  |  |  | NO
SteamSys
BoilerUnloadRatioMinimum | UnloadRatioMin | decimal | none |  |  | The minimum unloading capacity of the Boiler,expressed as a percentage of the rated capacity. Below this level the equipment must cycle to meet the load. | 2013 NR ACM: 5.8.1 Boilers Boiler Minimum Unloading Ratio, Table 64, |  |  |  |  | NO
ChillerCapAvailable |  | decimal | Btu per h |  |  | The available cooling capacity calculated by applying temperature conditions and capacity curve coefficients to the rated capacity. | 2013 NR ACM 5.8.2 Chillers Chiller Cooling Capacity Adjustment Curve equations 61 |  |  | 1. DR: This is a property that is calculated at each timestep by the simulation program. |  | NO
ChillerCapfTempFactor |  | decimal | none |  |  | Calculated using temperature conditions of entering water or air and capacity coefficients for calculating the available cooling capacity of equipment. Represented as CAP_FT in equations. | 2013 NR ACM 5.8.2 Chillers Chiller Cooling Capacity Adjustment Curve equations 61, 62, 63 |  |  | 1. DR: This is a property that is calculated at each timestep by the simulation program. |  | NO
ChillerCapRated | CapRated | decimal | Btu per h |  |  | Cooling capacity of chiller equipment at prescribed rating conditions. | 2013 NR ACM 5.8.2 Chillers Chiller Rated Capacity equations |  |  |  |  | NO
ChillerCondenserIn | CondenserIn | reference | none |  | FluidSegment | [6 empty] | NO
ChillerCondenserOut | CondenserOut | reference | none |  | FluidSegment | [6 empty] | NO
ChillerCoolingEfficiencyMin | CoolEffMin | decimal | none |  |  | The minimum efficiency that the Chiller must meet. | 2013 NR ACM 5.8.2 Chillers - Chiller Rated Efficiency |  | Rule | 1. DR: Do you want a separate property that describes the minimum efficiency requirement for each piece of equipment? Typically this is determined by ruleset and the exisiting terms are used. For example, a rule is used to determine the code-minumum DX EER, and CoilCoolingEER would be set to that value for the baseline version of the data model. Also, this term would also need to follow the convention we have for efficiency rarings, that is, be specific to EER, SEER, COP, HSPF, etc... |  | NO
ChillerCoolingHourlyLoad |  | decimal | Btu per h |  |  | The current load on the cooling equipment used in calculating the PartLoadRatio | 2013 NR ACM 5.7.5 Cooling Systems Direct Expansion Cooling Efficiency Adjustment Curve equation 23 5.8.2 Chillers Electric Chiller Cooling Efficiency Adjustment Curves equation 64 |  |  | 1. DR: This is a property that is calculated at each timestep by the simulation program. Also, it currently applies to more than one type of object. If it is included in SDD, suggest having separate terms for each. |  | NO
ChillerCOP | COP | decimal | none |  |  | The efficiency of the chiller expressed as the ARI rated coefficient of performance | 2013 NR ACM 5.8.2 Chillers Chiller Rated Efficiency |  | User;#Rule |  |  | NO
ChillerCount | Count | integer | none |  |  | The number of identical Chillers. Because all the features are the same in each unit, the Count can be used as a multiplier for calculating values like capacity of all the units | 2013 NR ACM: 5.8.2 Chillers Number of Identical Chiller Units; |  |  |  |  | NO
ChillerDBOutdoorTemp |  | decimal | F |  |  | The dry bulb temperature of the outside air which affects the performance of Chiller. | 2013 NR ACM: 5.8.2 Chillers Chiller Cooling Capacity Adjustment Curve equations 62; |  | Reference | 1. DR: This is a property that is used in calculations at each timestep by the simulation program. |  | NO
ChillerDesignEnteringTemp |  | decimal | F |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63 |  | User;#Rule | 1. DR: Need to discuss how SDD and NACM will support design vs. rated conditions |  | NO
ChillerDesignLeavingTemp |  | decimal | F |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63 |  | User;#Rule | 1. DSP: Do we need separate terms for each e.g. boiler and chiller? DR: Need to discuss how SDD and NACM will support design vs. rated conditions |  | NO
ChillerEIRfPLRCurveCoefficient |  | decimal | none |  |  | Coefficient used in calculating EIRFactorPLR. There are 3 coefficient values required for the calculations. | 2013 NR ACM 5.8.2 Chillers Electric Chiller Cooling Efficiency Adjustment Curves Tables 72 and 73 and 64 equations |  |  | JG: 1. Shouldn't this be an array? DP: This is the definition of the individual coefficient. The array called ChillerEIR-PLRCoefficients is defined in the HVAC objects list |  | NO
ChillerEIRfTempCurveCoefficient |  | decimal | none |  |  | Used in calculating EIRFactorTemp. There are 6 ChillerEIRTempCoefficient required for the calculations. | 2013 NR ACM 5.8.2 Chillers Electric Chiller Cooling Efficiency Adjustment Curves Tables 70 and 71 and 64 equations |  |  |  |  | NO
ChillerEIRfTempFactor |  | decimal | none |  |  | A factor applied to the EnergyInputRatio to account for the affect of different temperature attributes. | 2013 NR ACM 5.8.2 Chillers Electric Chiller Cooling Efficiency Adjustment Curves equation 64; 5.7.6.5 | CoilType = HeatPump and DirectExpansion only |  | 1. DR: This is a property that is calculated at each timestep by the simulation program. |  | NO
ChillerEnergyInputRatio | EIR | decimal | none |  |  | The ratio of energy used by the system to the cooling capacity in the same units. EIR is used in calculating a performance curve for cooling and heating equipment. It is the reciprocal of the coefficient of performance (COP) Represented as EIR | 2013 NR ACM: 5.8.2 Chillers Electric Chiller Cooling Efficiency Adjustment Curves |  |  |  |  | NO
ChillerEngineSpeedMin | EngineSpeedMin | decimal | none |  |  | The minimum fraction of full speed for engine driven chiller. It is used in calculating three sets of curves for different ranges of operation based on the engine speed. The value used in DOE2 is 0.3125. | 2013 NR ACM: 5.8.2 Chillers Tables 67, 75, 77 |  | User |  |  | NO
ChillerEvaporatorIn | EvapIn | reference | none |  | FluidSegment | [6 empty] | NO
ChillerEvaporatorOut | EvapOut | reference | none |  | FluidSegment | [6 empty] | NO
ChillerFIRfPLRCurveCoefficient |  | decimal | none |  |  | Used in calculating FIRFactorPLR for chillers that are fueled by steam or gas rather then electricity. This includes all absorption chillers. There are 4 ChillerFIR-PLRCoefficient required for the calculations. | 2013 NR ACM 5.8.2 Chillers Fuel and Steam Chiller Cooling Efficiency Adjustment Curves Tables 74 and 75 Note table 74 categories are not orthogonal |  |  |  |  | NO
ChillerFIRfPLRFactor |  | decimal | none |  |  | A factor applied to the Fuel Input Ratio (FIR) to account for the Part Load Ratio (PLR) | 2013 NR ACM 5.8.2 Chillers Fuel and Steam Chiller Cooling Efficiency Adjustment Curves equation 65,66 |  |  | 1. DR: This is a property that is calculated at each timestep by the simulation program. |  | NO
ChillerFIRfTempCurveCoefficient |  | decimal | none |  |  | One of 6 values used in calculating FIRFactorTemp for chillers that are fueled by steam or gas rather then electricity. This includes all absorption chillers. There are 6 ChillerFIRTempCoefficient values required for the calculations. | 2013 NR ACM 5.8.2 Chillers Fuel and Steam Chiller Cooling Efficiency Adjustment Curves Tables 76 and 77 Note table 76 categories are not orthogonal |  |  |  |  | NO
ChillerFuel | Fuel | enumerated list | none | Electric |  | Defines the type of energy used to run the equipment or provide heat. Values: electricity, natural gas, propane, fuel oil, hot water, steam, solar thermal. | 2013 NR ACM: 5.8.2 Chiller Fuel Tables 67, 68 and 69 are specific to the fuel type. | HotWater, Steam: Indirect-fired absorption untis only. NaturalGas, Oil: Direct-fired abssorption units only |  |  |  | NO
HotWaterSys
NaturalGasBoiler
Oil
SteamSys
ChillerFuelOperating |  | decimal | Btu per h |  |  | The rated fuel consujmption adjusted for part load ratio, | 2013 NR ACM 5.8.2 Chillers Fuel and Steam Chiller Cooling Efficiency Adjustment Curves equation 65,66 |  | User |  |  | NO
ChillerFuelRated |  | decimal | Btu per h |  |  | The ARI rated fuel consumption of Chiller | 2013 NR ACM 5.8.2 Chillers Fuel and Steam Chiller Cooling Efficiency Adjustment Curves equation 65,66 |  | User |  |  | NO
ChillerLeavingTemp |  | decimal | F |  |  | The temperature of a liquid as it leaves a piece of equipment. | 2013 NR ACM Equations 62, 63, 64, 66 refer to chilled water supply temperature, which is the temperature of chilled water as it leaves the chiller. |  |  | 1. DR: This is a property that is used in calculations at each timestep by the simulation program. |  | NO
ChillerPowerRated |  | decimal | kW |  |  | The rated electrical power draw of the Chiller at full capacity under ARI rating conditions. |  |  | User |  |  | NO
ChillerType | Type | enumerated list | none | Centrifugal | [5 empty] | 1. DR: Adsorption is not listed in 2013 NACM, and currently not supported by E+, so suggest we remove this type. 2. DR:Could have only Type = Absorption, and add new property 'AbsorptionType' with enumerations Single, Double, Direct (see Table 74 and 76). 3. DR: 2013 NACM currently does not have TripleEffect. 4. JG: Add Engine driven chiller to list. 5. DR: E+ categorizes WSEs as a Type of HeatExchanger object, while DOE-2 categorizes this as a Type of Chiller object. I suggest we stay with E+ convention. |  | NO
DoubleEffectAbsorption
HeatPump
HeatRecovery
Reciprocating
Screw
SingleEffectAbsorption
TripleEffectAbsorption
ChillerUnloadRatioMinimum | UnloadRatioMin | decimal | none |  |  | The minimum unloading capacity of the Chiller, expressed as a percentage of the rated capacity. Below this level the equipment must cycle to meet the load. | 2013 NR ACM: 5.8.2 Chillers Table 85 Default Minimum Unloading Ratios; |  |  |  |  | NO
CoilCondenserFlowType | CondFlowType | enumerated list | none | CondenserFixedFlow |  | Describes water flow control for a water-cooled condenser | 2013 NR ACM: 5.7.5.2 Direct Expansion Condenser Flow Type; |  | User | 1. DSP: Should this be folded into the Coil control strategy term(s)? DR: No, but need to discuss if we need to have both a CoilHeating and CoilCooling:CondenserFlowType |  | NO
CondenserTwoPositionFlow
CondenserVariableFlow
None
CoilCondenserType | CondType | enumerated list | none | Air |  | Defines the the type condenser heat sink used for DirectExpansion and HeatPump coils |  |  |  | 1. DR: See note for CoilCondenserFlowType 2. JG: Add evaporatively cooled as another option. |  | NO
Fluid
None
CoilCoolingBF_fAirFlowCurveCoefficient |  | decimal | none |  |  | Coefficient used to account for variation in air flow across the coil in calculating the adjusted coil bypass factor. There are four coefficient values used in the calculation. | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Adjustment Curve, Table 51 |  | User |  |  | NO
CoilCoolingBF_fPLRCurveCoefficient |  | decimal | none |  |  | Coefficient used to calculate the multiplier on the rated coil bypass factor to account for the part load ratio. There are two coefficient values used in the calculation. | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Adjustment Curve, Table 53 |  | User |  |  | NO
CoilCoolingBF_fTempCurveCoefficient |  | decimal | none |  |  | Coefficient used to account for a variation in coil entering conditions in calculatating the adjusted coil bypass factor. There are six coefficient values used in the calculation. | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Adjustment Curve, Table 52 |  | User |  |  | NO
CoilCoolingBFDesign | CBFDesign | decimal | none |  |  | The default design value assigned to the ratio of air that bypasses the cooling coil at design conditions to the total system airflow. | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Table 50 Default Coil Bypass Factors | 2013 NR ACM Table 50 requires system type in order to assign this value. | Rule | 1. DR: This term may be redundant to CBFRated; the NACM needs to clarify if the CBF should be defined at ARI condition only, or all for specificaiton design condition as well. Once decided, eqn 17 should be revised to reflect intent. |  | NO
CoilCoolingBFRated | CBFRated | decimal | none |  |  | The rated coil bypass factor at ARI conditions and is used to calculate the adjusted coil bypass factor value | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Adjustment Curve, Equations 17 |  | User |  |  | NO
CoilCoolingCap_fTempCurveCoefficient |  | decimal | none |  |  | One of six values used in calculating the available cooling capacity of the coil. | 2013 NR ACM Table 49 –Cooling Capacity Curve Coefficients; |  | User |  |  | NO
CoilCoolingCapSensibleAdjusted | CapSensAdj | decimal | Btu per h |  |  | Adjusts the CoilCapSensibleRated for supply fan heat | 2013 NR ACM 5.7.5 Cooling Systems Total Cooling Capacity Equation 12 |  |  | 1. DR: This value is calculated from coil rated value and fan BHP. Need to determine if this is specified by user, or calculated only by ruleset. |  | NO
CoilCoolingCapSensibleRated | CapSensRated | decimal | Btu per h |  |  | Heating or cooling capacity at prescribed rating conditions. For example, packaged DX systems are rated at ARI conditions | 2013 NR ACM 5.7.5 Cooling Systems Total Cooling Capacity Equation 11; 5.8.2 Chillers Chiller Rated Capacity equations 61; 5.7.6.4 Furnace 5.7.6.5 Electric Heat Pump equation 45; |  |  |  |  | NO
CoilCoolingCapTotalAdjusted | CapAdj | decimal | Btu per h |  |  | The rated cooling capacity of the coil adjusted for different effects e.g. supply fan heat | 2013 NR ACM 5.7.5 Cooling Systems Total Cooling Capacity Equation 11 | Packaged equipment only? |  | 1. DR: This value is calculated from coil rated value and fan BHP. Need to determine if this is specified by user, or calculated only by ruleset. |  | NO
CoilCoolingCapTotalRated | CapTotRated | decimal | Btu per h |  |  | The total cooling capacity of a coil at rated conditions | [5 empty] | NO
CoilCoolingDesignCoolingTemp | DesignClgTemp | decimal | F |  |  | The design cooling temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also is cold deck temp |  |  |  | 1. DR: Should this be with or w/o fan heat? DSP: Is there a reference to this in the 2013 NR ACM? DR: See 5.7.2.2 Cooling Supply Air Temperature. Other control specification are defined at AirSystem object, so this may be best defined there as well. |  | NO
CoilCoolingDxEER | DxEER | decimal | none |  |  | The energy efficiency ratio (EER) of net cooling capacity (in Btu/hr) to total rate of electrical energy input (in watts), of cooling equipment under designated operating conditions. | 2013 NR ACM 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency, equations 21 and 22 | CoilType = HeatPump and DirectExpansion only | User;#Rule |  |  | NO
CoilCoolingDxEIR_fPLRCurveCoefficient |  | decimal | none |  |  | One of four values used in in calculating EIRFactorPLR | 2013 NR ACM 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency Adjustment Curve equation 24 |  | User |  |  | NO
CoilCoolingDxEIR_fTempCurveCoefficient |  | decimal | none |  |  | One of six values used in adjusting efficiency to account for the wet-bulb temperature entering the coil and the outdoor dry-bulb temperature | 2013 NR ACM 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency Adjustment Curve equation 25, 26 |  | User |  |  | NO
CoilCoolingDxEIRFactorAirflowVerified | EIRFactorAirflowVerified | decimal | none |  |  | A performance adjustment factor set to 0.925 as a default. For systems where the airflow has been verified, it is 1.00 | 2013 NR ACM 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves |  | User | DR: Renamed to emphasize this is an adjustment factor for cooling EIR |  | NO
CoilCoolingDxEnergyInputRatio | DxEIR | decimal | none |  |  | The ratio of energy used by the system to the cooling or heating capacity in the same units. EIR is used in calculating a performance curve for cooling and heating equipment. It is the reciprocal of the coefficient of performance (COP) Represented as EIR | 2013 NR ACM: 5.7.5.2 Direct Expansion - Direct Expansion Cooling Efficiency Adjustment Curve; |  |  | 1. DR: This term is defined in NACM by a footnote. Suggest we discuss revising NACM to make conversion of EERAdj/COPAdj to CoolingEIR/HeatingEIR more explicit |  | NO
CoilCoolingDxFDDFactor | DxFDDFactor | decimal | none |  |  | The Fault Detection and Diagnosis performance factor and is used in calculating a performance curve for cooling and heating coil equipment. If FDD exists the value is 0.95. Otherwise it is 0.90. | 2013 NR ACM 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves |  | User |  |  | NO
CoilCoolingDxRefrigerantChargeFactor | DxRefrgChrgFactor | decimal | none |  |  | Used to adjust cooling efficiency for assumed slightly degraded performance if refrigerant charge is not verified through acceptance test procedures | 2013 NR ACM 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency Adjustment Curve |  | User |  |  | NO
CoilCoolingDxSEER | DxSEER | decimal | none |  |  | The Seasonal Energy Efficiency Ratio (SEER) of the coil in a DX cooling system | 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency | CoilType = HeatPump and DirectExpansion only | User;#Rule |  |  | NO
CoilCoolingDxUnloadRatioMinimum | UnloadRatioMin | decimal | none |  |  | The minimum unloading capacity of the Coil,expressed as a percentage of the rated capacity. Below this level the equipment must cycle to meet the load. | 2013 NR ACM: 5.7.5.2 Direct Expansion Minimum Unloading Ratio Unloading Ratios; |  |  |  |  | NO
CoilCoolingFuelSource | FuelSource | enumerated list | none | Electric |  |  |  |  | User |  |  | NO
NaturalGas
Oil
CoilCoolingSizingRatio | SizingRatio | decimal | none |  |  | The percent that the baseline cooling equipment is oversized after sizing calculations are performed. Current value is 15% for cooling equipment. | 2013 NR ACM: 2.4 Calculation Procedures step 8. oversizing the baseline cooling equipment by 15%; |  | User | 1. DR: Need to clarify in NACM if this applies to only coils or also fans |  | NO
CoilCoolingType | Type | enumerated list | none | ChilledWater |  |  |  |  | User |  |  | NO
DirectExpansion
WaterEconomizer
CoilCoolingWaterEconoCWSTempMax | WaterEconoCWSTempMax | decimal | F |  |  | The control temperature of the condenser water supply temperature above which the water-side economizer is disabled. | 2013 NR ACM 5.8.4 Water-side Economizers Water-Side Economizer Maximum CWS |  | User |  |  | NO
CoilCoolingWaterEconoCWSTempSetpoint | WaterEconoCWSTempSetpoint | decimal | F |  |  | The design condenser water supply temperature for the cooling tower in economizer mode. | 2013 NR ACM 5.8.4 Water-side Economizers Water-Side Economizer CWS Setpoint |  | User |  |  | NO
CoilCoolingWaterEconoDBTempMax | WaterEconoDBTempMax | decimal | F |  |  | The control temperature (outside air dry-bulb temperature) above which the water-side economizer is disabled. | 2013 NR ACM 5.8.4 Water-side Economizers Water-Side Economizer Maximum Tdb |  | User |  |  | NO
CoilCoolingWaterEconoHXEff | WaterEconoHXEff | decimal | none |  |  | Ratio expressing the effectiveness of a water-side heat exchanger at design conditions,dependent on entering and leaving temperatures | 2013 NR ACM 5.8.4 Water-side Economizers Water-Side Economizer HX Effectiveness |  | User |  |  | NO
CoilCoolingWaterEconoType | WaterEconoType | enumerated list | none | None |  | The type of water-side economizer used in cooling. | 2013 NR ACM 5.8.4 Water-side Economizers Water Economizer Type |  | User |  |  | NO
ParallelHX
SeriesHX
StrainerCycle
ThermoCycle
CoilCoolingWBEnteringTemp |  | decimal | F |  |  | The wet bulb temperature of the air as it enters cooling equipment. | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 14-16; |  |  | 1. DR: Is this the rated EWB? DSP: The equations list it as "The entering coil wet-bulb temperature (°F)" DR: This is a property that is calculated at each timestep by the simulation program. A coil may be sized based on non-ARI EWB temps, but we need to have a dicussion on how the SDD/NACM will handle design vs. rated conditions. |  | NO
CoilFluidFlowIn |  | reference | none |  | FluidSegment | Defined for Coil type = HotWater, ChilledWater, WaterEconomizer only |  | CoilType = HotWater, ChilledWater, TwoPipe, WaterEconomizer only |  |  |  | NO
CoilFluidFlowOut |  | reference | none |  | FluidSegment | Defined for Coil type = HotWater, ChilledWater, WaterEconomizer only |  | CoilType = HotWater, ChilledWater, TwoPipe, WaterEconomizer only |  |  |  | NO
CoilHeatingCrankcaseControlTemp | CrankcaseCtrlTemp | decimal | F |  |  | The dry bulb temperature at which the crank case in an electric heat pump is shut off. | 2013 NR ACM: 5.7.6.5 Electric Heat Pump Heat Pumps Crank Case Heater Shutoff Temperature | CoilType = HeatPump and DirectExpansion only | Rule |  |  | NO
CoilHeatingDesignHeatingTemp | DesignHtgTemp | decimal | F |  |  | The design heating temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also is hot deck temp | ??? |  |  | 1. DSP: Is there a reference to this in the 2013 NR ACM? DR: See 5.7.3.2 Heating Supply Air Temperature. Other control specification are defined at AirSystem object, so this may be best defined there as well. |  | NO
CoilHeatingFuelSource | FuelSource | enumerated list | none | Electric |  |  |  |  | User |  |  | NO
NaturalGas
Oil
CoilHeatingFurnaceAFUE | AFUE | decimal | none | [5 empty] | User |  |  | NO
CoilHeatingFurnaceFuelFullLoad | FuelFullLoad | decimal | Btu per h |  |  | The fuel consumption at design conditions | 2013 NR ACM 5.7.6.4 Furnace, equation |  |  |  |  | NO
CoilHeatingFurnaceHIR_fPLRCurveCoefficent |  | decimal | none |  |  | Used to calculate HeatingPLEffCurveFactor for Furnaces. There are three HeatingPLEffCurveCoefficent values required for the calculations. | 2013 NR ACM 5.7.6.4 Furnace, Table 59, equation 43 |  |  |  |  | NO
CoilHeatingFurnaceIgnitionType | IgnitionType | enumerated list | none | IntermittentIgnitionDevice |  | Either pilot or an intermittent ignition device (IID) in furnaces. An IID is mandatory for furnaces with capacities of 225,000 Btu/h and greater. | 2008 Title 24: Section 112 Mandatory Requirements For Space-Conditioning Equipment (d) Gas- and Oil-Fired Furnace Standby Loss Controls | CoilType = Furnace only |  | 1. DR: Confirm this is in 2013 NACM |  | NO
PilotLight
CoilHeatingFurnacePilotFuelInput | PilotFuelInput | decimal | Btu per h |  |  | The measure of energy required by the Furnace pilot light. | 2013 NR ACM: 5.7.6.4 Furnace Furnace Fuel Heating Pilot | CoilType = Furnace only |  |  |  | NO
CoilHeatingFurnaceThermalEff | ThermalEff | decimal | none |  |  | The full load of a water heater or heating coil efficiency calculated as the ratio of heat transferred to the water divided by the heat input of the fuel. | 2013 NR ACM 5.7.6.4 Furnace equation 41 | CoilType = Furnace only | User;#Rule |  |  | NO
CoilHeatingHpCap_fTempCurveCoefficient |  | decimal | none |  |  | Used in calculating the available heating capacity of heat pumps. There are four coefficient values required for the calculations. | 2013 NR ACM 5.7.6.5 Electric Heat Pump Table 60 |  |  |  |  | NO
CoilHeatingHpCOP | HpCOP | decimal | none |  |  | The ARI rated coefficient of performance for the heating equipment such as a heat pump | 2013 NR ACM 5.7.6.5 Electric Heat Pump Electric Heat Pump Heating Efficiency | CoilType = HeatPump only | User;#Rule |  |  | NO
CoilHeatingHpCOPAdjusted |  | decimal | none |  |  | The heating COP adjusted to remove the effect of fan energy | 2013 NR ACM 5.7.6.5 Electric Heat Pump equation 45 |  | User | 1. DR: 5.7.5.2 also has EERAdjusted, but this term is not currently defined. |  | NO
CoilHeatingHpDefrostControl | DefrostCtrl | enumerated list | none | OnDemand |  | Defines how the defrosting is activated, either on demand or on a timed cycle which is by default 3.5 minutes in length | 2013 NR ACM: 5.7.6.5 Heat Pumps Coil Defrost | CoilType = HeatPump only | Rule |  |  | NO
TimedCycle
CoilHeatingHpDefrostHeatSource | DefrostHeatSrc | enumerated list | none | Electric |  | Defines the source of the defrosting heat which is usually hot gas or electric resisitance | 2013 NR ACM: 5.7.6.5 Heat Pumps Coil Defrost | CoilType = HeatPump only | Rule |  |  | NO
HotGas
CoilHeatingHpEIR_fPLRCurveCoefficient |  | decimal | none |  |  | Used to calculate EIR- FPLR and EIR-FT for heat pumps. There are four HeatPumpEffCurveCoefficient values required for the calculations. | 2013 NR ACM 5.7.6.5 Electric Heat Pump Table 61 |  | User |  |  | NO
CoilHeatingHpEIR_fPLRFactor |  | decimal | none |  |  | A factor applied to the Energy Input Ratio (EIR) to account for the PartLoadRatio. | 2013 NR ACM 5.7.6.5 Electric Heat Pump Heating Efficiency Adjustment Curves equations 50, 53 | CoilType = HeatPump and DirectExpansion only | Rule | 1. DR: This is a property that is calculated at each timestep by the simulation program. |  | NO
CoilHeatingHpEIR_fTempCurveCoefficient |  | decimal | none |  |  | Used to calculate EIR- FPLR and EIR-FT for heat pumps. There are four HeatPumpEffCurveCoefficient values required for the calculations. | 2013 NR ACM 5.7.6.5 Electric Heat Pump Table 61 |  |  |  |  | NO
CoilHeatingHpEIR_fTempFactor |  | decimal | none |  |  | A factor applied to the EnergyInputRatio to account for the affect of different temperature attributes. | 2013 NR ACM 5.7.6.5 Electric Heat Pump Heating Efficiency Adjustment Curves equations 51, 52, 53 | CoilType = HeatPump and DirectExpansion only |  | 1. DR: This is a property that is calculated at each timestep by the simulation program. |  | NO
CoilHeatingHpEnergyInputRatio | EIR | decimal | none |  |  | The ratio of energy used by the system to the cooling or heating capacity in the same units. EIR is used in calculating a performance curve for cooling and heating equipment. It is the reciprocal of the coefficient of performance (COP) Represented as EIR | 2013 NR ACM: 5.7.5.2 Direct Expansion - Direct Expansion Cooling Efficiency Adjustment Curve; |  |  | 1. DR: NACM reference is to Cooling Efficiency. Suggest we discuss revising NACM to make conversion of EERAdj/COPAdj to CoolingEIR/HeatingEIR more explicit |  | NO
CoilHeatingHpHSPF | HSPF | decimal | none |  |  | A measure of efficiency of heating equipment using Heating Season Performance Factor (HSPF) | 2013 NR ACM 5.7.6.5 Electric Heat Pump Electric Heat Pump Heating Efficiency | CoilType = HeatPump only | User;#Rule |  |  | NO
CoilHeatingHpSupplementalOATemp |  | decimal | F |  |  | The dry bulb temperature at which supplemental heating equipment is allowed to be turned on | 2013 NR ACM 5.7.6.5 Heat Pumps Electric Heat Pump Electric Supplemental Heating Control Temp |  |  |  |  | NO
CoilHeatingSizingRatio | SizingRatio | decimal | none |  |  | The percent that the baseline heating equipment is oversized after sizing calculations are performed. Current value is 25% for heating equipment. | 2013 NR ACM: 2.4 Calculation Procedures step 8. oversizing the baseline heating system by 25%; |  | User | 1. DR: Need to clarify in NACM if this applies to only coils or also fans |  | NO
CoilHeatingType | Type | enumerated list | none | ElectricResistance |  |  |  |  | User |  |  | NO
Furnace
HeatPump
HotWater
EnergyRecoveryExhaustFlow | ExhaustFlow | reference | none |  | FluidSegment |  |  | CoilType = HotWater, ChilledWater, TwoPipe, WaterEconomizer only |  |  |  | NO
EnergyRecoveryFluidFlowIn | FluidFlowIn | reference | none |  | FluidSegment |  |  | CoilType = HotWater, ChilledWater, TwoPipe, WaterEconomizer only |  |  |  | NO
EnergyRecoveryFluidFlowOut | FluidFlowOut | reference | none |  | FluidSegment |  |  | CoilType = HotWater, ChilledWater, TwoPipe, WaterEconomizer only |  |  |  | NO
EnergyRecoverySupplyFlow | SupplyFlow | reference | none |  | FluidSegment |  |  | CoilType = HotWater, ChilledWater, TwoPipe, WaterEconomizer only |  |  |  | NO
EnergyRecoveryType | Type | enumerated list | none | CrossFlow | [5 empty] | 1. JG: Add support options related to 5.8.7 heat recovery equipment in a plant. |  | NO
RunAroundLoop
Wheel
EvapCoolerAirFlowPrimaryDesign | AirFlowPrimaryDesign | decimal | ft3 per min |  |  | The design primary air stream airflow for the evaporative cooler used to calculate the part load ratio in the performance curve calculations. | 2013 NR ACM 5.7.5.3 Evaporative Cooler Evaporative Cooling Performance Curves Equation 39 |  | User |  |  | NO
EvapCoolerAirFlowPrimaryOperating | AirFlowPrimaryOperating | decimal | ft3 per min |  |  | The operating primary air stream airflow for the evaporative cooler, used to calculate the part load ratio in the performance curve calculations. | 2013 NR ACM 5.7.5.3 Evaporative Cooler Evaporative Cooling Performance Curves Equation 39 |  | User |  |  | NO
EvapCoolerEffectiveness | Effectiveness | decimal | none |  |  | A ratio that represents the effectiveness of an EvaporativeCooler | 2013 NR ACM 5.7.5.3 Evaporative Cooler equations 37 and 38 |  | User |  |  | NO
EvapCoolerEnteringDBTemp | EnteringDBT | decimal | F |  |  | The dry bulb temperature of the supply air as it enters the evaporative cooler. | 2013 NR ACM 5.7.5.3 Evaporative Cooler equations 37 and 38 |  | Reference |  |  | NO
EvapCoolerEnteringWBTemp | EnteringWBTemp | decimal | F |  |  | The wet bulb temperature of the entering air or "scavenger air" as it enters the evaporative cooler, depending on the type of evaporative cooler. | 2013 NR ACM 5.7.5.3 Evaporative Cooler equations 37 and 38 |  | Reference |  |  | NO
EvapCoolerLeavingDBTemp | LeavingDBT | decimal | F |  |  | The dry bulb temperature of the supply air or direct stage air as it leaves the evaporative cooler, depending on the type of evaporative cooler. | 2013 NR ACM 5.7.5.3 Evaporative Cooler equations 37 and 38 |  | Reference |  |  | NO
EvapCoolerPerformanceCoefficient | PerformanceCoeff | decimal | none |  |  | One of three values used to calculate the performance curve for EvaporativeCooler | 2013 NR ACM 5.7.5.3 Evaporative Cooler equations 37 and 38 |  | User |  |  | NO
EvapCoolerType | Type | enumerated list | none | IntegratedDirectIndirect |  | Defines the type of EvaporativeCooler operation | 2013 NR ACM 5.7.5.3 Evaporative Cooler Evaporative Cooling Type |  | User |  |  | NO
IntegratedIndirect
NonIntegratedDirectIndirect
NonIntegratedIndirect
FanAxialType |  | enumerated list | none | Vane |  | Defines the mechanism of an axial fan | 2013 NR ACM 5.7.3 Fan Systems Part Load Power Curve Table 46 – Fan Curve Default Values |  | User | 1. DR: I don't see a power curve for AxialType = Vane. Also see comment for FanCentrifugalType |  | NO
VaneVariablePitchBlades
FanCentrifugalType |  | decimal | none | AirFoil |  | Defines the mechanism of a centrifugal fan | 2013 NR ACM 5.7.3 Fan Systems Part Load Power Curve Table 46 – Fan Curve Default Values |  | User | 1. DR: We should evaluate alternatives for defining the fan part-load performance, because this is one area where the current NACM is not consistent. |  | NO
AirFoilInletVanes
BackwardInclined
BackwardInclinedInletVanes
ForwardCurved
ForwardCurvedInletVanes
FanControlMethod | ControlMethod | enumerated list | none | ConstantVolume |  |  | 2013 NACR ACM 5.7.3.2, |  |  | 1. DR: See comment on FanCentrifugalType |  | NO
Dampers
InletVanes
TwoSpeedFanCtrl
VarPitch
VarSpeedDrive
FanDriveEfficiency |  | decimal | none |  |  | A measure of how much power transferred through the drive to the fan is lost as heat. DriveEff is one of the parameters used in calculating FanPowerIndex for performance compliance. | 2013 NR ACM 5.7.3.2 Supply Fans Supply Fan Brake Horsepower |  | User |  |  | NO
FanFlowCapacity | FlowCap | decimal | ft3 per min |  |  | Defines the volumetric capacity of the fan measured in cubic ft per minute (cfm). The fan's peak airflow is what it is rated at when running at full capacity. | 2013 Title 24: Section 140.4 (c) Power Consumption of Fans 2013 NR ACM 5.6.5.3 Zone Exhaust Exhaust Air Flow Rate; 5.7.3.4 Exhaust Fan Systems Exhaust Fan Rated Capacity; 5.7.3.2 Supply Fans Supply Fan Design Air Rated Capacity |  |  |  |  | NO
FanFlowMinimum | FanFlowMin | decimal | ft3 per min |  |  | The lowest flow rate rated for a fan | 2013 ? |  |  |  |  | NO
FanFlowPLRFactor |  | decimal | none |  |  | The ratio of AirFlowRate at part load to AirFlowRate at full load | 2013 NR ACM 5.7.3 Fan Systems Part Load Power Curve |  | Reference | 1. DR: This is a property that is calculated at each timestep by the simulation program. |  | NO
FanModelingMethod | ModelingMethod | enumerated list | none | BrakeHorsePower |  | Defines how the FanSystem is modeled. | 2013 NR ACM 5.7.3.2 Supply Fans; 5.7.3.4 Exhaust Fan Systems |  | User | 1. DR: Do we need to support multiple methods of describing fan power? Is the modeling method not applicable to Return/Relief fans, since it is not defined there? |  | NO
PowerPerUnitFlow
StaticPressure
FanMotorBHP | MotorBHP | decimal | hp |  |  | The brake horsepower of the motor before the loss in power caused by the gearbox, alternator, differential, and other auxiliary components. | 2013 NR ACM 5.7.3 Fan systems, |  |  |  |  | NO
FanMotorEfficiency | MotorEff | decimal | none |  |  | Indicates how well the motor converts electrical power into mechanical power and is defined as output power divided by input power expressed as a percentage . | 2013 NR ACM 5.7.3.2 Supply Fans Supply Motor Efficiency |  |  |  |  | NO
FanMotorHP | MotorHP | decimal | hp |  |  | The nameplate (rated) horsepower of the fan motor. | 2013 NR ACM Supply Motor Efficiency Table N2-20 Minimum Nominal Efficiency for Electric Motors (from 2008 NR ACM) |  |  |  |  | NO
FanMotorPoleCount | MotorPoleCount | integer | none |  |  | The number of pole electromagnetic windings in the motor's stator and used to assign MotorEfficiency. Poles is always paired, so PoleCount is always a multiple of 2. | 2013 NR ACM 5.7.3 Fan systems, References 2008 NR ACM Table N2-20 which requires PoleCount of the motor |  | User |  |  | NO
FanMotorPosition | MotorPosition | enumerated list | none | InAirStream |  | Defines where the Fan motor is located relative to the cooling air stream. Values: InAirStream, NotInAirStream | 2013 NR ACM 5.7.3 Fan systems, Motor position |  | User |  |  | NO
NotInAirStream
FanMotorRotationalSpeed | MototRPM | integer | rpm |  |  | The number of full revolutions in a unit of time and is used to assign MotorEfficiency. 2008 NR ACM table N2-20 has four speeds: 3600 rpm, 1800 rpm, 1200 rpm, 900 rpm. | 2013 NR ACM 5.7.3 Fan systems, References 2008 NR ACM Table N2-20 which requires RotationalSpeed of the motor |  | User |  |  | NO
FanMotorType | MotorType | enumerated list | none | Enclosed |  | Defines if the motor is Open or Enclosed | 2013 NR ACM 5.7.3 Fan systems, References 2008 NR ACM Table N2-20 which requires EnclosedType of the motor |  | User | 1. DR: Need to add enumerations for Open and Enclosed |  | NO
Open
FanOverallEfficiency |  | decimal | none |  |  | The efficiency of the Fan as a whole at design conditions | 2013 NR ACM: 5.7.3 Fan Systems Supply Fan Efficiency, Return/Relief Fan Efficiency |  | User | 1. DR: The NACM definition of Fan Efficiency is not clear. I believe the intent is this term indicate the combined motor, drive, and fan efficiency as a whole. If so, should consider revising to FanOverallEfficiency |  | NO
FanPartLoadPowerCurve | PLPowerCurve | reference | none | [6 empty] | 1. DSP: Are we going to have an object called FanPartLoadCurve? If so, what about all the other performance curves? DR: The fan power curve terminology needs to be reviewed |  | NO
FanPower | Power | decimal | kW |  |  | The power of the fan system at AirFlowCap | 2013 NR ACM 5.7.3.2 Supply Fan kW |  |  | 1. DR: The units in NACM are kW/cfm, which makes this redundant to PowerPerFlow and FanPowerIndex. This section of NACM needs to be reviewed and revised for consistancy. |  | NO
FanPower_fPLRCurveCoefficient |  | decimal | none |  |  | One of four values used in calculating the Fan part-flow power curve. | 2013 NR ACM 5.7.3 Fan Systems Part Load Power Curve Table 46 |  | User |  |  | NO
FanPowerIndex |  | decimal | W per ft3 per min |  |  | The power consumption of the all fans in the system divided by the airflow in watts per cfm of supply air | 2013 NR ACM 5.7.3.2 Supply Fans Supply Fan Brake Horsepower; 5.7.3.3 Relief Fans Return/Relief Fan Brake Horsepower |  | User |  |  | NO
FanPowerMinimum | PowerMin | decimal | W |  |  | The lowest Fan power draw and is used in calculating PartLoadRatio | 2013 NR ACM 5.7.3 Fan Systems Part Load Power Curve Equation 9 |  | User | 1. DR: May need to revise units to kW or ratio, depending on how other terms are defined. |  | NO
FanPowerPerFlow | PowerPerFlow | decimal | W per ft3 per min |  |  | Measures the full load power of the Fan per unit of air flow. | 2013 NR ACM 5.7.3 Fan Systems |  |  |  |  | NO
FanTotalStaticPressure | TotalSP | decimal | in |  |  | The design static pressure for the Fan | 2013 NR ACM 5.7.3 Fan Systems Supply Fan Static, Pressure Return/Relief Design Static Pressure |  | User | 1. DR: Units need to be "in H20", or inches of water column |  | NO
FluidSegmentConductionLoss |  | decimal | Btu per h F |  |  | The heat loss rate of piping which varies depending on pipe length and surrounding environment. | 2013 NR ACM 5.9.1 Water Heating 5.9.1.3 Recirculation Systems |  |  |  |  | NO
FluidSegmentPipeDiameter |  | decimal | in |  |  | The nominal diameter of the pipe, used in assigning insulation thickness. | 2013 Title 24: Section 120 Requirements For Pipe Insulation |  |  |  |  | NO
FluidSegmentPipeInsulationThk |  | decimal | in |  |  | Defines how thick insulation on pipes in a heating, cooling, water heating system is. | 2013 Title 24: Section 120 Requirements For Pipe Insulation |  |  |  |  | NO
FluidSegmentPrimarySegment | PrimarySegment | reference | none |  | FluidSegment | [6 empty] | NO
FluidSegmentSource | Source | enumerated list | none | FluidSystem |  |  |  | FluidFlowSegmentType = MakeUp only |  |  |  | NO
MunicipalWater
WellWater
FluidSegmentType | Type | enumerated list | none | LoadResetCoolCtrl | [7 empty] | NO
MakeupAir
PrimaryReturn
PrimarySupply
SecondaryReturn
SecondarySupply
FluidSystemCoolControl | CoolCtrl | enumerated list | none | FixedAirCool |  |  | 2013 NR ACM 5.7.2.2 Cooling Control |  |  |  |  | NO
OAResetAirCool
ScheduledAirCool
FluidSystemCoolResetSchedule | CoolResetSch | reference | none |  |  | The name of the reset schedule object that defines outdoor and supply water temperature control points during cooling. |  |  | User |  |  | NO
FluidSystemDescription | Description | integer | none | [6 empty] | 1. DR: Need to determine if this term is necessary. If so, should it be an enumerated list, or a string input? |  | NO
FluidSystemEquipmentControl | EquipCtrl | reference | none |  |  | Defined if more than one piece of equipment |  |  |  | 1. DR: Need to decide how to handle FluidSystem equipment controls DPS: Is this an object with properties like FDD enabled, control range, control mechanism, or is it an enumeration of control types? |  | NO
FluidSystemHeatControl | HeatCtrl | enumerated list | none | FixedAirCool |  |  | 2013 NR ACM 5.7.2.3 Heating Control |  |  |  |  | NO
OAResetAirCool
ScheduledAirCool
FluidSystemHeatlResetSchedule | HeatResetSch | reference | none |  |  | The name of the reset schedule object that defines outdoor and supply water temperature control points during heating. |  |  | User |  |  | NO
FluidSystemType | Type | decimal | none | ChilledWaterSys | [7 empty] | NO
HotWaterSys
ServiceHotWater
SteamSys
TwoPipe
FluidSystemUnmetCoolLoadHours | UnmetCoolLoadHours | decimal | h |  |  | The number of hours during the year when the space temperature is below the heating set point temperature or greater than the cooling set point temperature. UnmetLoadHours are used to determine if resizing is required. If greater than 300 there are rules for adjusting the baseline model to decrease the UnmetLoadHours | 2013 NR ACM 2.5 HVAC Capacity Requirements and Sizing; |  | User |  |  | NO
FluidSystemUnmetHeatLoadHours | UnmetHeatLoadHours | decimal | h |  |  | The number of hours during the year when the space temperature is below the heating set point temperature or greater than the cooling set point temperature. UnmetLoadHours are used to determine if resizing is required. If greater than 300 there are rules for adjusting the baseline model to decrease the UnmetLoadHours | 2013 NR ACM 2.5 HVAC Capacity Requirements and Sizing; |  | User |  |  | NO
HeatExchangerFluidDemandIn |  | reference | none | [5 empty] | User |  |  | NO
HeatExchangerFluidDemandOut |  | reference | none | [5 empty] | User |  |  | NO
HeatExchangerFluidSupplyn |  | reference | none | [5 empty] | User |  |  | NO
HeatExchangerFluidSupplyOut |  | reference | none | [5 empty] | User |  |  | NO
HeatExchangerType | Type | enumerated list | none | WaterEconomizer |  |  |  |  | User |  |  | NO
HeatRejectionCapfTempCurveCoefficient |  | decimal | none |  |  | Used in calculating the available cooling capacity of the CoolingTower heat rejection equipment. There are 6 HeatRejectinoCapCoefficient values required for the calculations. | 2013 NR ACM Table 78 Default Capacity Coefficients - Cooling Towers |  |  |  |  | NO
HeatRejectionCapRated |  | decimal | Btu per h |  |  | The rated cooling capacity at CTI test conditions. Units in MBH, 1000 Btu per hour | 2013 NR ACM 5.8.3 Cooling Towers Cooling Tower Capacity |  |  |  |  | NO
HeatRejectionCellCount | CellCount | decimal | none |  |  | The number of cells in the cooling tower. Each cell has its own fan, water flow allowing for responding to lower load conditions | 2013 NR ACM: 5.8.3 Cooling Towers Cooling Tower number of Cells; |  |  |  |  | NO
HeatRejectionDesignEnteringTemp | DesignEntTemp | decimal | F |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63 |  | User | 1. DR: Need to discuss how SDD and NACM will support design vs. rated conditions |  | NO
HeatRejectionDesignLeavingTemp | DesignLvgTemp | decimal | F |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63 |  | User | 1. DR: Need to discuss how SDD and NACM will support design vs. rated conditions |  | NO
HeatRejectionDesignWBTemp | DesignWBTemp | decimal | F | [6 empty] | 1. DR: Need to discuss how SDD and NACM will support design vs. rated conditions |  | NO
HeatRejectionFanType | FanType | enumerated list | none | Axial | [7 empty] | NO
Centrifugal
HeatRejectionFluidFlowIn |  | reference | none |  | FluidSegment |  |  |  | User |  |  | NO
HeatRejectionFluidFlowOut |  | reference | none |  | FluidSegment |  |  |  | User |  |  | NO
HeatRejectionModulationControl | ModCtrl | enumerated list | none | Bypass |  | Defines how the CoolingTower modulates capacity to respond to changing loads. Assignment of value depends on FanSystem and Fan attributes e.g. operation mode and Fan speed and pony motor attributes. | 2013 NR ACM: 5.8.3 Cooling Towers Cooling Tower Capacity Control |  |  |  |  | NO
Cycling
TwoSpeedFanCtrl
VarSpeedDrive
HeatRejectionTotalFanHP | TotalFanHP | decimal | hp |  |  | The sum of the nameplate rated horsepower (hp) of all fan motors on the cooling tower | 2013 NR ACM: 5.8.3 Cooling Towers CoolingTower Total Fan Power |  |  |  |  | NO
HeatRejectionType | Type | enumerated list | none | ClosedTower | [7 empty] | NO
GroundSourceHeatExchanger
Lake
OpenTower
Well
HVACSystemsCoolingOversizingRatio | CoolOversizingRatio | decimal | none |  |  | The percent that the baseline cooling equipment is oversized after sizing calculations are performed. Current value is 15% for cooling equipment. | 2013 NR ACM: 2.4 Calculation Procedures step 8. oversizing the baseline cooling equipment by 15%; |  | User | 1. DR: Need to clarify in NACM if this applies to only coils or also fans |  | NO
HVACSystemsHeatingOversizingRatio | HeatOversizingRatio | decimal | none |  |  | The percent that the baseline heating system equipment is oversized after sizing calculations are performed. Current value is 25% for heating. | 2013 NR ACM: 2.4 Calculation Procedures step 8. oversizing the baseline HeatingSystem by 25%; |  | User | 1. DR: Need to clarify in NACM if this applies to only coils or also fans |  | NO
HVACSystemsUnmetCoolLoadHours | UnmetCoolLoadHours | decimal | h | [5 empty] | User |  |  | NO
HVACSystemsUnmetHeatLoadHours | UnmetHeatLoadHours | decimal | h | [5 empty] | User |  |  | NO
HVACSystemsUnmetLoadHoursDeltaLimit | UnmetLoadHoursDeltaLimit | decimal | none |  |  | Calculated by subtracting baseline unmet load hours from proposed unmet load hours. | 2013 NR ACM 2.5 HVAC Capacity Requirements and Sizing; 2.5.2 Sizing Equipment in the Baseline Building |  | User |  |  | NO
HVACSystemsUnmetLoadHoursLimit | UnmetLoadHoursLimit | decimal | none |  |  | The maximum allowed unmet load hours per year which is 300 per year | 2013 NR ACM 2.5.2 Sizing Equipment in the Baseline Building |  | User |  |  | NO
Name |  | text | none |  |  | A text string that uniquely defines the HVAC object, and is used for referencing the object | [5 empty] | NO
OAControlEconoControlMethod | EconoControlMethod | enumerated list | none | DifferentialDryBulb | [7 empty] | NO
DifferentialEnthalpy
FixedDryBulb
FixedEnthalpy
NonIntegrated
OAControlEconoHighEnthalpyLockout | EconoHighEnthalpyLockout | decimal | Btu per lb |  |  | The outside air enthalpy above which the economizer will return to minimum position. This is used with fixed enthalpy or differential enthalpy economizers. | 2013 NR ACM 5.7.4.2 Air Side Economizers; Economizer Economizer High Enthalpy Lockout |  | User |  |  | NO
OAControlEconoHighTempLockout | EconoHighTempLockout | decimal | F |  |  | The outside air temperature above which the economizer will return to minimum position. This applies if ControlType is FixedDB | 2013 NR ACM 5.7.4.2 Air Side Economizers; Economizer High Temperature Lockout |  | User |  |  | NO
OAControlEconoLowTempLockout | EconoLowTempLockout | decimal | F |  |  | The outside air temperature below which the economizer will return to the minimum position. This appears to apply to all types of air-side economizers. | 2013 NR ACM 5.7.4.2 Air Side Economizers; Economizer Economizer Low Temperature Lockout |  | User |  |  | NO
OAControlOutsideAirRatio | OutsideAirRatio | decimal | none |  |  | The ratio of outside air to total system fan flow | [5 empty] | NO
OAControlReturnFlow | ReturnFlow | reference | none |  | AirSegment | [6 empty] | NO
OAControlSupplyFlow | SupplyFlow | reference | none |  | AirSegment | [6 empty] | NO
OAControlType | Type | enumerated list | none | Economizer | [5 empty] | 1. DR: Should be 'Fixed', not 'FixedEcono' |  | NO
FixedEcono
None
PreheatCoilType | Type | enumerated list | none | ElectricResistance | [7 empty] | NO
Furnace
HeatPump
HotWaterSys
WaterEconomizer
ProcessLoadEnergyLoad | EnergyLoad | decimal | Btu per h | [8 empty] | NO
ProcessLoadFlow | Flow | decimal | gal per min | [8 empty] | NO
ProcessLoadType | Type | enumerated list | none | Energy | [7 empty] | NO
Flow
PumpCount | Count | integer | none |  |  | The number of identical pumps serving equipment. Because all the features are the same in each unit, the Count can be used as a multiplier for calculating values like capacity of all the units | 2013 NR ACM: 5.8.5 Pumps Number of pumps |  |  |  |  | NO
PumpFlowCapacity | FlowCap | decimal | gal per min |  |  | The flow rate of fluid through the Pump in gallons per minute. | 2013 NR ACM 5.8.5 Pumps |  |  |  |  | NO
PumpFlowMin | FlowMin | decimal | gal per min |  |  | The lowest flow rate rated for a pump | 2008 NR ACM: Table N2-21 2013 ? |  |  |  |  | NO
PumpMinimumSpeed | MinSpeed | decimal | none | [8 empty] | NO
PumpMinimumSpeedRatio | MinSpeedRatio | decimal | none |  |  | The ratio of the lowest speed in a variable speed pump to the full load speed | 2013 NR ACM 5.8.5 Pumps Pump Minimum Speed |  | User |  |  | NO
PumpModelingMethod | ModelingMethod | decimal | none | PowerPerUnitFlow |  | Defines how the Pump is modeled. | 2013 NR ACM 5.8.5 Pumps Pump Motor Modeling Method |  |  |  |  | NO
PumpMotorBHP | MotorBHP | decimal | hp |  |  | The brake horsepower of the motor before the loss in power caused by the gearbox, alternator, differential, water pump, and other auxiliary components. | 2013 NR ACM 5.7.5 Cooling Systems Total Cooling Capacity equation 11; |  |  |  |  | NO
PumpMotorEfficiency | MotorEff | decimal | none |  |  | Indicates how well the motor converts electrical power into mechanical power and is defined as output power divided by input power expressed as a percentage . | 2013 NR ACM 5.8.5 Pumps Motor Efficiency |  |  |  |  | NO
PumpMotorHP | MotorHP | decimal | hp |  |  | The rated horsepower of the pump motor. | 2013 NR ACM 5.8.5 Pumps Motor Efficiency Table N2-20 Minimum Nominal Efficiency for Electric Motors (from 2008 NR ACM) |  |  |  |  | NO
PumpOperationControl | OperationCtrl | enumerated list | none |  |  | Defines how pump operation is controlled. Values: OnDemand, StandBy, Schedule | 2013 NR ACM 5.8.5 Pumps Pump Operation |  |  |  |  | NO
PumpPower | Power | decimal | kW |  |  | The power of the pump at FluidFlowCap | 2013 NR ACM 5.8.5 Pumps Equation 75 |  |  |  |  | NO
PumpPowerfPLRCurveCoefficient |  | decimal | none |  |  | The ratio of FluidFlowRate at part load to FluidFlowCap at full load | 2013 NR ACM 58.5 Pumps Part Load Power Curve Table 80 |  |  |  |  | NO
PumpPowerPerFlow | PowerPerFlow | decimal | W per gal per min |  |  | The power of the pump per unit flow at FluidFlowCap | 2013 NR ACM 5.8.5 Pumps Pump Motor Power-Per-Unit-Flow |  |  |  |  | NO
PumpSpeedControl | SpeedCtrl | enumerated list | none | ConstantSpeed | [7 empty] | NO
TwoSpeedFanCtrl
VariableSpeed
PumpType | Type | enumerated list | none | [8 empty] | NO
RefrigCondenserTempFactor |  | decimal | F |  |  | The number of degrees F to add to the design wet bulb or dry bulb temperatures to calculate the condensing temperature of the refrigerant in condensers in a RefrigerationSystem. | 2013 Title 24 Part 6 Section 120.6 (a) Mandatory Requirements for Refrigerated Warehouses 4. Condensers 2. Design saturated Condensing temperatures |  | User | DSP: This isn't in the 2013 NR ACM but I am still unclear how mandatory rules are going to be applied during compliance analysis. My understanding is equipment has to pass mandatory when performance compliance approval is sought. |  | NO
RefrigCondenserTempSaturated |  | decimal | F |  |  | The temperature at which the air cooling the condenser is saturated. This is evaluated in mandatory measures for condensers used in refrigeration equipment. | 2013 Title 24 Part 6 Section 120.6 (a) Mandatory Requirements for Refrigerated Warehouses 4. Condensers 2. Design saturated Condensing temperatures |  | User | DSP: Mandatory requirement. Do we need it for the SDD? |  | NO
RefrigCondenserTempSetpointMin |  | decimal | F |  |  | Minimum condensing temperature setpoint for Condensers in refrigerated warehouses, and used to control the speed of all condenser fans | 2013 Title 24 Part 6 Section 120.6 (a) Mandatory Requirements for Refrigerated Warehouses 4. Condensers C and D |  | User | DSP: Mandatory requirement Do we need it for the SDD? |  | NO
RefrigCondenserTotalHeatOfRejection |  | decimal | Btu per h |  |  | A measure of the capacity of a refrigeration condenser in Btu per hour. Often expressed in MBH or 1000 BTU per hour, the total heat of rejection is used to calculate mandatory minimum efficiency of some types of fan-powered condensers used in refrigeration systems | 2013 Title 24 Part 6 Section 120.6 (a) Mandatory Requirements for Refrigerated Warehouses Table Fan-Powered Condensers Minimum Efficiency Requirements |  | User | DSP: Mandatory requirement Do we need it for the SDD? |  | NO
RefrigEquipCOP | COP | decimal | none |  |  | The efficiency of the refrigeration equipment expressed as the ARI rated coefficient of performance | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment |  | User;#Rule |  |  | NO
RefrigEquipFloorArea |  | decimal | ft2 |  |  | The measure of floor space in a walk-in cooler or freezer. It is used to assign default Power | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Table 24 Default Power for Walk-in Refirgerators and Freezers |  | User |  |  | NO
RefrigEquipGlassDoorCount |  | integer | none |  |  | The number of glass display doors in the RefrigerationEquipment | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Equation 6 |  | User |  |  | NO
RefrigEquipGlassDoorPower |  | decimal | W |  |  | The power associated with a glass display door for a walk-in refrigerator or freezer |  |  | User |  |  | NO
RefrigEquipPowerPerUnitArea |  | decimal | W per ft2 |  |  | The measure of power per square foot of space in a walk-in cooler or freezer | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Table 24 Default Power for Walk-in Refirgerators and Freezers |  | User |  |  | NO
RefrigEquipType |  | enumerated list | none | Casework |  |  | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment |  | User |  |  | NO
WalkInCooler
WalkInFreezer
RefrigRemoteCondenserFraction |  | decimal | none |  |  | The fraction of condenser heat that is rejected to the outdoors. For self-contained refrigeration casework, this value will be zero. For remote condenser systems, this value is 1.0. For combination systems, the value should be weighted according refrigeration capacity. | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Remote Condenser Fraction |  | User |  |  | NO
RefrigRemoteCondenserHeatRemovalRate |  | decimal | Btu per h |  |  | The rate of heat removal from the space due to the continuous operation of the refrigeration system (kBtu/h). A negative number means that heat is being removed from the space; a positive number means that heat is being added. | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Remote Condenser Fraction |  | User | DSP: With condensers in refrigeration equipment, do we treat them as a different animal than other condensers, which are just a property of Coil? Also this term name which is what is used in the NR ACM is a bit misleading as a positive value means heat is added. Should we change it? |  | NO
Service |  | reference | none |  | AirSegment | [6 empty] | NO
AirSystem
Boiler
Chiller
FluidSegment
FluidSystem
HeatRejection
TerminalUnit
Status |  | enumerated list | none |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. | [5 empty] | NO
StorageTankCapacity | Capacity | decimal | gal | [8 empty] | NO
StorageTankFluidFlowIn | FluidFlowIn | reference | none |  | FluidSegment |  |  |  | User |  |  | NO
StorageTankFluidFlowOut | FluidFlowOut | reference | none |  | FluidSegment |  |  |  | User |  |  | NO
StorageTankRValue | RValue | decimal | h ft2 F per Btu |  |  | Performance of unfired storage tank insulation. | [5 empty] | NO
TerminalUnitHotDuctAirSegment | HotDuctFlowSegment | reference | none |  | AirSegment | Name of heating AirFlowSegment for DualDuct systems | [5 empty] | NO
TerminalUnitInducedAirZone | InducedAirZone | reference | none |  | ThermalZone | The Name of ThermalZone that air is induced from | [5 empty] | NO
TerminalUnitInductionRatio | InductionRatio | decimal | none |  |  | The fraction of induced air, divided by AirFlowPrimary | [5 empty] | NO
TerminalUnitParallelBoxTStatSetpoint | ParallelBoxTStatSetpoint | decimal | F |  |  | The temperature setpoint at which fan in a FanPoweredParallel VAV box should turn on, and is usually a couple of degrees higher than the heating setpoint | 2013 NR ACM 5.6.2 Terminal Device Data Terminal Type 5.6.5.2 Fan Powered Boxes Parallel Fan Box Thermostat Setpoint |  | User | 1. DR: I believe this should be a temperature schedule |  | NO
TerminalUnitPrimaryAirFlow | AirFlowPrimary | decimal | ft3 per min |  |  | Primary air flow in CFM, or AutoSize |  | For Object = TerminalUnit only |  | 1. DR: Confirm E+ supports autosizing of terminal unit air flows. Do we want to allow auto-size of proposed terminal units? DSP: in XSD could call this optional and then it would be blank and autosize would happen. DSP: Evap coolers also have an airflow primary property which I added. Maybe we should prefix the term with TerminalUnit |  | NO
TerminalUnitPrimaryAirSegment | PrimaryFlowSegment | reference | none |  | AirSegment | Name of primary AirFlowSegment, or cooling AirFlowSegment for DualDuct systems | [5 empty] | NO
TerminalUnitType | Type | enumerated list | none | CVReheat | [7 empty] | NO
ParallelFanBox
SeriesFanBox
Uncontrolled
VAVNoReheat
VAVReheat
TerminalUnitZoneServed | ZoneServed | reference | none |  | ThermalZone | [6 empty] | NO
ThermalZoneCoolingSystem | CoolingSystem | reference | none |  | AirSystem | [6 empty] | NO
ThermalZoneCoolingTStatSchedule | CoolTStatSch | reference | none | [5 empty] | User |  |  | NO
ThermalZoneDescription | Description | text | none | [5 empty] | User |  |  | NO
ThermalZoneExhaustSystem |  | reference | none |  | AirSegment |  |  |  |  | 1. DR: Need to revisit how exhaust fan/systems will be described in SDD. Currently, described as a separate 'AirSystem', but this may not be appropriate for zone exhaust fans. |  | NO
ThermalZoneHeatingSystem | HeatingSystem | reference | none |  | AirSystem | [6 empty] | NO
ThermalZoneHeatingTStatSchedule | HeatTStatSch | reference | none | [5 empty] | User |  |  | NO
ThermalZoneSupplementalCoolingSystem | SuppCoolingSystem | reference | none |  | AirSystem | [6 empty] | NO
ThermalZoneSupplementalHeatingSystem | SuppHeatingSystem | reference | none |  | AirSystem |  |  |  | User |  |  | NO
ThermalZoneThrottlingRange | ThrottlingRange | reference | none | [5 empty] | User |  |  | NO
ThermalZoneType | Type | enumerated list | none | Conditioned |  | Defines the type of conditioning in the thermal zone |  |  | User |  |  | NO
PlenumZones
Unconditioned
ThermalZoneVentControlMethod | VentCtrlMethod | enumerated list | none | CO2Sensors |  | The method used to determine outside air ventilation needed for each hour in the simulation | 2013 NR ACM 5.6.5.4 Outdoor Air Ventilation Ventilation Control Method |  | User |  |  | NO
FixedVentCtrl
OccupantSensors
ThermalZoneVentilationSystem | VentilationSystem | reference | none |  | AirSystem |  |  |  | User |  |  | NO
ThermalZoneVentRateDesign | VentRateDesign | decimal | ft3 per min |  |  | The quantity of ventilation air that is provided to the space at maximum occupancy. | 2013 NR ACM 5.6.5.4 Outdoor Air Ventilation Design Ventilation Rate |  | User | 1. DR: Need to decide if this is a property of Space, ThermalZone, or possiblly both 2. DR: Need to add a cfm/ft2 and cfm/person property as well |  | NO
ThermalZoneVentRateMin | VentRateMin | decimal | ft3 per min |  |  | The minimum quantity of ventilation air that must provided to the space when it is occupied | 2013 NR ACM 5.6.5.4 Outdoor Air Ventilation Minimum Ventilation Rate |  | User | 1. DR: Need to decide if this is a property of Space, ThermalZone, or possiblly both 2. DR: Need to add a cfm/ft2 property as well |  | NO
ThrottlingRangeLowerTemp |  | decimal | F |  |  | The lowest temperature in the throttling range within which the HVAC system is neither calling for heating or cooling. | 2013 NR ACM: 5.6.1 Space Temperature Control Space Thermostat Throttling Range |  | User |  |  | NO
ThrottlingRangeUpperTemp |  | decimal | F |  |  | The higest temperature in the throttling range within which the HVAC system is neither calling for heating or cooling. | 2013 NR ACM: 5.6.1 Space Temperature Control Space Thermostat Throttling Range |  | User |  |  | NO
WaterHeaterEnergyFactor | EF | decimal | none |  |  | The ratio of the energy delivered by the water heater divided by the energy used, in the same units. | 2013 NR ACM 5.9.1.2 Water Heaters Energy Factor |  |  |  |  | NO
WaterHeaterFIRfPLRCurveCoefficent |  | decimal | none |  |  | Used in calculating the part load curve for the water heater. There are three coefficient values required for the calculations | 2013 NR ACM 5.9.1.2 Water Heaters Fuel Water Heater Part Load Efficiency Curve equation 76 |  |  |  |  | NO
WaterHeaterFluidFlowIn | FluidFlowIn | reference | none |  | FluidSegment |  |  |  | User |  |  | NO
WaterHeaterFluidFlowOut | FluidFlowOut | reference | none |  | FluidSegment |  |  |  | User |  |  | NO
WaterHeaterMakeUp | MakeUp | reference | none | [5 empty] | User |  |  | NO
WaterHeaterStandByLoss | StandByLoss | decimal | Btu per h | [8 empty] | NO
WaterHeaterStorageCapacity | StorageCapacity | decimal | gal | [5 empty] | User |  |  | NO
WaterHeaterThermalEff | ThermalEff | decimal | none | [5 empty] | User | 1. DR: Need to decide if efficiencies are described as a ratio or decimal |  | NO
WaterHeaterType | Type | enumerated list | none | [8 empty] | NO

## HvacEnumerations
| Term | Property | Definition | Term Short Form
AirSegmentPath
| Direct | AirSegmentPath
| Ducted | AirSegmentPath
| PlenumZones | AirSegmentPath
AirSegmentSource
| AirSystem | AirSegmentSource
| OutdoorAir | AirSegmentSource
| ZoneAir | AirSegmentSource
AirSegmentType
| DualDuctSplitter | AirSegmentType
| ExhaustSegment | AirSegmentType
| MakeupAir | AirSegmentType |  | Makeup
| Relief | AirSegmentType
| Return | AirSegmentType
| Supply | AirSegmentType
AirSystemCoolControl
| ColdestReset | AirSystemCoolControl
| FixedAirCool | AirSystemCoolControl |  | Fixed
| OAResetAirCool | AirSystemCoolControl |  | OAReset
| ScheduledAirCool | AirSystemCoolControl |  | Scheduled
AirSystemHeatControl
| FixedAirHeat | AirSystemHeatControl |  | Fixed
| OAResetAirHeat | AirSystemHeatControl |  | OAReset
| ScheduledAirHeat | AirSystemHeatControl |  | Scheduled
| WarmestReset | AirSystemHeatControl
AirSystemType
| BuiltUp | AirSystemType
| ExhaustSystem | AirSystemType
| Unitary | AirSystemType
AirSystemVentilationControl
| AverageFlow | AirSystemVentilationControl
| CriticalZone | AirSystemVentilationControl
| FixedAirVent | AirSystemVentilationControl
| FixedVentCtrl | AirSystemVentilationControl |  | Fixed
BoilerDraftType
| Atmospheric | BoilerDraftType
| MechanicalForced | BoilerDraftType
| MechanicalInduced | BoilerDraftType
BoilerFuel
| HotWaterFuel | BoilerFuel |  | HotWater
| NaturalGasBoiler | BoilerFuel
| Oil | BoilerFuel
| SteamFuel | BoilerFuel
BoilerFuel; ChillerFuel
| ElectricChiller | BoilerFuel; ChillerFuel
BoilerFuel; CoilHeatingHpDefrostHeatSource
| Electric | BoilerFuel; CoilHeatingHpDefrostHeatSource
BoilerType
| HotWater | BoilerType
| HotWaterBoiler | BoilerType
| Steam | BoilerType
ChillerFuel
| NaturalGasChiller | ChillerFuel
ChillerType
| Adsorption | ChillerType
| Centrifugal | ChillerType
| DoubleEffectAbsorption | ChillerType
| HeatPump | ChillerType
| HeatRecovery | ChillerType
| Reciprocating | ChillerType
| Screw | ChillerType
| Scroll | ChillerType
| SingleEffectAbsorption | ChillerType
| TripleEffectAbsorption | ChillerType
CoilCondenserFlowType
| CondenserFixedFlow | CoilCondenserFlowType |  | Fixed
| CondenserTwoPositionFlow | CoilCondenserFlowType |  | TwoPositionFlow
| CondenserVariableFlow | CoilCondenserFlowType |  | VariableFlow
CoilCondenserType
| Air | CoilCondenserType
| Fluid | CoilCondenserType
CoilCoolingFuelSource
| ElectricCooling | CoilCoolingFuelSource
| NaturalGasCooling | CoilCoolingFuelSource
CoilCoolingType
| ChilledWater | CoilCoolingType
| DirectExpansion | CoilCoolingType
| WaterEconomizer | CoilCoolingType |  | WaterEconomizer
CoilCoolingWaterEconoType
| ParallelHX | CoilCoolingWaterEconoType
| SeriesHX | CoilCoolingWaterEconoType
| StrainerCycle | CoilCoolingWaterEconoType
| ThermoCycle | CoilCoolingWaterEconoType
CoilHeatingFuelSource
| ElectricHeating | CoilHeatingFuelSource
| NaturalGas | CoilHeatingFuelSource
CoilHeatingFurnaceIgnitionType
| IntermittentIgnitionDevice | CoilHeatingFurnaceIgnitionType |  | IID
| PilotLight | CoilHeatingFurnaceIgnitionType
CoilHeatingHpDefrostControl
| OnDemand | CoilHeatingHpDefrostControl
| TimedCycle | CoilHeatingHpDefrostControl
CoilHeatingHpDefrostHeatSource
| HotGas | CoilHeatingHpDefrostHeatSource
CoilHeatingType
| ElectricResistance | CoilHeatingType
| Furnace | CoilHeatingType
| HeatPumpCoil | CoilHeatingType |  | HeatPump
| HotWaterCoil | CoilHeatingType |  | HotWater
EnergyRecoveryType
| CrossFlow | EnergyRecoveryType
| RunAroundLoop | EnergyRecoveryType
| Wheel | EnergyRecoveryType
EvapCoolerType
| IntegratedDirectIndirect | EvapCoolerType
| IntegratedIndirect | EvapCoolerType
| NonIntegratedDirectIndirect | EvapCoolerType
| NonIntegratedIndirect | EvapCoolerType
FanAxialType
| Vane | FanAxialType
| VaneVariablePitchBlades | FanAxialType
FanCentrifugalType
| AirFoil | FanCentrifugalType
| AirFoilInletVanes | FanCentrifugalType
| BackwardInclined | FanCentrifugalType
| BackwardInclinedInletVanes | FanCentrifugalType
| ForwardCurved | FanCentrifugalType
| ForwardCurvedInletVanes | FanCentrifugalType
FanControlMethod
| ConstantVolume | FanControlMethod
| Dampers | FanControlMethod
| InletVanes | FanControlMethod
| TwoSpeedFanCtrl | FanControlMethod |  | TwoSpeed
| VarPitch | FanControlMethod
| VarSpeedDrive | FanControlMethod |  | VarSpeedDrive
FanModelingMethod
| BrakeHorsePower | FanModelingMethod
| PowerPerUnitFlow | FanModelingMethod
| StaticPressure | FanModelingMethod
FanMotorPosition
| InAirStream | FanMotorPosition
| NotInAirStream | FanMotorPosition
FanMotorType
| Enclosed | FanMotorType
| Open | FanMotorType
FluidSegmentSource
| FluidSystem | FluidSegmentSource
| MunicipalWater | FluidSegmentSource
| WellWater | FluidSegmentSource
FluidSegmentType
| Discharge | FluidSegmentType
| LoadReset | FluidSegmentType
| MakeupFluid | FluidSegmentType |  | Makeup
| PrimaryReturn | FluidSegmentType
| PrimarySupply | FluidSegmentType
| SecondaryReturn | FluidSegmentType
| SecondarySupply | FluidSegmentType
FluidSystemCoolControl
| FixedFluidCool | FluidSystemCoolControl |  | Fixed
| LoadResetCoolCtrl | FluidSystemCoolControl |  | LoadReset
| OAResetFluidCool | FluidSystemCoolControl |  | OAReset
| ScheduledFluidCool | FluidSystemCoolControl |  | Scheduled
FluidSystemHeatControl
| FixedFluidHeat | FluidSystemHeatControl |  | Fixed
| OAResetFluidHeat | FluidSystemHeatControl |  | OAReset
| ScheduledFluidHeat | FluidSystemHeatControl |  | Scheduled
FluidSystemType
| ChilledWaterSys | FluidSystemType |  | ChilledWater
| CondenserWater | FluidSystemType
| HotWaterSys | FluidSystemType |  | HotWater
| ServiceHotWater | FluidSystemType
| SteamSys | FluidSystemType
| TwoPipe | FluidSystemType
HeatExchangerType
| WaterEconomizerHX | HeatExchangerType |  | WaterEconomizer
HeatRejectionFanType
| Axial | HeatRejectionFanType
| CentrifugalFan | HeatRejectionFanType
HeatRejectionModulationControl
| Bypass | HeatRejectionModulationControl
| Cycling | HeatRejectionModulationControl
| TwoSpeed | HeatRejectionModulationControl
| VarSpeedDriveFanCtl | HeatRejectionModulationControl |  | VarSpeedDrive
HeatRejectionType
| ClosedTower | HeatRejectionType
| GroundSourceHeatExchanger | HeatRejectionType
| Lake | HeatRejectionType
| OpenTower | HeatRejectionType
| Well | HeatRejectionType
OAControlEconoControlMethod
| DifferentialDryBulb | OAControlEconoControlMethod
| DifferentialEnthalpy | OAControlEconoControlMethod
| FixedDryBulb | OAControlEconoControlMethod
| FixedEnthalpy | OAControlEconoControlMethod
| NonIntegrated | OAControlEconoControlMethod
OAControlType
| Economizer | OAControlType
| FixedEcono | OAControlType
| None | OAControlType
PreheatCoilType
| ElectricResistancePreheat | PreheatCoilType |  | ElectricResistance
| FurnacePreheat | PreheatCoilType |  | Furnace
| HeatPumpPreheat | PreheatCoilType |  | HeatPump
| HotWaterPreheat | PreheatCoilType |  | HotWater
| WaterEconomizerPreheat | PreheatCoilType |  | WaterEconomizer
ProcessLoadType
| Energy | ProcessLoadType
| Flow | ProcessLoadType
PumpSpeedControl
| ConstantSpeed | PumpSpeedControl
| TwoSpeedPumpCtrl | PumpSpeedControl |  | TwoSpeed
| VariableSpeed | PumpSpeedControl
RefrigEquipType
| Casework | RefrigEquipType
| WalkInCooler | RefrigEquipType
| WalkInFreezer | RefrigEquipType
TerminalUnitType
| CVReheat | TerminalUnitType
| ParallelFanBox | TerminalUnitType
| SeriesFanBox | TerminalUnitType
| Uncontrolled | TerminalUnitType
| VAVNoReheat | TerminalUnitType
| VAVReheat | TerminalUnitType
ThermalZoneType
| Conditioned | ThermalZoneType
| Plenum | ThermalZoneType
| Unconditioned | ThermalZoneType
ThermalZoneVentControlMethod
| CO2Sensors | ThermalZoneVentControlMethod
| FixedVentilation | ThermalZoneVentControlMethod
| OccupantSensors | ThermalZoneVentControlMethod
(no property)
AFUE
Boiler
CombustionEfficiency
DCV
ServiceWaterHeating
Storage
ThermalEfficiency
Ventilation

## LightingObjects
Term | Term Short Form | SDD Building Parent | SDD Parent | Properties | Referenced Objects | ObjectType | Array Count | ArrayObject | ArrayProperty | Definition | Standards Reference | Constraints | Set By | Issues | Resolutions | Collapsed From
IndoorLightingSystem | IndoorLtgSys | Building |  | ComplianceApproach |  | Heterogeneous |  |  |  | Container for Building level Lighting System properties
ComplianceApproval
LightingPowerBudget
LightingPowerProposed
LightingPrescriptiveMethod
IndoorLightingArea | IndoorLtgArea | OccupancyArea |  | Area |  | Heterogeneous | varies |  |  | Container for space occupancy area properties related to indoor lighting system
FixedLightingPowerProposed
IESNAIlluminanceCategory
LightingAlterationType
LightingPowerBudget
LightingPowerProposed
PortableLightingPowerProposed
PrimaryFunction
RoomCavityRatio
LightingControls | LtgCtrls |  | IndoorLightingArea | LightingControlDevice |  | Heterogeneous | varies |  |  | One or more controls to be installed in an indoor lighting area. Each type of control has characteristics that are tracked. | 2008 Title 24: Section 119 Mandatory Requirements For Lighting Control Devices, Ballasts, And Luminaires; Section 130 Lighting Controls And Equipment General, Section 131 - Indoor Lighting Controls That Shall Be Installed; Table 146-C Lighting Power Adjustment Factors; 2008 NR ACM Tables N2-8 through N2-12 Occupancy Schedules 2013 Title 24: Section 110.9
LightingControlScheme
PowerAdjustmentFactor
LightingAllowance | LtgAllowance |  | IndoorLightingArea | LightingAllowanceAmount |  | Heterogeneous | varies |  |  | Type and amount of reduction allowed in calculating indoor lighting power density. |  |  | User
LightingAllowanceType
MountingHeightMultiplier
LightingFixture | LtgFixture |  | IndoorLightingArea | AreaCategoryFixtureType |  | Heterogeneous | varies |  |  | Component-based unit comprising fixtures in a lighting system. |  |  | User
BallastEfficiency
BallastPower
BallastRemote
Dimmable
FixturePowerBudget
FixturePowerProposed
HighEfficiencyLEDSystem
Portable
RelativeSystemEfficiency
TailoredFixtureType

## LightingProperties
Term | Term Short Form | DataType | Units | Enumerations | Definition | Standards Reference | Constraints | Set By | Issues | Resolutions
Area | Area | decimal | ft2 |  | Floor area of the indoor lighting area including any daylit areas | 2008 Title 24: Section 146 Prescriptive Requirements For Indoor Lighting For the "Area Category Method", area "all contiguous spaces which accommodate or are associated with a single one of the primary functions listed in TABLE 146-FC . Where areas are bounded or separated by interior partitions, the floor space occupied by those interior partitions shall be included in any area. 2013 Draft Title 24: Section 140.6. Table 140.6-C.
AreaCategoryAllowance | AreaCatAllow | decimal | W per ft2 |  | Total lighting power density reduction for all area category method allowances
AreaCategoryFixtureType | AreaFixtureType | enumerated list | none | OrnamentalFixture | Enumeration type for Area Category method |  |  | User
PrecisionWorkFixture
SchoolLabTaskFixture
SpecializedTaskFixture
BallastEfficiency | BallastEff | decimal | none |  | Efficiency of the ballast, may be expressed as ballast efficacy factor (BFF). | 2008 Title 24: Section 130 Lighting Controls And Equipment-General (d) Luminaire power. Section 146 Prescriptive Requirements For Indoor Lighting Table 146 D. 2013 Title 24: Section 130.0.c |  | User
BallastPower | BallastPow | decimal | W |  | Rated wattage used by the ballast. | 2008 Title 24: Section 130 Lighting Controls And Equipment-General (d) Luminaire power. 2013 Title 24: Section 130.0.c |  | User
BallastRemote | BallastRemote | boolean | none |  | Identifies whether the ballast is remote (true) from the lighting fixture or a permanent part of the fixture (false). | 2008 Title 24: Section 130 Lighting Controls And Equipment-General (d) Luminaire power. 2013 Title 24: Section 130.0.c |  | User
ComplianceApproach | ComplianceApproach | enumerated list | none | Performance | Prescriptive or performance lighting compliance approach
Prescriptive
ComplianceApproval | ComplianceApproval | boolean | none |  | Lighting compliance approval status: pass/fail
Dimmable | Dimmable | boolean | none |  | If true allows the application of power adjustment factor. | 2008 Title 24: Section 146 Prescriptive Requirements For Indoor Lighting Table 146 C 2013 Draft Title 24: Section 140.6 |  | User
FixedLightingPowerProposed | FixedLtgPowerProposed | decimal | W |  | The sum of all proposed lighting power to fixtures that are permanent. All power from permanent physically fixed fixtures is added to the calculation of proposed lighting power. | 2008 Title 24: Section 146 EXCEPTION to Section 146(a). 2013 Draft Title 24:Section 140.6 (a)
FixturePowerBudget | FixturePowBudget | decimal | W |  | Allowed wattage depending on characteristics of the lighting fixture. | 2008 Title 24: Section 130 (d) Luminaire power. 2013 Title 24: Section 130.0.c |  | User
FixturePowerProposed | FixturePowProp | decimal | W |  | The product rated wattage for the proposed lighting fixture | 2008 Title 24: Section 130 (d) Luminaire power. 2013 Title 24: Section 130.0.c |  | User
HighEfficiencyLEDSystem | HighEffLED | boolean | none |  | A high efficacy LED luminaire, or LED light engine with integral heat sink that meets minimum efficacy requirements | 2008 Title 24: section 119 mandatory requirements for lighting control devices, ballasts, and luminaires. 2013 Title 24: Section 110.9 |  | User
IESNAIlluminanceCategory | IESNAIllCat | enumerated list | none | A | COMNET does not include this kind of detail. One of seven categories developed by Illuminating Engineering Society of North America (IESNA) to establish recommended levels of light for various tasks in the lighting area. Used in the Tailored method, categories range from A which is 3 foot candles or 30 lux for public spaces to G which covers 300 to 1000 foot candles (3,000 - 10,000 lux) for areas where visual acuity is critical e.g. a medical surgery room | T24, Related: "IESNA LIGHTING HANDBOOK is the Illuminating Engineering Society National Association document entitled “The IESNA Lighting Handbook: Reference and Applications, Ninth Edition” (2000)." T24, Related: "If a specific IESNA Illuminance Category is listed in Column 2 of TABLE 146-G, then such illuminance Category shall be used. Otherwise, determine the illuminance category for each lighting primary function type according to categories specified in the IESNA Lighting Handbook (IESNA HB), using the “Design Guide” for illuminance. Tasks that are performed less than 2 hours a day or poor quality tasks that can be improved shall not be employed to justify use of Illuminance Categories E, F, or G."
B
C
D
E
F
LightingAllowanceAmount | LtgAllowAmt | decimal | W per ft2 |  | Amount of lighting allowance used in calculating allowed indoor lighting power density in lighting areas. |  |  | User
LightingAllowanceType | LtgAllowType | enumerated list | none | AreaOrnamentalAllowance | Type of lighting allowance used in calculating allowed indoor lighting power density in lighting areas. |  |  | User
AreaPrecisionWorkAllowance
AreaSchoolLabTaskAllowance
AreaSpecializedTaskAllowance
OfficePortableAllowance
TailoredDisplayCaseAllowance
TailoredFloorDisplayAllowance
TailoredGeneralLightingAllowance
TailoredOrnamentalAllowance
TailoredSpecialEffectAllowance
TailoredWallDisplayAllowance
LightingAlterationType | LtgAltType | enumerated list | none | LightingAlterationArea | Alteration type for a lighting area that qualifies the calculation of lighting power allowances. | 2008 Title 24: Section149(b) 2013 Draft Title 24: Section 141.0.B |  | User
LightingAlterationCrossingLPDThresholdArea
LightingSubdividedArea
LightingWiringAlterationArea
LightingControlDevice | LtgCtrlDevice | enumerated list | none | AutomaticMultiLevelDaylightingControl | Type of lighting control device used in calculating allowed lighting power. |  |  | User
Dimmer
InterlockSwitch
ManualOnOccupancy
MultiLevelAstronomicalTimeSwitch
MultiLevelLightingControl
MultiLevelOccupancyControl
OutdoorAstronomicalTimeSwitch
OverrideSwitch
SwitchingOrControlDevice
SystemDRControl
SystemShutOff
LightingControlScheme | LtgCtrlScheme | enumerated list | none | AreaControl | Type of lighting control scheme used in calculating allowed lighting power. |  |  | User
AstronomicalTimeSwitch
AutomaticDaylighting
AutomaticShutoff
AutomaticTimeClock
DemandResponsive
Dimming
MultiLevelLighting
MultiLevelOccupancy
MultipleInterlockedLighting
MultiSceneProgrammable
Vacancy
LightingPower | LtgPower | decimal | W |  | Maximum amount of power drawn by a lighting system.
LightingPowerBudget | LtgPowerBudget | decimal | W |  | The allowed lighting power density times the floor area of an indoor lighting area, dependent on the primary function of the lighting area and the prescriptive method. | 2008 NR ACM: 2.4.2 Lighting Power 2.4.2.2 Indoor Lighting 2008 Title 24: Table 146 E-F - Lighting Power Density Values 2013 Title 24: Section 140.6. Table 140.6-B, Table 140.6-C
LightingPowerDensity | LtgPowerDensity | decimal | W per ft2 |  | LightingPowerDensity is the maximum amount of power drawn by a building or zone's lighting systems, divided by that building or zone's floor area. | When the user indicates with that lighting compliance will be performed and lighting plans will be submitted for the entire building (excluding the residential units of high-rise residential buildings and hotel/motel guest rooms), the compliance software shall require the user to select and input the occupancy type(s) from Table N2-5 or Table N2-6 and enter the proposed interior lighting equipment or interior lighting power density (LPD) for each space that is modeled. Proposed design use-it-or-loose-it lighting power shall be entered separately from the general lighting. However, if lighting plans will be submitted only for portions of the building, the compliance software shall require the user to select and input the occupancy type(s) from Table N2-6 and enter the actual lighting levels for portions of the building with lighting plans.
LightingPowerProposed | LtgPowerProposed | decimal | W |  | Total proposed wattage of all lighting fixtures and controls in a lighting area, less adjustments for any qualifying automatic lighting controls, such as occupant-sensing devices or automatic daylighting controls. Also, , total proposed wattage for all indoor lighting areas served by a lighting system, | 2008 Title 24: Table 146-C Lighting Power Adjustment Factors; 2008 NR ACM: 2.4.2.2 Indoor Lighting 2013 Title 24: Table removed
LightingPrescriptiveMethod | LtgPrescripMeth | enumerated list | none | AreaCategory | Prescriptive compliance approach for lighting systems
CompleteBuilding
Tailored
LightingType | LtgType | enumerated list | none | Decorative | COMNET lists several different types of lighting power. To more easily support multiple ways to specify each of those (primarily lighting power and lighting power density), the types of lighting of interest to CEC and standards more generally are being broken away into this enumeration. All values except Regulated Exterior were taken directly from the COMNET building descriptors. | Enumeration of types of lighting found in a building.
Indoor Lighting
Non-Regulated Interior
Outdoor Lighting
Regulated Exterior
Regulated Interior
VDT Viewing
MountingHeightMultiplier | MountHgtMult | decimal | none |  | An adjustment to the Wall Display allowance and the Floor Display allowance in the Tailored Method, based on the mounting height of the fixtures. | 2008 Title 24 Section 146(c)3B and Table 146-H 2013 Title 24: Section 140.6.C.3.B; Table 140.6-E |  | User
Portable | Portable | boolean | none |  | Is (true), or is not (false) a portable lighting fixture. | 2008 Title 24: Section 146 Prescriptive Requirements for Indoor Lighting. 2013 Title 24: Section 140.6. |  | User
PortableLightingPowerProposed | PortLtgPowerProposed | decimal | W |  | The sum of all proposed lighting power to fixtures that are portable. There is an exception that allows the deduction of up to 0.2 watts per square foot of portable lighting in office spaces. | 2008 Title 24: Section 146 EXCEPTION to Section 146(a). 2013 Draft Title 24:Section 140.6 (a)
PowerAdjustmentFactor | PAF | decimal | none |  | The fraction that may be subtracted from the total controlled lighting wattage to simulate energy savings resulting from control devices such as occupancy sensor controls that turn lights off when no one is in the space. | Title 24: There is no definition of PAF however Section 146(a)2 explains how it is used: The controlled watts of any luminaire may be reduced by the number of controlled watts times the applicable Power Adjustment Factor (PAF) from TABLE 146-C NR ACM:
PrimaryFunction | PrimaryFunc | enumerated list | none |  | Main activity type in the indoor lighting area. The enumerated list is different for prescriptive methods, Area and Tailored for establishing allowed lighting power DSP: Need to link this to OccSpace and OccAncillary lists | 2008 Title 24: Section 146 (c) Calculation of Allowed Title 23: Indoor Lighting Power Density 2. Area Category Method; Table 146-F Area Category Method - Lighting Power Density Values and Table 146-G Tailored Method Special Lighting Power Allowances 2008 NR ACM: Table N2-6 Area Occupancy Assumptions 2013 Draft Title 24: Section 140.6. Table 140.6-C. Table 140.6-D
RelativeSystemEfficiency | RSE | decimal | none |  | Calculated for dimmable electronic ballasts using with T5 & T8 fluorescent lights to calculate applicable power adjustment factor. | 2008 Title 24; Table 146-D Relative System Efficiency (RSE) For Dimmable Electronic Ballasts Used To Qualify For Power Adjustment Factor 2013 Title 24: Section 140.6. Table 140.6-A. |  | User
RoomCavityRatio | RCR | decimal | none |  | Required if using the Tailored method, which defines the configuration of space using task lighting. Used in Table 146 I to establish LightingPowerDensity based on IlluminanceCategory. Calculated using the length and width of the indoor lighting area and the vertical distance from the work plane to the centerline of the lighting fixture. | 2008 Title 24: Equation 146- G Room Cavity Ratio For Rectangular Rooms; NR ACM: calculation for light wells or other skylights: minimal mention - used for well cavity ratio. 2013 Draft Title 24:Section 140.6. Table 140.6-D
TailoredFixtureType | TailoredFixtureType | enumerated list | none | FloorDisplayFixture | Enumeration type for Tailored method |  |  | User
OrnamentalSpecialEffectFixture
VeryValuableDisplayFixture
WallDisplayFixture

## LightingEnumerations
Term | Property | Definition
AreaCategory |  | Allowed lighting power for a building is the sum of the allowed lighting power for all "areas" in the building based on LPDs in Table 146-F
AreaOrnamentalAllowance |  | Area Category Method allowance for task area ornamental chandeliers and sconces.
AreaPrecisionWorkAllowance |  | Area Category Method allowance for task area required for precision work.
AreaSchoolLabTaskAllowance |  | Area Category Method for task area in science laboratories in schools.
AreaSpecializedTaskAllowance |  | Area Category Method allowance for task space required for art, craft assembly or manufacturing operation work.
Atrium: Floors 1-3
Atrium: Floors 4+
CompleteBuilding |  | To be used only for buildings with only one type of use occupancy, or where one type of use occupancy makes up 90% of the area. Shall not be used for retail and wholesale stores, hotel/motel, and high-rise residential buildings
Decorative
FloorDisplayFixture |  | Floor display light fixture
Indoor Lighting
LightingAlterationArea |  | A lighting area in which the lighting load is increased during an alteration, or in which 50 percent or more of the luminaires are replaced during an alteration project.
LightingAlterationCrossingLPDThresholdArea |  | An existing lighting area in which the lighting power density is increased beyond a defined threshold.
LightingSubdividedArea |  | An existing lighting area that is subdivided into two or more areas during an alteration project
LightingWiringAlterationArea |  | An existing lighting area in which certain wiring alterations are made
Non-Regulated Interior
OfficePortableAllowance |  | Allowance for portable lighting in office areas.
OrnamentalFixture |  | Ornamental light fixture
OrnamentalSpecialEffectFixture |  | Ornamental special effect light fixture
Outdoor Lighting
Performance
PrecisionWorkFixture |  | Precision work light fixture
Prescriptive
Regulated Exterior
Regulated Interior
SchoolLabTaskFixture |  | School lab task light fixture
SpecializedTaskFixture |  | Specialized task light fixture
Tailored |  | To be used only on projects with primary function areas that do not use the Area Category Method (calculated based on space type, IES category, area, room cavity ratio and other allowances). Wall display, floor display and ornamental/special effects lighting allowances shall be separate allotments without trade-offs between the allotments.
TailoredDisplayCaseAllowance |  | Tailored Method lighting allowance for display cases presenting very valuable display items
TailoredFloorDisplayAllowance |  | Tailored Method lighting allowance for floor displays.
TailoredGeneralLightingAllowance |  | Tailored Method general lighting allowance
TailoredOrnamentalAllowance |  | Tailored Method lighting allowance for ornamental lighting.
TailoredSpecialEffectAllowance |  | Tailored Method lighting allowance for special effect lighting.
TailoredWallDisplayAllowance |  | Tailored Method lighting allowance for wall displays.
VDT Viewing
VeryValuableDisplayFixture |  | Very valuable display light fixture
WallDisplayFixture |  | Wall display light fixture
A | IESNAIlluminanceCategory | Public Spaces - 30 lux (3 fc)
B | IESNAIlluminanceCategory | Simple Orientation for Short Visits - 50 lux (5 fc)
C | IESNAIlluminanceCategory | Working Spaces where simple tasks are performed - 100 lux (10 fc)
D | IESNAIlluminanceCategory | Performance of visual tasks of high contrast and large size - 300 lux (30 fc)
E | IESNAIlluminanceCategory | Performance of visual tasks of high contrast and small size, or low contrast and large size - 500 lux (50 fc)
F | IESNAIlluminanceCategory | Performance of visual tasks of low contrast and small size - 1000 lux (100 fc)
G | IESNAIlluminanceCategory | Performance of visual tasks near threshold - 3000-10,000 lux (300-1000 fc)
AutomaticMultiLevelDaylightingControl | LightingControlDevice | Multi-level lighting control that automatically reduces lighting in multiple steps or continuous dimming in response to available daylight. This control uses one or more photosensors to detect changes in daylight illumination and then change the electric lighting level in response to the daylight changes.
Dimmer | LightingControlDevice | Lighting control device capable of reducing lighting power consumption.
InterlockSwitch | LightingControlDevice | A nonprogrammable double throw switch control for lighting areas that have multiple interlocked lighting systems to control which systems are on. If this device is used,only the highest wattage lighting system is used in calculating the total lighting power for the lighting area.
ManualOnOccupancy | LightingControlDevice | A manual-on occupant sensor (also known as a vacancy sensor)
MultiLevelAstronomicalTimeSwitch | LightingControlDevice | Multi-level astronomical time-switch control
MultiLevelLightingControl | LightingControlDevice | A lighting control device that reduces lighting power in multiple steps while maintaining a reasonably uniform level of illuminance throughout the area controlled.
MultiLevelOccupancyControl | LightingControlDevice | Multi-level occupant sensor with an automatic OFF function that turns off all the lights, and either an automatic or a manually controlled ON function.
OutdoorAstronomicalTimeSwitch | LightingControlDevice | An astronomical time-switch used to control outdoor lighting
OverrideSwitch | LightingControlDevice | A manually operated switch that sends a signal that overrides an automatic control and keeps the lights on for no more than two hours. The device must be readily accessible and located so that a person using the device can see the lights or the area controlled by that switch, or so that the area being lit is annunciated.
SwitchingOrControlDevice | LightingControlDevice | A switching or control device is any device capable of manually or automatically switching off lighting. The device must be A. Readily accessible, B. Located so that a person using the device can see the lights or the area controlled by that switch, or so that the area being lit is annunciated.
SystemDRControl | LightingControlDevice | A demand responsive control that can reduce lighting power consumption.
SystemShutOff | LightingControlDevice | An automatic shut off control for all the lights (except security areas, egress or dwelling units) on every floor of the project.
AreaControl | LightingControlScheme | All the lighting in an area enclosed by ceiling-height partitions are switched off either automatically by an occupant sensor or manually by a switch.
AstronomicalTimeSwitch | LightingControlScheme | Lights turn on and off based on sunrise and sunset prediction for astronomical time parameters (longitude, latitude, and time zone).
AutomaticDaylighting | LightingControlScheme | Lights adjust in response to the availability of daylight
AutomaticShutoff | LightingControlScheme | Lights are automatically shut off in response to an automatic signal. This signal may come from an occupant sensor, time switch, or other device. The scheme must incorporate a "holiday shut off" feature that shuts off all loads for at least 24 hours, then resumes normally scheduled operation.
AutomaticTimeClock | LightingControlScheme | Lights are automatically turned on and off according to a time clock
DemandResponsive | LightingControlScheme | Lighting power consumption is uniformly reduced in response to demand signal.
Dimming | LightingControlScheme | Lights can be dimmed to multiple levels with the ability to lower lighting energy use.
MultiLevelLighting | LightingControlScheme | General lighting in an area enclosed by ceiling-height partitions is capable of being controlled to between 30% and 70% of full output, using prescribed combinations of switching and dimming.
MultiLevelOccupancy | LightingControlScheme | Lights turn on when occupant enters room and turn off when occupant leaves (after some delay).
MultipleInterlockedLighting | LightingControlScheme | Only the highest wattage system is used to calculate lighting power density if the lighting systems are interlocked with a non-programmable double throw switch to prevent simultaneous operation.
MultiSceneProgrammable | LightingControlScheme | Different scenes can be selected with lights set at levels other than only 100% on.
Vacancy | LightingControlScheme | Lights turn off when occupant leaves (after some delay). Lights do not automatically turn on.