## Outline
CBECC NR SDD Outline | [7 empty] | Properties
Project | [7 empty] | AnalysisType; City; CompOptAdd; CompOptAlt; CompOptDHW; CompOptEnve; CompOptExist; CompOptLtg; CompOptMech; CompOptNew; CompOptPartLtg; CompOptPartMech; GeometryInpType; NumOfDaysPerQuickAnalysisPeriod; NumOfQuickAnalysisPeriods; NumTimeStepsPerHr; PermitScope; RunPeriodBeginDay; RunPeriodBeginMonth; RunPeriodEndDay; RunPeriodEndMonth; RunPeriodYear; SimDsgnDays; SimVarsDayltg; SimVarsFen; SimVarsHVACPri; SimVarsHVACSec; SimVarsHVACZn; SimVarsSite; SimVarsThrmlZn; State; StreetAddress; VentStd; Zipcode; NRCAEnv02F; NRCALti02A; NRCALti03A; NRCALti04A; NRCALti05A; NRCALto02A; NRCAPrc01E; NRCAPrc01F; NRCAPrc02F; NRCAPrc03F; NRCAPrc04F; NRCAPrc05F; NRCAPrc06F; NRCAPrc07F; NRCAPrc08F; NRCAPrc12F; NRCAPrc13F; NRCIElc01E; NRCIEnv01E; NRCILti01E; NRCILti02E; NRCILti03E; NRCILti04E; NRCILti05E; NRCILti06E; NRCILto01E; NRCILto02E; NRCILts01E; NRCIMch01E; NRCIPlb01E; NRCIPlb02E; NRCIPlb03E; NRCIPlb21E; NRCIPlb22E; NRCISpv01E; NRCISth01E; NRCVMch04H; NRCVPlb21H; NRCVPlb22H; CompPathComputerRm; CompPathDHW; CompPathEnv; CompPathKit; CompPathLab; CompPathLtg; CompPathMech; CompReportPDF; CompReportStd; CompReportXML; DHWDetailsLctn; EnvDetailsLctn; ExcptCondExtLtg; ExcptCondNarrative; ExcptCondNoClgSys; ExcptCondRtdCap; ExcptDsgnModelFile; LtgOutdrComp; LtgSignComp; LtgUncondComp; LtgDetailsLctn; CommKitchenMandComp; ComRfrgMandComp; ComplexHVACMandComp; CompressedAirMandComp; ComputerRoomMandComp; ElecMandComp; ElevLtgVentMandComp; EscalSpdCtrlMandComp; LabExhaustMandComp; ParkingGarageMandComp; ProcBlrMandComp; RfrgWarehouseMandComp; SimpleHVACMandComp; SolReadyMandComp; MechDetailsLctn; NarrativeDetails; CompType; AutoDayltgRpt; AutoTimeSwitchRpt; DemandResponsiveRpt; InstitutionalTuningPAFRpt; OccSensorCntRpt; OutdrCtrlsRpt; RuleReportFileAppend; RuleReportType; RunTitle; SoftwareVersion; SolThrmlComp; StandardsVersion; UseExcptDsgnModel; VentMult; DocAuthName; DocAuthCompany; DocAuthAddress; DocAuthCEAIdent; DocAuthCity; DocAuthState; DocAuthZipCode; DocAuthPhone; EnvDsgnrAddress; EnvDsgnrCity; EnvDsgnrCompany; EnvDsgnrLicense; EnvDsgnrName; EnvDsgnrPhone; EnvDsgnrState; EnvDsgnrType; EnvDsgnrZipCode; LtgDsgnrAddress; LtgDsgnrCity; LtgDsgnrCompany; LtgDsgnrLicense; LtgDsgnrName; LtgDsgnrPhone; LtgDsgnrState; LtgDsgnrType; LtgDsgnrZipCode; MechDsgnrAddress; MechDsgnrCity; MechDsgnrCompany; MechDsgnrLicense; MechDsgnrName; MechDsgnrPhone; MechDsgnrState; MechDsgnrType; MechDsgnrZipCode
| Building | [6 empty] | AboveGrdStoryCnt; AboveGrdStoryCntAltered; AboveGrdStoryCntExisting; AboveGrdStoryCntNew; BelowGrdStoryCnt; FuncClassMthd; CoilClgCap; CoilClgCapHydronic; CoilHtgCap; CoilHtgCapHydronic; CtrlSysType; LivingUnitCntAltered; LivingUnitCntExisting; LivingUnitCntNew; NonResFlrArea; PlantClgCap; PlantHtgCap; BldgTerrain; TotCondVol; TotFlrArea; TotStoryCnt; TotStoryCntAltered; TotStoryCntExisting; TotStoryCntNew; TotUncondFlrArea; BuildingUniqueID_CEC; HighRiseResLivingUnitCnt; HotelMotelGuestRmCnt; Name; NonResStoryCntElecHt; NonResStoryCntFossilHt; BldgAz; OccFrac; RelocPubSchoolBldg; ResFlrArea; ResStoryCntElecHt; ResStoryCntFossilHt; WholeBldgModeled; WholePlantModeled; Zipcode; TopLevelOccupancy
|  | BuildingStory | [5 empty] | Mult; Z; FlrToCeilingHgt; FlrToFlrHgt; Name
|  |  | Space |  |  |  |  | CommRfrgLatFrac; CommRfrgLostFrac; CommRfrgRadFrac; GlrAz; MaxGlrIdx; MinDimLtgFrac; MinDimPwrFrac; NumOfCtrlSteps; DayltgCtrlType; DwellingUnitTypeArea; DwellingUnitTypeCnt; ElevCnt; ElevLatFrac; ElevLostFrac; ElevPwr; ElevRadFrac; ElevSchRef; EnclosedSpc; EscalCnt; EscalLatFrac; EscalLostFrac; EscalPwr; EscalRadFrac; EscalSchRef; ExhACH; ExhPerArea; ExhPerSpc; FxdSeat; GasEqpLatFrac; GasEqpLostFrac; GasEqpPwrDens; GasEqpRadFrac; HasProcExh; HighRiseResCondFlrArea; HotelMotelGuestRmCondFlrArea; HotelMotelGuestRmCnt; HotWtrHtgTot; HotWtrSupTempSchRef; IntLtgNonRegHtGnRadFrac; IntLtgNonRegHtGnSpcFrac; IntLtgNonRegSchRef; IntLtgRegHtGnRadFrac; IntLtgRegHtGnSpcFrac; IsAtriumGT55Ft; IsPlenumRet; KitExhHoodDuty; KitExhHoodFlow; KitchenExhHoodLen; KitchenExhHoodStyle; LabExhRtType; Name; OccFrac; OccNumFxdSeat; Perim; PriSideDayltgCtrlLtgPwr; PriSideDayltgIllumSetpt; PriSideDayltgInstalledLtgPwr; PriSide100PctControlled; ProcElecLatFrac; ProcElecLostFrac; ProcElecRadFrac; ProcElecSchRef; ProcGasLatFrac; ProcGasLostFrac; ProcGasPwrDens; ProcGasRadFrac; ProcGasSchRef; RecptLatFrac; RecptLostFrac; RecptRadFrac; ResDHWSysRef; ResHotWtrHtgRt; RetPlenumSpcRef; SecSideDayltgCtrlLtgPwr; SecSideDayltgIllumSetpt; SecSideDayltgInstalledLtgPwr; SecSide100PctControlled; SHWFluidSegRef; SkyltReqExcpt; SkyltReqExcptArea; SkyltReqExcptFrac; Skylit100PctControlled; SkylitDayltgCtrlLtgPwr; SkylitDayltgIllumSetpt; SkylitDayltgInstalledLtgPwr; Area; CondgType; EnvStatus; FlrArea; FlrToCeilingHgt; FlrZ; SpcFunc; SpcFuncDefaultsRef; IntLtgSpecMthd; LtgStatus; Vol; SupPlenumSpcRef; ThrmlZnRef; VentACH; VentPerArea; VentPerPerson; VentPerSpc; MandatoryLtgCtrlCntRpt; MandatoryLtgCtrlDescRpt; MandatoryLtgCtrlIsAcceptanceTestReqdRpt; MandatoryLtgCtrlIsAutoShutOffCtrlRpt; MandatoryLtgCtrlIsDayltgCtrlRpt; MandatoryLtgCtrlIsDemandResponseCtrlRpt; MandatoryLtgCtrlIsManAreaCtrlRpt; MandatoryLtgCtrlIsMultiLvlCtrlRpt
|  |  |  | Ceiling |  |  |  | Area; Name; AdjacentSpcRef; Az; ConsAssmRef; Tilt
PolyLoop
[6 empty] | CartesianPoint |  | Coord
|  |  |  | ExteriorFloor |  |  |  | Area; Name; Status; AdjacentSpcRef; Az; ConsAssmRef; Tilt
PolyLoop
[6 empty] | CartesianPoint |  | Coord
|  |  |  | ExteriorWall |  |  |  | Area; DisplayPerim; Hgt; Name; Status; Wd; AdjacentSpcRef; Az; ConsAssmRef; Tilt
[5 empty] | Door |  |  | Area; DrConsRef; Oper; Hgt; Name; Status; Wd; X; Y
PolyLoop
[7 empty] | CartesianPoint | Coord
PolyLoop
[6 empty] | CartesianPoint |  | Coord
[5 empty] | Window |  |  | EnableWinShades; FenConsRef; Hgt; LeftFinAngle; LeftFinDepth; LeftFinDistance; LeftFinDistanceAbove; LeftFinDistanceBelow; LeftFinTrans; LeftFinTransOption; LeftFinTransSchRef; Name; OverhangAngle; OverhangDepth; OverhangDistance; OverhangLeftExtension; OverhangRightExtension; OverhangTrans; OverhangTransOption; OverhangTransmittanceScheduleReference; RightFinAngle; RightFinDepth; RightFinDistance; RightFinDistanceAbove; RightFinDistanceBelow; RightFinTrans; RightFinTransOption; RightFinTransSchRef; Status; Wd; Area; X; Y
PolyLoop
[7 empty] | CartesianPoint | Coord
|  |  |  | InteriorFloor |  |  |  | AdjacentSpcRef; ConsAssmRef; Area; Name; Status; Az; Tilt
PolyLoop
[6 empty] | CartesianPoint |  | Coord
|  |  |  | InteriorLightingSystem |  |  |  | DaylitAreaType; AllowArea; AllowLen; AllowQty; AllowType; NonRegExclusion; PwrReg; IsAcceptanceTestReqdRpt; LtgCtrlCntRpt; LumCnt; LumMntgHgt; LumRef; LumStatus; Name; VeryValDispDesc; WorkPlaneHgt
|  |  |  | InteriorWall |  |  |  | Area; Name; Status; AdjacentSpcRef; Az; ConsAssmRef; Tilt
[5 empty] | Door |  |  | Area; DrConsRef; Oper; Hgt; Name; Status; Wd; X; Y
PolyLoop
[7 empty] | CartesianPoint | Coord
PolyLoop
[6 empty] | CartesianPoint |  | Coord
PolyLoop
[5 empty] | CartesianPoint |  |  | Coord
|  |  |  | Roof |  |  |  | CRRCAgedEmit; CRRCAgedRefl; CRRCAgedSRI; CRRCInitialEmit; CRRCInitialRefl; CRRCInitialSRI; CRRCProdID; FieldAppliedCoating; Name; Area; Status; AdjacentSpcRef; Az; ConsAssmRef; Tilt
PolyLoop
[6 empty] | CartesianPoint |  | Coord
[5 empty] | Skylight |  |  | FenConsRef; Name; Area; Status
PolyLoop
[7 empty] | CartesianPoint | Coord
|  |  |  | UndergroundFloor |  |  |  | Name; PerimExposed; Status; Area; AdjacentSpcRef; Az; ConsAssmRef; Tilt
PolyLoop
[6 empty] | CartesianPoint |  | Coord
|  |  |  | UndergroundWall |  |  |  | Name; Status; Area; Hgt; AdjacentSpcRef; Az; ConsAssmRef; Tilt
PolyLoop
[6 empty] | CartesianPoint |  | Coord
|  | AirSystem | [5 empty] | CtrlSysType; CtrlZnRef; ClgCtrl; ClgDsgnSupAirTemp; ClgFixedSupTemp; ClgSetptSchRef; Cnt; DuctLctn; DuctStatus; SubType; FanCtrl; FanPos; HtgDsgnSupAirTemp; HtgFixedSupTemp; HtgSetPtSchRef; NightCycleFanCtrl; OptStart; ReheatCtrlMthd; Type; ClRstOutdrHi; ClRstOutdrLow; ClRstSupHi; ClRstSupLow; Desc; DuctIns; ExhCtrlMthd; ExhOperMode; ExhSysType; IsAllOA; IsComplexSystem; Name; Status; AcceptanceTestReq; HERSDuctTested; HERSDuctReq; NRCAMch02A; NRCAMch03A; NRCAMch04H; NRCAMch05A; NRCAMch06A; NRCAMch07A; NRCAMch08A; NRCAMch09A; NRCAMch10A; NRCAMch11A; NRCAMch12A; NRCAMch13A; NRCAMch14A; NRCAMch15A; NRCAMch16A; NRCAMch17A; NRCAMch18A
|  |  | AirSegment |  |  |  |  | Path; Type; Name
|  |  |  | CoilCooling |  |  |  | BypassMinEffCheck; CndsrType; AuxPwr; CapTotNetRtd; CapTotGrossRtd; CapTotRtdStageFrac; DXEER; DXIEER; DXSEER; DXCrankcaseCtrlTemp; DXCrankcaseHtCap; MinHotGasRat; NumClgStages; Type; CoilHdDsgn; FluidFlowRtDsgn; FluidSegInRef; FluidSegOutRef; Name
|  |  |  | CoilHeating |  |  |  | BypassMinEffCheck; CndsrType; CoilHdDsgn; AuxPwr; CapTotGrossRtd; CapTotNetRtd; FuelSrc; FurnAFUE; FurnIgnType; FurnPilotFuelInp; FurnThrmlEff; HtPumpCprsrLockoutTemp; HtPumpCOP; HtPumpCrankcaseCtrlTemp; HtPumpCrankcaseHtCap; HtPumpDefCtrl; HtPumpDefHtCap; HtPumpDefHtSrc; HtPumpHSPF; HtPumpSuppCoilHtgRef; HtPumpSuppTemp; Type; FluidFlowRtDsgn; FluidSegInRef; FluidSegOutRef; Name
|  |  |  | EvaporativeCooler |  |  |  | Eff; IndirectDewPtEff; Name; PumpPwr; SecAirSrc; SecFanFlowCap; SecFanTotEff; SecFanTotStaticPress; Type
|  |  |  | Fan |  |  |  | CentType; Class; CtrlMthd; FlowCap; FlowMin; ModelingMthd; MtrPoleCnt; MtrPos; MtrType; FlowEff; TotStaticPress; MtrBHP; MtrEff; MtrHP; Name
|  |  | HeatRecovery |  |  |  |  | AuxPwr; ClgLatEff100; ClgLatEff75; ClgSensEff100; ClgSensEff75; ClgTotEff100; ClgTotEff75; DefrostCtrl; DefrostCtrlTemp; EconoLockout; FixedSupTemp; HasHXBypass; HtgLatEff100; HtgLatEff75; HtgSensEff100; HtgSensEff75; HtgTotEff100; HtgTotEff75; RcvryType; SupFlowRtd; TempCtrl; TempSetptSchRef; Type
|  |  | OutsideAirControl |  |  |  |  | Name; AirSegRetRef; AirSegSupRef; EconoCtrlMthd; EconoHiTempLockout; EconoIntegration; EconoLowTempLockout; HtRcvryRef
|  |  | TerminalUnit |  |  |  |  | Name; Status; Cnt; HtgAirFlowMax; InducedAirZnRef; InductionRat; ParallelBoxFanFlowFrac; PriAirFlowMax; PriAirFlowMin; PriAirSegRef; ReheatCtrlMthd; TotAirFlow; Type; ZnServedRef
|  |  |  | CoilHeating |  |  |  | BypassMinEffCheck; CndsrType; CoilHdDsgn; AuxPwr; CapTotGrossRtd; CapTotNetRtd; FuelSrc; FurnAFUE; FurnIgnType; FurnPilotFuelInp; FurnThrmlEff; HtPumpCprsrLockoutTemp; HtPumpCOP; HtPumpCrankcaseCtrlTemp; HtPumpCrankcaseHtCap; HtPumpDefCtrl; HtPumpDefHtCap; HtPumpDefHtSrc; HtPumpHSPF; HtPumpSuppCoilHtgRef; HtPumpSuppTemp; Type; FluidFlowRtDsgn; FluidSegInRef; FluidSegOutRef; Name
|  |  |  | Fan |  |  |  | CentType; Class; CtrlMthd; FlowCap; FlowMin; ModelingMthd; MtrPoleCnt; MtrPos; MtrType; FlowEff; TotStaticPress; MtrBHP; MtrEff; MtrHP; Name
|  | ThermalZone | [5 empty] | Desc; ExhSysRef; Name; OperableWinInterlock; OperableWinHaveInterlock; RetPlenumZnRef; SupPlenumZnRef; Type; ClgDsgnSupAirTemp; ClgDsgnSupAirTempDiff; DayltgCtrlLtgFrac1; DayltgCtrlLtgFrac2; DayltgCtrlType; DayltgMinDimLtgFrac; DayltgMinDimPwrFrac; DayltgNumCtrlSteps; HtgDsgnMaxFlowFrac; HtgDsgnSupAirTemp; HtgDsgnSupAirTempDiff; HVACZnCnt; PriAirCondgSysPriority; PrimAirCondgSysRef; VentCtrlMthd; VentSrc; VentSpecMthd; VentStdDesc; VentSysPriority; VentSysRef; AddClgSys; HasNoClg; HasUnknownHVAC; VentStd
|  | ZoneSystem | [5 empty] | Desc; DuctIns; DuctStatus; ExhCtrlMthd; ExhOperMode; ExhSysType; HVACAutoSizing; IsComplexSystem; Name; Status; ClgDsgnSupAirTemp; Cnt; DuctLctn; SubType; FanCtrl; HtgDsgnSupAirTemp; Type; AcceptanceTestReq; HERSDuctTested; HERSDuctReq; NRCAMch02A; NRCAMch03A; NRCAMch04H; NRCAMch05A; NRCAMch06A; NRCAMch07A; NRCAMch08A; NRCAMch09A; NRCAMch10A; NRCAMch11A; NRCAMch12A; NRCAMch13A; NRCAMch14A; NRCAMch15A; NRCAMch16A; NRCAMch17A; NRCAMch18A
|  |  | CoilCooling |  |  |  |  | BypassMinEffCheck; CndsrType; AuxPwr; CapTotNetRtd; CapTotGrossRtd; CapTotRtdStageFrac; DXEER; DXIEER; DXSEER; DXCrankcaseCtrlTemp; DXCrankcaseHtCap; MinHotGasRat; NumClgStages; Type; CoilHdDsgn; FluidFlowRtDsgn; FluidSegInRef; FluidSegOutRef; Name
|  |  | CoilHeating |  |  |  |  | BypassMinEffCheck; CndsrType; CoilHdDsgn; AuxPwr; CapTotGrossRtd; CapTotNetRtd; FuelSrc; FurnAFUE; FurnIgnType; FurnPilotFuelInp; FurnThrmlEff; HtPumpCprsrLockoutTemp; HtPumpCOP; HtPumpCrankcaseCtrlTemp; HtPumpCrankcaseHtCap; HtPumpDefCtrl; HtPumpDefHtCap; HtPumpDefHtSrc; HtPumpHSPF; HtPumpSuppCoilHtgRef; HtPumpSuppTemp; Type; FluidFlowRtDsgn; FluidSegInRef; FluidSegOutRef; Name
|  |  | Fan |  |  |  |  | CentType; Class; CtrlMthd; FlowCap; FlowMin; ModelingMthd; MtrPoleCnt; MtrPos; MtrType; FlowEff; TotStaticPress; MtrBHP; MtrEff; MtrHP; Name
| DesignDay | [6 empty] | CoinWB; Type; WindDirection; WindSpd; DsgnDBRng; DsgnDB; Day; Month; Name; SkyClear
| ExternalShadingObject | [6 empty] | SolRefl; VisRefl; Name; Status; Trans; TransOption; TransSchRef; WinRef
PolyLoop
|  |  | CartesianPoint |  |  |  |  | Coord
| Holiday | [6 empty] | DayOfWeek; Day; SpecMthd; Month; Name
| ThermalEnergyStorageModeScheduleDay | [6 empty] | Hr; Type
| FluidSystem | [6 empty] | AngleFromTrueNorth; AnnualSolFrac; AvailSchRef; Desc; NumOfIdenticalDwellingUnits; EquipList1Name; EquipList2Name; EquipList3Name; EquipList4Name; CentralSys; CtrlType; ClgSupTemp; Cnt; DsgnSupWtrTemp; DsgnSupWtrTempDelT; FixedSupTemp; HtgDsgnSupWtrTemp; HtgFixedSupTemp; HtgSupTemp; HtgTempSetptSchRef; HotWtrSupTemp; LdRngLim; RstOutdrHi; RstOutdrLow; RstSupHi; RstSupLow; TempCtrl; TempSetptSchRef; Type; WetBulbApproach; Name; SecondaryTankVol; SlopeFromHorizontal; SolCollectorCnt; Status; WtrHtrTankVol; Area; Brand; RatedEffCurveIntercept; RatedEffCurveSlope; Fluid; Manufacturer; ModelNum; CollectorType; NameOfProgramUsed; Version; SRRCCertNum; NRCAMch02A; NRCAMch03A; NRCAMch04H; NRCAMch05A; NRCAMch06A; NRCAMch07A; NRCAMch08A; NRCAMch09A; NRCAMch10A; NRCAMch11A; NRCAMch12A; NRCAMch13A; NRCAMch14A; NRCAMch15A; NRCAMch16A; NRCAMch17A; NRCAMch18A
|  | Boiler | [5 empty] | AFUE; CapRtd; CombEff; DraftFanHp; DraftType; EIR; EntTempDsgn; FuelFullLd; FuelSrc; HasBypass; HtLoss; LvgTempDsgn; ParasiticLd; Type; UnldRatMin; FluidSegInRef; FluidSegOutRef; Name; Status; ThrmlEff
|  |  | Pump |  |  |  |  | MinSpdRat; Name; FlowCap; FlowMin; ImpellerEff; ModelingMthd; MtrEff; MtrHP; OperCtrl; SpdCtrl; TotHd; Status
|  | Chiller | [5 empty] | AuxPwr; CapRtd; CndsrInRef; CndsrOutRef; CndsrPwrRtd; CndsrType; COP; EER; EnableOnThrmlEngyStorDischrg; EntTempDsgn; EntTempRtd; EvapInRef; EvapOutRef; EvapHasBypass; FuelSrc; IPLVCOP; IPLVEER; IPLVKwPerTon; KwPerTon; LvgTempDsgn; LvgTempRtd; PLRMin; Type; UnldRatMin; DsgnGenFluidDelT; EntGenTempDsgn; GenFluidFlowCap; GenFluidSegInRef; GenFluidSegOutRef; Name; Status
|  |  | Pump |  |  |  |  | MinSpdRat; Name; FlowCap; FlowMin; ImpellerEff; ModelingMthd; MtrEff; MtrHP; OperCtrl; SpdCtrl; TotHd; Status
|  | FluidSegment | [5 empty] | PriSegRef; Src; Type; Name
|  |  | Pump |  |  |  |  | MinSpdRat; Name; FlowCap; FlowMin; ImpellerEff; ModelingMthd; MtrEff; MtrHP; OperCtrl; SpdCtrl; TotHd; Status
|  | HeatExchanger | [5 empty] | CapRtd; CHWEntTempDsgn; CHWFluidSegInRef; CHWFluidSegOutRef; CHWLvgTempDsgn; CWFluidSegInRef; CWFluidSegOutRef; CWLvgTempDsgn; EconoIntegration; Type; Name; Status
|  | HeatRejection | [5 empty] | FluidSegInRef; FluidSegOutRef; AirFlowCap; CapRtd; CellCnt; DsgnWBTemp; EntTempDsgn; FanType; LvgTempDsgn; LowSpdAirFlowRat; MinSpdRat; ModCtrl; TotFanHP; Type; WtrFlowCap; Name; Status
|  |  | Pump |  |  |  |  | MinSpdRat; Name; FlowCap; FlowMin; ImpellerEff; ModelingMthd; MtrEff; MtrHP; OperCtrl; SpdCtrl; TotHd; Status
|  | ThermalEnergyStorage | [5 empty] | StorCap; CapRtd; ChrgFluidSegInRef; ChrgFluidSegOutRef; DischrgFluidSegInRef; DischrgFluidSegOutRef; DischargePriority; StorLctn; StorLctnSim; ModeSchRef; TankHgt; TankLenToWdRat; TankNodeCnt; TankR; TankShape; Type; StorageZoneReference
|  |  | Pump |  |  |  |  | MinSpdRat; Name; FlowCap; FlowMin; ImpellerEff; ModelingMthd; MtrEff; MtrHP; OperCtrl; SpdCtrl; TotHd; Status
|  | WaterHeater | [5 empty] | Name; RE; ThrmlEff; Status; CapRtd; CprsrLoc; CprsrZnRef; Cnt; DraftFanPwr; ElecIgnit; EF; FirstHrRating; FlowRt; FluidSegMakeupRef; FluidSegOutRef; FluidSysCnt; FuelSrc; InpPwr; MinCap; StdbyLossFrac; StorCap; StorCapSim; StorLoc; StorZnRef; TankHgtSim; Type; UEF
|  |  | Pump |  |  |  |  | MinSpdRat; Name; FlowCap; FlowMin; ImpellerEff; ModelingMthd; MtrEff; MtrHP; OperCtrl; SpdCtrl; TotHd; Status
| ResidentialDHWSystem | [6 empty] | AngleFromTrueNorth; AnnualSolFrac; NumOfIdenticalDwellingUnits; Name; BaseResWtrHtrRef; CentralSys; DistType; LpCnt; LpPipeInsThkns; Manufacturer; Mult; PipeLctn; PumpBHP; PumpEff; PumpPwr; SolFracFluidSysName; SysStoryCnt; SuppStorTankVol; TotInpRating; TotTankVol; Type; SecondaryTankVol; SlopeFromHorizontal; Status; WtrHtrTankVol; Area; Brand; SolCollectorCnt; RatedEffCurveIntercept; RatedEffCurveSlope; Fluid; Manufacturer; ModelNum; CollectorType; NameOfProgramUsed; Version; SRRCCertNum; BuriedReport; OutsideReport; PlenumReport; SolFracRpt
|  | ResidentialWaterHeater | [5 empty] | AmbCond; CprsrZn; Cnt; ElecMiniTank; ElecMiniTankPwr; ElementType; EngyFac; FirstHrRating; FlowRt; HPWHBrand; HPWHModel; HtPumpWtrHtrNEEARtd; InpRating; InpRatingElec; IsUEFRtd; Name; RE; StdbyLossFrac; Status; TankCat; TankExtInsR; TankIntInsR; TankVol; TankZn; ThrmlEff; UEF
| ConstructAssembly | [6 empty] | BallastedRoof; BuiltUpRoof; CompatibleSurfType; ConsAssmNotes; CRRCAgedEmit; CRRCAgedRefl; CRRCAgedSRI; CRRCInitialEmit; CRRCInitialRefl; CRRCInitialSRI; CRRCProdID; CRRCSRI; FieldAppliedCoating; MatRef; Name; RoofDens; SlabInsOrientation; SlabInsThrmlR; SlabType
| DoorConstruction | [6 empty] | DrAutoCloser; CertificationMthd; Open; Type; Name; UFactor
| FenestrationConstruction | [6 empty] | AssmContext; CertificationMthd; Diffusing; DynamicGlz; UFactor; VT; FenFrm; FenPanes; FenProdType; FenType; GlzTint; GreenhouseGardenWin; Name; OperableWinConfiguration; ShdgCred; SkyltCurb; SkyltGlz; SHGC; SHGCCOG; UFactorCOG; VTCOG; WinDivider
| Luminaire | [6 empty] | LumDescRpt; FxtrType; HtGnRadFrac; HtGnSpcFrac; LampType; LumMntgHgt; Pwr; Name; PwrNA8Default
| Material | [6 empty] | CavityIns; CavityInsOpt; FrmConfig; FrmDepth; CodeCat; CodeItem; Name; FrmMat
| Schedule | [6 empty] | EndDay; EndMonth; Name; Type; SchWeekRef
| ScheduleDay | [6 empty] | Name; Hr; Type
| ScheduleWeek | [6 empty] | Name; SchDayAllRef; SchDayClgDDRef; SchDayFriRef; SchDayHtgDDRef; SchDayHolRef; SchDayMonRef; SchDaySatRef; SchDaySunRef; SchDayThuRef; SchDayTueRef; SchDayWedRef; SchDayWDRef; SchDayWERef; Type
| SpaceFunctionDefaults | [6 empty] | CommRfrgLatFrac; CommRfrgLostFrac; CommRfrgRadFrac; DsgnInfRt; ElevCnt; ElevLatFrac; ElevLostFrac; ElevPwr; ElevRadFrac; ElevSchRef; EscalCnt; EscalLatFrac; EscalLostFrac; EscalPwr; EscalRadFrac; EscalSchRef; ExhACH; ExhPerArea; ExhPerSpc; GasEqpLatFrac; GasEqpLostFrac; GasEqpPwrDens; GasEqpRadFrac; HotWtrSupTemp; HotWtrSupTempSchRef; InfMthd; InfModelCoefA; InfModelCoefB; InfModelCoefC; InfModelCoefD; InfSchRef; IntLtgNonRegHtGnRadFrac; IntLtgNonRegHtGnSpcFrac; IntLtgNonRegSchRef; IntLtgRegHtGnRadFrac; IntLtgRegHtGnSpcFrac; Name; OccFrac; OccLatHtRt; OccSensHtRt; ProcElecLatFrac; ProcElecLostFrac; ProcElecRadFrac; ProcElecSchRef; ProcGasLatFrac; ProcGasLostFrac; ProcGasPwrDens; ProcGasRadFrac; ProcGasSchRef; RecptLatFrac; RecptLostFrac; RecptRadFrac; ResDHWSysRef; FuncSchGrp; SHWFluidSegRef; SpcFunc; VentACH; VentPerArea; VentPerPerson; VentPerSpc

## Objects
CBECC NR Term | CBECC NR Term Short Form | CBECC NR Parent | T24Objects NR CBECC Parent | Properties | Properties Short Form | Compliance Reporting Properties | Library Object | Referenced HVAC Object | Compliance Use | Components | Definition | Standards Reference | XSD ELEMATTRIB maxOccurs | Collapsed From
Building | Bldg |  | Project | AboveGradeStoryCount | AboveGrdStoryCnt |  | NO |  | Required | AirSys | The root element of the building description file, Building is any structure or space covered by Section 100.0 of the Building Energy Efficiency Standards. ASHRAE: a structure wholly or partially enclosed within exterior walls, or within exterior and party walls, and a roof, affording shelter to persons, animals, or property. | The Standards refer to any construction project as a building. Entire Building is the term used to represent a stand alone structure and the ensemble of all enclosed spaces including the space for which a permit is sought, plus all existing conditioned and unconditioned space within the structure. |  | BuildingOccupancyProperties
|  |  |  | AboveGradeStoryCountAltered | AboveGrdStoryCntAltered |  |  |  |  | Story
|  |  |  | AboveGradeStoryCountExisting | AboveGrdStoryCntExisting |  |  |  |  | ThrmlZn
|  |  |  | AboveGradeStoryCountNew | AboveGrdStoryCntNew |  |  |  |  | ZnSys
|  |  |  | BelowGradeStoryCount | BelowGrdStoryCnt
|  |  |  | BuildingAzimuth | BldgAz
|  |  |  | BuildingTerrain | BldgTerrain
|  |  |  | BuildingUniqueID_CEC | BuildingUniqueID_CEC
|  |  |  | CoilCoolingCapacity | CoilClgCap
|  |  |  | CoilCoolingCapacityHydronic | CoilClgCapHydronic
|  |  |  | CoilHeatingCapacity | CoilHtgCap
|  |  |  | CoilHeatingCapacityHydronic | CoilHtgCapHydronic
|  |  |  | ControlSystemType | CtrlSysType
|  |  |  | FunctionClassificationMethod | FuncClassMthd
|  |  |  | HighRiseResidentialLivingUnitCount | HighRiseResLivingUnitCnt
|  |  |  | HotelMotelGuestRoomCount | HotelMotelGuestRmCnt
|  |  |  | LivingUnitCountAltered | LivingUnitCntAltered
|  |  |  | LivingUnitCountExisting | LivingUnitCntExisting
|  |  |  | LivingUnitCountNew | LivingUnitCntNew
|  |  |  | Name | Name
|  |  |  | NonresidentialFloorArea | NonResFlrArea
|  |  |  | NonresidentialStoryCountElectricHeat | NonResStoryCntElecHt
|  |  |  | NonresidentialStoryCountFossilHeat | NonResStoryCntFossilHt
|  |  |  | OccupantFraction | OccFrac
|  |  |  | PlantCoolingCapacity | PlantClgCap
|  |  |  | PlantHeatingCapacity | PlantHtgCap
|  |  |  | RelocatablePublicSchoolBuilding | RelocPubSchoolBldg
|  |  |  | ResidentialFloorArea | ResFlrArea
|  |  |  | ResidentialStoryCountElectricHeat | ResStoryCntElecHt
|  |  |  | ResidentialStoryCountFossilHeat | ResStoryCntFossilHt
|  |  |  | TopLevelOccupancy | TopLevelOccupancy
|  |  |  | TotalConditionedVolume | TotCondVol
|  |  |  | TotalFloorArea | TotFlrArea
|  |  |  | TotalStoryCount | TotStoryCnt
|  |  |  | TotalStoryCountAltered | TotStoryCntAltered
|  |  |  | TotalStoryCountExisting | TotStoryCntExisting
|  |  |  | TotalStoryCountNew | TotStoryCntNew
|  |  |  | TotalUnconditionedFloorArea | TotUncondFlrArea
|  |  |  | WholeBuildingModeled | WholeBldgModeled
|  |  |  | WholePlantModeled | WholePlantModeled
|  |  |  | Zipcode | Zipcode
BuildingStory | Story | Bldg |  | FloorToCeilingHeight | FlrToCeilingHgt |  | NO |  | Required | Spc | The portion of a building included between the upper surface of a floor and the upper surface of the next floor or roof if it is the top floor.. It is measured as the vertical distance from top to top of two successive tiers of beams or finished floor surfaces. Source: definition in CBC ASHRAE: portion of a building that is between one finished floor level and the next higher finished floor level or the roof, provided, however, that a basement or cellar shall not be considered a story. | 2013 T24: The number of stories is used to differentiate between low rise residential and high rise residential which uses the nonresidential standards for the most part. | unbounded
|  |  |  | FloorToFloorHeight | FlrToFlrHgt
|  |  |  | Multiplier | Mult
|  |  |  | Name | Name
|  |  |  | Z | Z
CartesianPoint | CartesianPt | PolyLp |  | Coordinate | Coord |  | NO |  | Required |  | The cartesian triple (x, y and z) locating a three-dimensional point relative to some specified origin of coordinates. | NA | unbounded
Ceiling | Ceiling | Spc |  | AdjacentSpaceReference | AdjacentSpcRef |  | NO |  | Optional | PolyLp | A building partition forming the interior, overhead boundary of a space. | 2013 NR ACM: Ceiling is not a Building Descriptor JA1: Ceiling is the interior upper surface of a space separating it from an attic, plenum, indirectly or directly conditioned space or the roof assembly, 2013 JA4 tables in section 4.2 have rules regarding Ceiling properties | unbounded | Partition
|  |  |  | Area | Area
|  |  |  | Azimuth | Az
|  |  |  | ConstructAssemblyReference | ConsAssmRef
|  |  |  | Name | Name
|  |  |  | Tilt | Tilt
ConstructAssembly | ConsAssm |  | Project | BallastedRoof | BallastedRoof |  | YES |  | Required |  | If the construcntion specification method is Layers, this is an array of up to 10 references to materials layers. Otherwise the descriptive name for the construction assembly. is used to assign a UFactor or FFactor | 2013 JA 4 contains tables for assigning UFactor and FFactor to defined construction assembles.
|  |  |  | BuiltUpRoof | BuiltUpRoof
|  |  |  | CRRCAgedEmittance | CRRCAgedEmit
|  |  |  | CRRCAgedReflectance | CRRCAgedRefl
|  |  |  | CRRCAgedSRI | CRRCAgedSRI
|  |  |  | CRRCInitialEmittance | CRRCInitialEmit
|  |  |  | CRRCInitialReflectance | CRRCInitialRefl
|  |  |  | CRRCInitialSRI | CRRCInitialSRI
|  |  |  | CRRCProductID | CRRCProdID
|  |  |  | CRRCSolarReflectanceIndex | CRRCSRI
|  |  |  | CompatibleSurfaceType | CompatibleSurfType
|  |  |  | ConstructionAssemblyNotes | ConsAssmNotes
|  |  |  | FieldAppliedCoating | FieldAppliedCoating
|  |  |  | MaterialReference | MatRef
|  |  |  | Name | Name
|  |  |  | RoofDensity | RoofDens
|  |  |  | SlabInsulationOrientation | SlabInsOrientation
|  |  |  | SlabInsulationThermalResistance | SlabInsThrmlR
|  |  |  | SlabType | SlabType
DesignDay | DD |  | Project | CoincidentWetBulb | CoinWB |  | NO |  | Required |  | The design day specifies a number of weather related properties dependent on the location and climate zone of the project, which are used in establishing the correct size of the HVAC systems for space heating and cooling. | 2013 T24: Section 140.4 - references JA2-68 | unbounded
|  |  |  | DesignDryBulb | DsgnDB
|  |  |  | DesignDryBulbRange | DsgnDBRng
|  |  |  | Month | Month
|  |  |  | MonthDay | Day
|  |  |  | Name | Name
|  |  |  | SkyClearness | SkyClear
|  |  |  | Type | Type
|  |  |  | WindDirection | WindDirection
|  |  |  | WindSpeed | WindSpd
Door | Dr | ExtWall |  | Area | Area |  | NO |  | Optional | PolyLp | An opening in the building envelope or an internal wall, which is opaque or has less than 50% glazing. and provides passage to and from an interior space. | 2013 NR ACM: Section 5.5.6 Doors (no longer called Exterior Doors). Table 30 Baseline Building U-factor Criteria for Doors. | unbounded
|  | IntWall |  | DoorConstructionReference | DrConsRef
|  |  |  | Height | Hgt
|  |  |  | Name | Name
|  |  |  | Operation | Oper
|  |  |  | Status | Status
|  |  |  | Width | Wd
|  |  |  | X | X
|  |  |  | Y | Y
DoorConstruction | DrCons |  | Project | CertificationMethod | CertificationMthd |  | YES |  | Optional |  | This is a composite definition of a door's construction providing required data to evaluate in assigning UFactor. |  | unbounded
|  |  |  | DoorAutomaticCloser | DrAutoCloser
|  |  |  | Name | Name
|  |  |  | Open | Open
|  |  |  | Type | Type
|  |  |  | UFactor | UFactor
ExteriorFloor | ExtFlr | Spc |  | AdjacentSpaceReference | AdjacentSpcRef |  | NO |  | Optional | PolyLp | A Floor that separates the Space from surface ground | 2013 JA4 4.4 Floors and Slabs contains tables for exterior floors with or without a crawl space. |  | Partition
|  |  |  | Area | Area
|  |  |  | Azimuth | Az
|  |  |  | ConstructAssemblyReference | ConsAssmRef
|  |  |  | Name | Name
|  |  |  | Status | Status
|  |  |  | Tilt | Tilt
ExteriorWall | ExtWall | Spc |  | AdjacentSpaceReference | AdjacentSpcRef |  | NO |  | Optional | Dr | A Wall that separated the Space from outdoors | 2013 JA4 4.3 Walls contains tables for exterior walls |  | Partition
|  |  |  | Area | Area |  |  |  |  | PolyLp
|  |  |  | Azimuth | Az |  |  |  |  | Win
|  |  |  | ConstructAssemblyReference | ConsAssmRef
|  |  |  | DisplayPerimeter | DisplayPerim
|  |  |  | Height | Hgt
|  |  |  | Name | Name
|  |  |  | Status | Status
|  |  |  | Tilt | Tilt
|  |  |  | Width | Wd
ExternalShadingObject | ExtShdgObj |  | Project | Name | Name |  | NO |  | Optional | PolyLp | Devices or building features, such as overhangs, fins, on the exterior face of the wall, that are documented on the construction documents and shade the glazing or shade the Building. | 2013 NR ACM This is a building description found in section 5.5.7 Fenestration
|  |  |  | SolarReflectance | SolRefl
|  |  |  | Status | Status
|  |  |  | Transmittance | Trans
|  |  |  | TransmittanceOption | TransOption
|  |  |  | TransmittanceScheduleReference | TransSchRef
|  |  |  | VisibleReflectance | VisRefl
|  |  |  | WindowReference | WinRef
FenestrationConstruction | FenCons |  | Project | AssemblyContext | AssmContext |  | YES |  | Optional |  | A structure specifying the construction attributes and associated thermal and optical properties that apply to all fenestration products. | 2013 NR ACM: A property building descriptor of Fenestration. Also, Section 5.11.7 Fenestration Construction common data structure for this property. T24: Fenestration construction is defined in the Fenestration Product which is any transparent or translucent material plus any sash, frame, mullions and dividers, that fills an open space in the envelope of a building, such as a window, sliding glass door, French door, skylight, curtain wall, garden window, or an open space in a door where the opening is more than one half of the door area.
|  |  |  | CertificationMethod | CertificationMthd
|  |  |  | Diffusing | Diffusing
|  |  |  | DynamicGlazing | DynamicGlz
|  |  |  | FenestrationFraming | FenFrm
|  |  |  | FenestrationPanes | FenPanes
|  |  |  | FenestrationProductType | FenProdType
|  |  |  | FenestrationType | FenType
|  |  |  | GlazingTint | GlzTint
|  |  |  | GreenhouseGardenWindow | GreenhouseGardenWin
|  |  |  | Name | Name
|  |  |  | OperableWindowConfiguration | OperableWinConfiguration
|  |  |  | SHGC | SHGC
|  |  |  | SHGCCenterOfGlass | SHGCCOG
|  |  |  | ShadingCredit | ShdgCred
|  |  |  | SkylightCurb | SkyltCurb
|  |  |  | SkylightGlazing | SkyltGlz
|  |  |  | UFactor | UFactor
|  |  |  | UFactorCenterOfGlass | UFactorCOG
|  |  |  | VisibleTransmittance | VT
|  |  |  | VisibleTransmittanceCenterOfGlass | VTCOG
|  |  |  | WindowDivider | WinDivider
Holiday | Holiday |  | Project | Day | Day |  | NO |  |  |  | Allows for specification of individual Holidays simulated by EnergyPlus
|  |  |  | DayOfWeek | DayOfWeek
|  |  |  | Month | Month
|  |  |  | Name | Name
|  |  |  | SpecificationMethod | SpecMthd
InteriorFloor | IntFlr | Spc |  | AdjacentSpaceReference | AdjacentSpcRef |  | NO |  | Optional | PolyLp | A Floor that separates the Space from another interior Space | NA |  | Partition
|  |  |  | Area | Area
|  |  |  | Azimuth | Az
|  |  |  | ConstructAssemblyReference | ConsAssmRef
|  |  |  | Name | Name
|  |  |  | Status | Status
|  |  |  | Tilt | Tilt
InteriorLightingSystem | IntLtgSys | Spc |  | AllowanceArea | AllowArea |  | NO |  | Optional |  | Container for building descriptors provided for each lighting system in a space. Typically a space will have only one lighting system, but in some cases, it could have two or more . Examples include a general and task lighting system in offices or hotel multi-purpose rooms that have lighting systems for different functions. | 2013 Draft ACM Sec 5.4 | unbounded
|  |  |  | AllowanceLength | AllowLen
|  |  |  | AllowanceQuantity | AllowQty
|  |  |  | AllowanceType | AllowType
|  |  |  | DaylitAreaType | DaylitAreaType
|  |  |  | IsAcceptanceTestRequiredReport | IsAcceptanceTestReqdRpt
|  |  |  | LightingControlCountReport | LtgCtrlCntRpt
|  |  |  | LuminaireCount | LumCnt
|  |  |  | LuminaireMountingHeight | LumMntgHgt
|  |  |  | LuminaireReference | LumRef
|  |  |  | LuminaireStatus | LumStatus
|  |  |  | Name | Name
|  |  |  | NonRegulatedExclusion | NonRegExclusion
|  |  |  | PowerRegulated | PwrReg
|  |  |  | VeryValuableDisplayDescription | VeryValDispDesc
|  |  |  | WorkPlaneHeight | WorkPlaneHgt
InteriorWall | IntWall | Spc |  | AdjacentSpaceReference | AdjacentSpcRef |  | NO |  | Optional | Dr | A Wall that separates the Space from another interior Space |  | unbounded | Partition
|  |  |  | Area | Area |  |  |  |  | PolyLp
|  |  |  | Azimuth | Az
|  |  |  | ConstructAssemblyReference | ConsAssmRef
|  |  |  | Name | Name
|  |  |  | Status | Status
|  |  |  | Tilt | Tilt
Luminaire | Lum |  | Project | FixtureType | FxtrType |  | YES |  | Optional |  | Container for details of a luminaire type. | 2013 Draft ACM Sec 5.4 | unbounded
|  |  |  | HeatGainRadiantFraction | HtGnRadFrac
|  |  |  | HeatGainSpaceFraction | HtGnSpcFrac
|  |  |  | LampType | LampType
|  |  |  | LuminaireDescriptionReport | LumDescRpt
|  |  |  | LuminaireMountingHeight | LumMntgHgt
|  |  |  | Name | Name
|  |  |  | Power | Pwr
|  |  |  | PowerNA8Default | PwrNA8Default
Material | Mat |  | Project | CavityInsulation | CavityIns |  | YES |  | Optional |  | Used in layers in a Construction Assembly and records the type of material and it's characteristics that effect heat transfer such as specific heat capacity, density, thickness. | 2013 NR ACM Appendix 5.5A Construction Materials
|  |  |  | CavityInsulationOption | CavityInsOpt
|  |  |  | CodeCategory | CodeCat
|  |  |  | CodeItem | CodeItem
|  |  |  | FramingConfiguration | FrmConfig
|  |  |  | FramingDepth | FrmDepth
|  |  |  | FramingMaterial | FrmMat
|  |  |  | Name | Name
PolyLoop | PolyLp | Ceiling |  |  |  |  | NO |  | Required | CartesianPt | A list of coordinates that make up a polygon in three-dimensional space. All coordinates must lie on the same plane. The right-hand rule applies for defining the outward normal of a surface: For every surface, points must be defined in order, such that the direction of (the average cross-product between (any point, the centroid of the surface, and the next point)) points in the direction of the outward normal, which is a vector pointing away from the associated/parent zone/space. Includes a number of child CartesianPoint objects, with a maximum allowed based on the default quantity of polygon vertices allowed in EnergyPlus (this is 120 in DOE-2.2). | NA
Dr
ExtFlr
ExtShdgObj
ExtWall
IntFlr
IntWall
Roof
Skylt
Spc
UndgrFlr
UndgrWall
Win
Roof | Roof | Spc |  | AdjacentSpaceReference | AdjacentSpcRef |  | NO |  | Optional | PolyLp | Makes up the top exterior boundary of the building envelope. It is generally horizontal or sloped less than 60 degrees from horizontal. | T24: Roof is the outside cover of a building or structure including the structural supports, decking, and top layer that is exposed to the outside with a slope less than 60 degrees from the horizontal. 2013 NR ACM 5.5.3 Roofs Maps to Roof, which is a building descriptor |  | Partition
|  |  |  | Area | Area |  |  |  |  | Skylt
|  |  |  | Azimuth | Az
|  |  |  | CRRCAgedEmittance | CRRCAgedEmit
|  |  |  | CRRCAgedReflectance | CRRCAgedRefl
|  |  |  | CRRCAgedSRI | CRRCAgedSRI
|  |  |  | CRRCInitialEmittance | CRRCInitialEmit
|  |  |  | CRRCInitialReflectance | CRRCInitialRefl
|  |  |  | CRRCInitialSRI | CRRCInitialSRI
|  |  |  | CRRCProductID | CRRCProdID
|  |  |  | ConstructAssemblyReference | ConsAssmRef
|  |  |  | FieldAppliedCoating | FieldAppliedCoating
|  |  |  | Name | Name
|  |  |  | Status | Status
|  |  |  | Tilt | Tilt
Schedule | Sch |  | Project | EndDay | EndDay |  | YES |  | Required |  |  | 2013 NR ACM Appendix 5.4B 2008 NR ACM oad schedules in tables N2-8 through N2-12
|  |  |  | EndMonth | EndMonth
|  |  |  | Name | Name
|  |  |  | ScheduleWeekReference | SchWeekRef
|  |  |  | Type | Type
ScheduleDay | SchDay |  | Project | Hour | Hr |  | YES |  | Required |  |  | 2013 NR ACM Appendix 5.4B
|  |  |  | Name | Name
|  |  |  | Type | Type
ScheduleWeek | SchWeek |  | Project | Name | Name |  | YES |  | Required |  |  | 2013 NR ACM Appendix 5.4B
|  |  |  | ScheduleDayAllDaysReference | SchDayAllRef
|  |  |  | ScheduleDayCoolingDesignDayReference | SchDayClgDDRef
|  |  |  | ScheduleDayFridayReference | SchDayFriRef
|  |  |  | ScheduleDayHeatingDesignDayReference | SchDayHtgDDRef
|  |  |  | ScheduleDayHolidayReference | SchDayHolRef
|  |  |  | ScheduleDayMondayReference | SchDayMonRef
|  |  |  | ScheduleDaySaturdayReference | SchDaySatRef
|  |  |  | ScheduleDaySundayReference | SchDaySunRef
|  |  |  | ScheduleDayThursdayReference | SchDayThuRef
|  |  |  | ScheduleDayTuesdayReference | SchDayTueRef
|  |  |  | ScheduleDayWednesdayReference | SchDayWedRef
|  |  |  | ScheduleDayWeekdaysReference | SchDayWDRef
|  |  |  | ScheduleDayWeekendsReference | SchDayWERef
|  |  |  | Type | Type
Skylight | Skylt | Roof |  | Area | Area |  | NO |  | Optional | PolyLp | A fenestration skylight product installed in a roof and includes all construction and thermal properties required for applying the Standards. | 2013 T24: Skylight is fenestration installed on a roof less than 60 degrees from the horizontal. NR ACM 2.3.5.6 Fenestration Thermal Properties 2013 NR ACM Maps to Skylight Fenestration. In the building description Fenestration, skylight is defined as fenestration that has a tilt of less than 60 degrees from horizontal. | unbounded
|  |  |  | FenestrationConstructionReference | FenConsRef
|  |  |  | Name | Name
|  |  |  | Status | Status
Space | Spc | Story |  | Area | Area | MandatoryLtgCtrlCntRpt | NO | ThermalZone | Required | Ceiling | The fundamental unit of space conditioning based on the occupancy type | Title 24 Part 6 Section 101 definitions: ZONE, SPACE-CONDITIONING, is a space or group of spaces within a building with sufficiently similar comfort conditioning requirements so that comfort conditions, as specified in Section 144(b)3 or 150(h), as applicable, can be maintained throughout the zone by a single controlling device. 2013 NR ACM Space maps to HVAC Zone which is defined as follows: HVAC zone is a physical space within the building that has its own thermostat and zonal system for maintaining thermal comfort. It isn't clear how this differs from Thermal Block | unbounded | KitchenExhaustHood SpaceGeometry
|  |  |  | CommercialRefrigerationLatentFraction | CommRfrgLatFrac | MandatoryLtgCtrlDescRpt |  |  |  | ExtFlr
|  |  |  | CommercialRefrigerationLostFraction | CommRfrgLostFrac | MandatoryLtgCtrlIsAcceptanceTestReqdRpt |  |  |  | ExtWall
|  |  |  | CommercialRefrigerationRadiationFraction | CommRfrgRadFrac | MandatoryLtgCtrlIsAutoShutOffCtrlRpt |  |  |  | IntFlr
|  |  |  | ConditioningType | CondgType | MandatoryLtgCtrlIsDayltgCtrlRpt |  |  |  | IntLtgSys
|  |  |  | DaylightingControlType | DayltgCtrlType | MandatoryLtgCtrlIsDemandResponseCtrlRpt |  |  |  | IntWall
|  |  |  | DwellingUnitTypeArea | DwellingUnitTypeArea | MandatoryLtgCtrlIsManAreaCtrlRpt |  |  |  | PolyLp
|  |  |  | DwellingUnitTypeCount | DwellingUnitTypeCnt | MandatoryLtgCtrlIsMultiLvlCtrlRpt |  |  |  | Roof
|  |  |  | ElevatorCount | ElevCnt |  |  |  |  | UndgrFlr
|  |  |  | ElevatorLatentFraction | ElevLatFrac |  |  |  |  | UndgrWall
|  |  |  | ElevatorLostFraction | ElevLostFrac
|  |  |  | ElevatorPower | ElevPwr
|  |  |  | ElevatorRadiationFraction | ElevRadFrac
|  |  |  | ElevatorScheduleReference | ElevSchRef
|  |  |  | EnclosedSpace | EnclosedSpc
|  |  |  | EnvelopeStatus | EnvStatus
|  |  |  | EscalatorCount | EscalCnt
|  |  |  | EscalatorLatentFraction | EscalLatFrac
|  |  |  | EscalatorLostFraction | EscalLostFrac
|  |  |  | EscalatorPower | EscalPwr
|  |  |  | EscalatorRadiationFraction | EscalRadFrac
|  |  |  | EscalatorScheduleReference | EscalSchRef
|  |  |  | ExhaustAirChangesPerHour | ExhACH
|  |  |  | ExhaustPerArea | ExhPerArea
|  |  |  | ExhaustPerSpace | ExhPerSpc
|  |  |  | FixedSeating | FxdSeat
|  |  |  | FloorArea | FlrArea
|  |  |  | FloorToCeilingHeight | FlrToCeilingHgt
|  |  |  | FloorZ | FlrZ
|  |  |  | GasEquipmentLatentFraction | GasEqpLatFrac
|  |  |  | GasEquipmentLostFraction | GasEqpLostFrac
|  |  |  | GasEquipmentPowerDensity | GasEqpPwrDens
|  |  |  | GasEquipmentRadiationFraction | GasEqpRadFrac
|  |  |  | GlareAzimuth | GlrAz
|  |  |  | HasProcessExhaust | HasProcExh
|  |  |  | HighRiseResidentialConditionedFloorArea | HighRiseResCondFlrArea
|  |  |  | HotWaterHeatingTotal | HotWtrHtgTot
|  |  |  | HotWaterSupplyTemperatureScheduleReference | HotWtrSupTempSchRef
|  |  |  | HotelModelGuestRoomConditionedFloorArea | HotelMotelGuestRmCondFlrArea
|  |  |  | HotelMotelGuestRoomCount | HotelMotelGuestRmCnt
|  |  |  | InteriorLightingNonRegulatedHeatGainRadiantFraction | IntLtgNonRegHtGnRadFrac
|  |  |  | InteriorLightingNonRegulatedHeatGainSpaceFraction | IntLtgNonRegHtGnSpcFrac
|  |  |  | InteriorLightingNonRegulatedScheduleReference | IntLtgNonRegSchRef
|  |  |  | InteriorLightingRegulatedHeatGainRadiantFraction | IntLtgRegHtGnRadFrac
|  |  |  | InteriorLightingRegulatedHeatGainSpaceFraction | IntLtgRegHtGnSpcFrac
|  |  |  | InteriorLightingSpecificationMethod | IntLtgSpecMthd
|  |  |  | IsAtriumGreaterThan55Feet | IsAtriumGT55Ft
|  |  |  | IsPlenumReturn | IsPlenumRet
|  |  |  | KitchenExhaustHoodDuty | KitExhHoodDuty
|  |  |  | KitchenExhaustHoodFlow | KitExhHoodFlow
|  |  |  | KitchenExhaustHoodLength | KitchenExhHoodLen
|  |  |  | KitchenExhaustHoodStyle | KitchenExhHoodStyle
|  |  |  | LaboratoryExhaustRateType | LabExhRtType
|  |  |  | LightingStatus | LtgStatus
|  |  |  | MaximumGlareIndex | MaxGlrIdx
|  |  |  | MinimumDimmingLightFraction | MinDimLtgFrac
|  |  |  | MinimumDimmingPowerFraction | MinDimPwrFrac
|  |  |  | Name | Name
|  |  |  | NumberOfControlSteps | NumOfCtrlSteps
|  |  |  | OccupantFraction | OccFrac
|  |  |  | OccupantNumberFixedSeating | OccNumFxdSeat
|  |  |  | Perimeter | Perim
|  |  |  | PrimarySideDaylightingControlledLightingPower | PriSideDayltgCtrlLtgPwr
|  |  |  | PrimarySideDaylightingIlluminanceSetPoint | PriSideDayltgIllumSetpt
|  |  |  | PrimarySideDaylightingInstalledLightingPower | PriSideDayltgInstalledLtgPwr
|  |  |  | PrimarySidelit100PercentControlled | PriSide100PctControlled
|  |  |  | ProcessElectricalLatentFraction | ProcElecLatFrac
|  |  |  | ProcessElectricalLostFraction | ProcElecLostFrac
|  |  |  | ProcessElectricalRadiationFraction | ProcElecRadFrac
|  |  |  | ProcessElectricalScheduleReference | ProcElecSchRef
|  |  |  | ProcessGasLatentFraction | ProcGasLatFrac
|  |  |  | ProcessGasLostFraction | ProcGasLostFrac
|  |  |  | ProcessGasPowerDensity | ProcGasPwrDens
|  |  |  | ProcessGasRadiationFraction | ProcGasRadFrac
|  |  |  | ProcessGasScheduleReference | ProcGasSchRef
|  |  |  | ReceptacleLatentFraction | RecptLatFrac
|  |  |  | ReceptacleLostFraction | RecptLostFrac
|  |  |  | ReceptacleRadiationFraction | RecptRadFrac
|  |  |  | ResidentialDHWSystemReference | ResDHWSysRef
|  |  |  | ResidentialHotWaterHeatingRate | ResHotWtrHtgRt
|  |  |  | ReturnPlenumSpaceReference | RetPlenumSpcRef
|  |  |  | SHWFluidSegmentReference | SHWFluidSegRef
|  |  |  | SecondarySideDaylightingControlledLightingPower | SecSideDayltgCtrlLtgPwr
|  |  |  | SecondarySideDaylightingIlluminanceSetPoint | SecSideDayltgIllumSetpt
|  |  |  | SecondarySideDaylightingInstalledLightingPower | SecSideDayltgInstalledLtgPwr
|  |  |  | SecondarySidelit100PercentControlled | SecSide100PctControlled
|  |  |  | SkylightRequirementException | SkyltReqExcpt
|  |  |  | SkylightRequirementExceptionArea | SkyltReqExcptArea
|  |  |  | SkylightRequirementExceptionFraction | SkyltReqExcptFrac
|  |  |  | Skylit100PercentControlled | Skylit100PctControlled
|  |  |  | SkylitDaylightingControlledLightingPower | SkylitDayltgCtrlLtgPwr
|  |  |  | SkylitDaylightingIlluminanceSetPoint | SkylitDayltgIllumSetpt
|  |  |  | SkylitDaylightingInstalledLightingPower | SkylitDayltgInstalledLtgPwr
|  |  |  | SpaceFunction | SpcFunc
|  |  |  | SpaceFunctionDefaultsReference | SpcFuncDefaultsRef
|  |  |  | SupplyPlenumSpaceReference | SupPlenumSpcRef
|  |  |  | ThermalZoneReference | ThrmlZnRef
|  |  |  | VentilationAirChangesPerHour | VentACH
|  |  |  | VentilationPerArea | VentPerArea
|  |  |  | VentilationPerPerson | VentPerPerson
|  |  |  | VentilationPerSpace | VentPerSpc
|  |  |  | Volume | Vol
SpaceFunctionDefaults | SpcFuncDefaults |  | Project | CommercialRefrigerationLatentFraction | CommRfrgLatFrac |  | YES |  | Optional |  | Container for default specification of internal loads within a Space, based on Space Occupancy Function type. | 2013 Draft Nonresidential ACM
|  |  |  | CommercialRefrigerationLostFraction | CommRfrgLostFrac
|  |  |  | CommercialRefrigerationRadiationFraction | CommRfrgRadFrac
|  |  |  | DesignInfiltrationRate | DsgnInfRt
|  |  |  | ElevatorCount | ElevCnt
|  |  |  | ElevatorLatentFraction | ElevLatFrac
|  |  |  | ElevatorLostFraction | ElevLostFrac
|  |  |  | ElevatorPower | ElevPwr
|  |  |  | ElevatorRadiationFraction | ElevRadFrac
|  |  |  | ElevatorScheduleReference | ElevSchRef
|  |  |  | EscalatorCount | EscalCnt
|  |  |  | EscalatorLatentFraction | EscalLatFrac
|  |  |  | EscalatorLostFraction | EscalLostFrac
|  |  |  | EscalatorPower | EscalPwr
|  |  |  | EscalatorRadiationFraction | EscalRadFrac
|  |  |  | EscalatorScheduleReference | EscalSchRef
|  |  |  | ExhaustAirChangesPerHour | ExhACH
|  |  |  | ExhaustPerArea | ExhPerArea
|  |  |  | ExhaustPerSpace | ExhPerSpc
|  |  |  | FunctionScheduleGroup | FuncSchGrp
|  |  |  | GasEquipmentLatentFraction | GasEqpLatFrac
|  |  |  | GasEquipmentLostFraction | GasEqpLostFrac
|  |  |  | GasEquipmentPowerDensity | GasEqpPwrDens
|  |  |  | GasEquipmentRadiationFraction | GasEqpRadFrac
|  |  |  | HotWaterSupplyTemperature | HotWtrSupTemp
|  |  |  | HotWaterSupplyTemperatureScheduleReference | HotWtrSupTempSchRef
|  |  |  | InfiltrationMethod | InfMthd
|  |  |  | InfiltrationModelCoefficientA | InfModelCoefA
|  |  |  | InfiltrationModelCoefficientB | InfModelCoefB
|  |  |  | InfiltrationModelCoefficientC | InfModelCoefC
|  |  |  | InfiltrationModelCoefficientD | InfModelCoefD
|  |  |  | InfiltrationScheduleReference | InfSchRef
|  |  |  | InteriorLightingNonRegulatedHeatGainRadiantFraction | IntLtgNonRegHtGnRadFrac
|  |  |  | InteriorLightingNonRegulatedHeatGainSpaceFraction | IntLtgNonRegHtGnSpcFrac
|  |  |  | InteriorLightingNonRegulatedScheduleReference | IntLtgNonRegSchRef
|  |  |  | InteriorLightingRegulatedHeatGainRadiantFraction | IntLtgRegHtGnRadFrac
|  |  |  | InteriorLightingRegulatedHeatGainSpaceFraction | IntLtgRegHtGnSpcFrac
|  |  |  | Name | Name
|  |  |  | OccupantFraction | OccFrac
|  |  |  | OccupantLatentHeatRate | OccLatHtRt
|  |  |  | OccupantSensibleHeatRate | OccSensHtRt
|  |  |  | ProcessElectricalLatentFraction | ProcElecLatFrac
|  |  |  | ProcessElectricalLostFraction | ProcElecLostFrac
|  |  |  | ProcessElectricalRadiationFraction | ProcElecRadFrac
|  |  |  | ProcessElectricalScheduleReference | ProcElecSchRef
|  |  |  | ProcessGasLatentFraction | ProcGasLatFrac
|  |  |  | ProcessGasLostFraction | ProcGasLostFrac
|  |  |  | ProcessGasPowerDensity | ProcGasPwrDens
|  |  |  | ProcessGasRadiationFraction | ProcGasRadFrac
|  |  |  | ProcessGasScheduleReference | ProcGasSchRef
|  |  |  | ReceptacleLatentFraction | RecptLatFrac
|  |  |  | ReceptacleLostFraction | RecptLostFrac
|  |  |  | ReceptacleRadiationFraction | RecptRadFrac
|  |  |  | ResidentialDHWSystemReference | ResDHWSysRef
|  |  |  | SHWFluidSegmentReference | SHWFluidSegRef
|  |  |  | SpaceFunction | SpcFunc
|  |  |  | VentilationAirChangesPerHour | VentACH
|  |  |  | VentilationPerArea | VentPerArea
|  |  |  | VentilationPerPerson | VentPerPerson
|  |  |  | VentilationPerSpace | VentPerSpc
ThermalEnergyStorageModeScheduleDay | ThrmlEngyStorModeSchDay |  | Project | Hour | Hr |  | NO
|  |  |  | Type | Type
UndergroundFloor | UndgrFlr | Spc |  | AdjacentSpaceReference | AdjacentSpcRef |  | NO |  | Optional | PolyLp | A Floor that separates the Space from underground environment |  |  | Partition
|  |  |  | Area | Area
|  |  |  | Azimuth | Az
|  |  |  | ConstructAssemblyReference | ConsAssmRef
|  |  |  | Name | Name
|  |  |  | PerimeterExposed | PerimExposed
|  |  |  | Status | Status
|  |  |  | Tilt | Tilt
UndergroundWall | UndgrWall | Spc |  | AdjacentSpaceReference | AdjacentSpcRef |  | NO |  | Optional | PolyLp | A Wall that separates the Space from underground environment |  |  | Partition
|  |  |  | Area | Area
|  |  |  | Azimuth | Az
|  |  |  | ConstructAssemblyReference | ConsAssmRef
|  |  |  | Height | Hgt
|  |  |  | Name | Name
|  |  |  | Status | Status
|  |  |  | Tilt | Tilt
Window | Win | ExtWall |  | Area | Area |  | NO |  | Optional | PolyLp | Vertical fenestration installed an opening in an exterior wall. It may be a window, curtain wall, garden window and a door with 50% or more glazing. | 2013 T24 glossary definition: WINDOW is fenestration that is not a skylight and that is an assembled unit consisting of a frame and sash component holding one or more pieces of glazing | unbounded
|  |  |  | EnableWindowShades | EnableWinShades
|  |  |  | FenestrationConstructionReference | FenConsRef
|  |  |  | Height | Hgt
|  |  |  | LeftFinAngle | LeftFinAngle
|  |  |  | LeftFinDepth | LeftFinDepth
|  |  |  | LeftFinDistance | LeftFinDistance
|  |  |  | LeftFinDistanceAbove | LeftFinDistanceAbove
|  |  |  | LeftFinDistanceBelow | LeftFinDistanceBelow
|  |  |  | LeftFinTransmittance | LeftFinTrans
|  |  |  | LeftFinTransmittanceOption | LeftFinTransOption
|  |  |  | LeftFinTransmittanceScheduleReference | LeftFinTransSchRef
|  |  |  | Name | Name
|  |  |  | OverhangAngle | OverhangAngle
|  |  |  | OverhangDepth | OverhangDepth
|  |  |  | OverhangDistance | OverhangDistance
|  |  |  | OverhangLeftExtension | OverhangLeftExtension
|  |  |  | OverhangRightExtension | OverhangRightExtension
|  |  |  | OverhangTransmittance | OverhangTrans
|  |  |  | OverhangTransmittanceOption | OverhangTransOption
|  |  |  | OverhangTransmittanceScheduleReference | OverhangTransmittanceScheduleReference
|  |  |  | RightFinAngle | RightFinAngle
|  |  |  | RightFinDepth | RightFinDepth
|  |  |  | RightFinDistance | RightFinDistance
|  |  |  | RightFinDistanceAbove | RightFinDistanceAbove
|  |  |  | RightFinDistanceBelow | RightFinDistanceBelow
|  |  |  | RightFinTransmittance | RightFinTrans
|  |  |  | RightFinTransmittanceOption | RightFinTransOption
|  |  |  | RightFinTransmittanceScheduleReference | RightFinTransSchRef
|  |  |  | Status | Status
|  |  |  | Width | Wd
|  |  |  | X | X
|  |  |  | Y | Y

## ObjProps
Object | CBECC NR Property | CBECC NR Property Short Form | DataType | Units | Enumerations | CBECC NR Array | XSD ELEMATTRIB minOccurs | XSD ELEMATTRIB maxOccurs | CBECC NR minInclusive | CBECC NR maxInclusive | CBECC NR Different Data Type | Compliance Use | Referenced Objects | XSD Base Type | Definition | Standards Reference | Calculations And Rules
Building
| AboveGradeStoryCount | AboveGrdStoryCnt | integer | none |  |  |  |  | 1 |  |  | Required |  | dtyp:IntegerNonnegative | An attribute of the Building object for recording the number of above grade stories in the building which is used in several rules. | T24/CBC/Nonres Compliance Manual: The total number of stories in the building that have the finished floor surface entirely above the plane of grade or 50% of its volume above grade. Table N2-13 Standard Design HVAC System Selection tests if building has 3 or fewer stories above grade.
| AboveGradeStoryCountAltered | AboveGrdStoryCntAltered | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The number of altered above grade stories in an alterations/additions building which is used in several rules. | 2013 NR ACM
| AboveGradeStoryCountExisting | AboveGrdStoryCntExisting | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The number of existing above grade stories in an alterations/additions building which is used in several rules. | 2013 NR ACM
| AboveGradeStoryCountNew | AboveGrdStoryCntNew | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The number of new above grade stories in an alterations/additions building which is used in several rules. | 2013 NR ACM
| BelowGradeStoryCount | BelowGrdStoryCnt | integer | none
| BuildingAzimuth | BldgAz | decimal | deg arc |  |  |  |  | 0 | 360 |  | Required |  | dtyp:Decimal | the angle between the model Y axis and True North, measured clockwise from the Y Axis in Degrees
| BuildingTerrain | BldgTerrain | enumerated list | none | City; Country; Ocean; Suburbs; Urban | [6 empty] | Optional |  |  | This describes the terrain in which the building is located and has an affect on design day and annual simulations.
| BuildingUniqueID_CEC |  | string | none |  | No | [7 empty] | xsd:string | This token uniquely identifies a whole building, developed by the California Energy Commission.
| CoilCoolingCapacity | CoilClgCap | decimal | Btu per h |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
| CoilCoolingCapacityHydronic | CoilClgCapHydronic | decimal | Btu per h |  | No | [5 empty] | Defaulted |  | dtyp:DecimalNonnegative
| CoilHeatingCapacity | CoilHtgCap | decimal | Btu per h |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
| CoilHeatingCapacityHydronic | CoilHtgCapHydronic | decimal | Btu per h |  | No | [5 empty] | Defaulted |  | dtyp:DecimalNonnegative
| ControlSystemType | CtrlSysType | enumerated list | none | DDCToZoneLevel; NoControlSystem; OtherControlSystem | [9 empty] | This defines what type of control system is used in the building to control energy use. | 2013 NR ACM 5.6.1
| FunctionClassificationMethod | FuncClassMthd | enumerated list | none | AreaCategoryMethod | [6 empty] | Optional |  |  | One of two methods of assigning building occupancy for the project - either complete building or at the space level. This is dependent on whether the user have submitted lighting plans for the whole building or not. | 2013 NR ACM building classification method assigns whole building or space by space occupancy type. 2008 Title 24 Part 6) Tables 146E and 146F) and 2008 NR ACM Tables N2-5, N2-6 and N2-7 - in lighting compliance there are two levels that are similar: the complete buildng or area occupancy.
| HighRiseResidentialLivingUnitCount | HighRiseResLivingUnitCnt | integer | none |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:IntegerNonnegative | The total number of high-rise residential or hotel/motel living units in the building
| HotelMotelGuestRoomCount | HotelMotelGuestRmCnt | integer | none |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:IntegerNonnegative
| LivingUnitCountAltered | LivingUnitCntAltered | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of altered high-rise residential or hotel/motel living units in an alterations/additions building | 2013 2016 NR ACM
| LivingUnitCountExisting | LivingUnitCntExisting | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of existing high-rise residential or hotel/motel living units in an alterations/additions building | 2013 2016 NR ACM
| LivingUnitCountNew | LivingUnitCntNew | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of new high-rise residential or hotel/motel living units in an alterations/additions building | 2013 2016 NR ACM
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| NonresidentialFloorArea | NonResFlrArea | decimal | ft2 |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
| NonresidentialStoryCountElectricHeat | NonResStoryCntElecHt | integer | none | [7 empty] | Optional
| NonresidentialStoryCountFossilHeat | NonResStoryCntFossilHt | integer | none | [7 empty] | Optional
| OccupantFraction | OccFrac | decimal | none |  |  |  |  | 0.5 | 5 |  | Defaulted |  |  | This is the percentage of BuildingTotalGrossFloorArea that is occupied and operational
| PlantCoolingCapacity | PlantClgCap | decimal | Btu per h |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
| PlantHeatingCapacity | PlantHtgCap | decimal | Btu per h |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
| RelocatablePublicSchoolBuilding | RelocPubSchoolBldg | boolean | none | [7 empty] | Optional
| ResidentialFloorArea | ResFlrArea | decimal | ft2 |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
| ResidentialStoryCountElectricHeat | ResStoryCntElecHt | integer | none | [7 empty] | Optional
| ResidentialStoryCountFossilHeat | ResStoryCntFossilHt | integer | none | [7 empty] | Optional
| TopLevelOccupancy |  | enumerated list | none | HotelMotelGuestRoom | [9 empty] | The highest-level definition of building occupancy with a value of Nonresidential or a type of residential facility: highrise, hotel/motel or lowrise ( just called residential) . The value for TopLevelOccupancy is assigned based on the occupancy type that covers teh majority of the space. Residential assignments are also dependent on whether the building is single or multi-family, and how many stories there are in the building. | T24 Section 100 Scope (a) Buildings Covered
| TotalConditionedVolume | TotCondVol | decimal | ft3 |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative
| TotalFloorArea | TotFlrArea | decimal | ft2 |  |  |  |  | 1 |  |  | Defaulted |  |  | BuildlingGrossTotalFloorArea is the gross floor area of the building measured from exterior surface to exterior surface and including all reas inside the building envelope. | 2013 Title 24 Section 140 (c) Calculation of Allowed Indoor Lighting Power Density 1. Complete Building Method involves the entire building which is defined as including all conditioned and unconditioned space which a building permit is sought plus any conditioned and unconditioned space of the existing structure when applying lighting compliance to the complete building. 2013 NR ACM 5.2.2 Baseline Standard Building Classification discusses use of the Complete Building Method
| TotalStoryCount | TotStoryCnt | integer | none |  |  |  |  | 1 |  |  | Required |  | dtyp:IntegerNonnegative | The total number of stories in a building and includes both above grade stories and any below grade stories. | 2013 NR ACM
| TotalStoryCountAltered | TotStoryCntAltered | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of altered stories in an alterations/additions building and includes both above grade stories and any below grade stories. | 2013 NR ACM
| TotalStoryCountExisting | TotStoryCntExisting | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of existing stories in an alterations/additions building and includes both above grade stories and any below grade stories. | 2013 NR ACM
| TotalStoryCountNew | TotStoryCntNew | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of new stories in an alterations/additions building and includes both above grade stories and any below grade stories. | 2013 NR ACM
| TotalUnconditionedFloorArea | TotUncondFlrArea | decimal | ft2 | [7 empty] | NotInput |  |  | All unconditioned floor area in the Building project. It can be derived by summing Zone Floor Area of all Zones with Space Conditioning Type set to Unconditioned | 2008 NR ACM 5.7.1.1: The total floor area of enclosed unconditioned space in the building. Used to describe compliance documentation necessary for additions when meeting the indoor lighting requirements of the Nonresidential Standards.
| WholeBuildingModeled | WholeBldgModeled | boolean | none | [7 empty] | Defaulted |  |  |  | 2013 NR ACM
| WholePlantModeled | WholePlantModeled | boolean | none |  | No | [5 empty] | Defaulted
| Zipcode | Zipcode | string | none | [9 empty] | dtyp:Zipcode
BuildingStory
| FloorToCeilingHeight | FlrToCeilingHgt | decimal | ft | [7 empty] | Required |  |  | The measurement of height from the top surface of the floor to the bottom surface of the ceiling in an enclosed space. | Floor to Ceiling Height measurement is used in several places in the Standards e.g. in Section Section 131 Indoor Lighting Controls That Shall Be Installed, Floor to Ceiling Height is used in calculating skylit daylight areas. | Required when Project:GeometryInputType = 'Simplified', else NotInput
| FloorToFloorHeight | FlrToFlrHgt | decimal | ft | [7 empty] | Required |  |  | The measurement of height from the top surface of the floor to the top surface of the floor in the above story space. | 2013 NR ACM | Required when Project:GeometryInputType = 'Simplified', else NotInput
| Multiplier | Mult | integer | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:IntegerNonnegative | The number of duplicate building stories to be simulated in the model. This value must be consistent with the multipliers for thermal zones and the number of HVAC systems that serve zones on floors with multipliers | 2013 NR ACM sections 2.3.1 and 5.3
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Z | Z | decimal | ft | [7 empty] | CondRequired |  |  | Height above site ground level (negative for below grade stories) | 2013 NR ACM | Required when Project:GeometryInputType = 'Simplified', else NotInput
CartesianPoint
| Coordinate | Coord | decimal | ft |  | Yes | 3 | 3 |  |  |  | Required |  |  | The x, y or z length measured from an origin.
Ceiling
| AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Space |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConstructAssembly
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
ConstructAssembly
| BallastedRoof | BallastedRoof | boolean | none | [7 empty] | Defaulted
| BuiltUpRoof | BuiltUpRoof | boolean | none | [7 empty] | Defaulted
| CompatibleSurfaceType | CompatibleSurfType | enumerated list | none | Ceiling; ExteriorFloor; ExteriorWall; InteriorFloor; InteriorWall; Roof; UndergroundFloor; UndergroundWall | [6 empty] | Required |  |  | Identifies the valid surface object type that the ConstructionAssembly can be assigned to. | None. Used to QC valid object assignments in UI/compliance ruleset.
| ConstructionAssemblyNotes | ConsAssmNotes | string | none | [7 empty] | CondRequired
| CRRCAgedEmittance | CRRCAgedEmit | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated 3-year aged thermal emittance of a roofing material. | NACM-5.5.1, Reflectance
| CRRCAgedReflectance | CRRCAgedRefl | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated 3-year aged solar reflectance of a roofing material. | NACM-5.5.1, Reflectance
| CRRCAgedSRI | CRRCAgedSRI | integer | none | [7 empty] | CondRequired |  |  | The CRRC rated 3-year aged Solar Reflective Index (SRI) of a roofing material.The SRIis a measure defined by the Lawrence Berkeley National Laboratory as the roof's ability to reject solar heat, as shown by a small temperature rise. | 2013 T24 Part 6, 110.8(i)3
| CRRCInitialEmittance | CRRCInitialEmit | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated initial thermal emittance of a roofing material. | NACM-5.5.1, Reflectance
| CRRCInitialReflectance | CRRCInitialRefl | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated initial solar reflectance of a roofing material. | NACM-5.5.1, Reflectance
| CRRCInitialSRI | CRRCInitialSRI | integer | none | [7 empty] | CondRequired |  |  | The CRRC rated initial Solar Reflective Index (SRI) of a roofing material.The SRIis a measure defined by the Lawrence Berkeley National Laboratory as the roof's ability to reject solar heat, as shown by a small temperature rise. | 2013 T24 Part 6, 110.8(i)3
| CRRCProductID | CRRCProdID | string | none | [7 empty] | CondRequired |  |  | The CRRC product identification number for the roofing product
| CRRCSolarReflectanceIndex | CRRCSRI | decimal | none | [7 empty] | Optional
| FieldAppliedCoating | FieldAppliedCoating | boolean | none | [7 empty] | CondRequired |  |  | Defines whether a roof coating is field or factory applied. Required for ACM aged reflectance equation. | NACM-5.5.1, Reflectance
| MaterialReference | MatRef | reference | none |  | Yes | 0 | 10 |  |  |  | CondRequired | Material
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| RoofDensity | RoofDens | boolean | none | [7 empty] | Defaulted
| SlabInsulationOrientation | SlabInsOrientation | enumerated list | none | 12inHorizontal; 12inVertical; 24inHorizontal; 24inVertical; 36inHorizontal; 36inVertical; 48inHorizontal; 48inVertical; FullyInsulatedSlab; None | [6 empty] | Optional |  |  | The location and extent of slab-on-grade floor insulation | 2013 NACM-5.5.9
| SlabInsulationThermalResistance | SlabInsThrmlR | enumerated list | none | R0; R10; R15; R20; R25; R30; R35; R40; R45; R5; R50; R55; R7_5 | [6 empty] | Optional |  |  | The rated R-value of slab-on-grade floor insulation. | 2013 NACM-5.5.9
| SlabType | SlabType | enumerated list | none | [7 empty] | Optional |  |  | The classifications for floors in contact with the ground. | 2013 NACM-5.5.9
DesignDay
| CoincidentWetBulb | CoinWB | decimal | F | [7 empty] | Required |  |  | The wet bulb termperature occuring coincident with a specific dry bulb temperature | 2013 Appendix JA2 Reference Weather/Climate Data has the mean coincident wet bulb termperature for every dry bulb measurement used for cooling calulations
| DesignDryBulb | DsgnDB | decimal | F | [7 empty] | Required |  |  | The design dry bulb temperature is the used for equipment sizing calculations | 2013 T24 Section 140.4 and Joint Appendix 2
| DesignDryBulbRange | DsgnDBRng | decimal | F | [7 empty] | Required |  |  |  | 2013 NR ACM section 5.2.3 Geographic and Climate Data Design Day Data
| Month | Month | integer | none |  |  |  |  | 1 | 12 |  | Required |  |  | Interger value represents the month of the year and therefore is in the range of 1-12
| MonthDay | Day | integer | none |  |  |  |  | 1 | 31 |  | Required |  |  | Integer value represents the day of the month and therefore is in the range of 1-31, with limits on the high end depending on the value for the Month property
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| SkyClearness | SkyClear | decimal | none | [7 empty] | Required |  |  | This is a decmial value denoting the clearness used in the design day simulation
| Type | Type | enumerated list | none | Cooling; Heating | [6 empty] | Required |  |  |  | 2013 NR ACM section 5.2.3 Geographic and Climate Data Design Day Data
| WindDirection | WindDirection | decimal | deg arc | [7 empty] | Required |  |  |  | 2013 NR ACM section 5.2.3 Geographic and Climate Data Weather Data for Simulation
| WindSpeed | WindSpd | decimal | mph | [7 empty] | Required |  |  |  | 2013 NR ACM section 5.2.3 Geographic and Climate Data Weather Data for Simulation
Door
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| DoorConstructionReference | DrConsRef | reference | none | [7 empty] | Optional | DoorConstruction
| Height | Hgt | decimal | ft | [7 empty] | CondRequired |  |  | Measures the vertical extent of a vertical rectangular surface such as a wall or door or a space. Units: feet. | Height is used in the Standards to measure the vertical extent of a building component e.g. Wall, or the vertical distance between two building components e.g. between the ceiling and the roof. | Required when GeometryInpType = Simplified and window shades specified, else NotInput
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Operation | Oper | enumerated list | none | NonSwinging; Swinging | [6 empty] | Optional |  |  | An enumeration with values of swinging and non-swinging. Non-swinging would include sliding doors and roll-up doors.
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Width | Wd | decimal | ft | [7 empty] | CondRequired |  |  | The shorter of the two dimensions of a horizontal rectangular surface or the horizontal extent of a vertical rectangular surface Units: feet | The Standards use length and width interchangeably. For example the Display Perimeter which is the horizontal dimension of a vertical surface is defined as the length of an exterior wall, but the horizontal dimension for window which is also a vertical surface is referred to as width. | Required when GeometryInpType = Simplified and window shades specified, else NotInput
| X | X | decimal | ft | [7 empty] | CondRequired |  |  | A member of a CartesianPoint representing the length along the X axis from the origin. |  | For CBECC-Com nonresidential simulations, this is required when GeometryInpType = Simplified and window shades specified and multiple windows or doors, else NotInput
| Y | Y | decimal | ft | [7 empty] | CondRequired |  |  | A member of a CartesianPoint representing the length along the Y axis from the origin. |  | For CBECC-Com nonresidential simulations, this is required when GeometryInpType = Simplified and window shades specified and multiple windows or doors, else NotInput
DoorConstruction
| CertificationMethod | CertificationMthd | enumerated list | none | CECDefaultPerformance_Door; NFRCRated_Door | [6 empty] | Required
| DoorAutomaticCloser | DrAutoCloser | boolean | none |  | No | [5 empty] | Defaulted
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Open | Open | enumerated list | none | NonSwinging; Swinging | [6 empty] | Optional |  |  | An enumeration with values of swinging and non-swinging. Non-swinging would include sliding doors and roll-up doors. | Title 24 Table 143-A/B and C assign U-Factor based on whether the door is swinging or non swinging. 2013 NR ACM Maps to Door Type with same two values of swinging and non-swinging.
| Type | Type | enumerated list | none | InsulatedSingleLayerSectionalMetal; InsulatedSwingingMetal; UninsulatedDoubleLayerMetal; UninsulatedSingleLayerMetal; UninsulatedSingleLayerRollupMetal; WoodOther; WoodThick | [6 empty] | Required |  |  |  | 2013 Joint Appendix JA4 Table 4.5.1 Opaque Doors
| UFactor | UFactor | decimal | Btu per h ft2 F | [7 empty] | Optional |  | dtyp:Decimal3Places | The overall coefficient of thermal transmittance through a layer or construction assembly. It includes air film resistance at both surfaces. | T24 Part 6 definition: U-FACTOR is the overall coefficient of thermal transmittance of a construction assembly, in Btu/(hr x ft² x ºF). Used in table 143 and JA 4 tables of construction assemblies
ExteriorFloor
| AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Space |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConstructAssembly
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
ExteriorWall
| AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Space |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConstructAssembly
| DisplayPerimeter | DisplayPerim | decimal | ft | [7 empty] | Optional |  |  | The length of an exterior wall in a building of CBC Occupancy Group B; F Div1, or M, that immediately abuts a public sidewalk, measured at the sidewalk level for each story that abuts a public sidewalk. It can be derived using the CBC Occupancy type and the Width dimension of the Exterior Wall. | T24 definition: DISPLAY PERIMETER is the length of an exterior wall in a building of CBC Occupancy Group B; F Div1, or M, that immediately abuts a public sidewalk, measured at the sidewalk level for each story that abuts a public sidewalk.
| Height | Hgt | decimal | ft | [7 empty] | CondRequired |  |  | Measures the vertical extent of a vertical rectangular surface such as a wall or door or a space. Units: feet. | Height is used in the Standards to measure the vertical extent of a building component e.g. Wall, or the vertical distance between two building components e.g. between the ceiling and the roof. | Required when GeometryInpType = Simplified and window shades specified, else NotInput
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Width | Wd | decimal | ft | [7 empty] | CondRequired |  |  | The shorter of the two dimensions of a horizontal rectangular surface or the horizontal extent of a vertical rectangular surface Units: feet | The Standards use length and width interchangeably. For example the Display Perimeter which is the horizontal dimension of a vertical surface is defined as the length of an exterior wall, but the horizontal dimension for window which is also a vertical surface is referred to as width. | Required when GeometryInpType = Simplified and window shades specified, else NotInput
ExternalShadingObject
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| SolarReflectance | SolRefl | decimal | none | [7 empty] | Optional |  |  | From E+ Input/Output Ref:The diffuse solar reflectance of the unglazed part of the shading surface (default = 0.2). This reflectance is assumed to be the same for beam-to-diffuse and diffuse-to-diffuse reflection. Beam-to-diffuse reflection is assumed to be independent of angle of incidence of beam radiation. Diffuse-to-diffuse reflection is assumed to be independent of angular distribution of the incident of diffuse radiation. The outgoing diffuse radiation is assumed to be isotropic (hemispherically uniform). The sum of this reflectance and the shading surface transmittance should be less than or equal to 1.0. | 2013 NR ACM 5.5.7
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Transmittance | Trans | decimal | none | [7 empty] | Optional
| TransmittanceOption | TransOption | enumerated list | none | Constant; Scheduled | [6 empty] | Defaulted
| TransmittanceScheduleReference | TransSchRef | reference | none | [7 empty] | Optional | Schedule |  | A schedule of type Fraction which defines the hourly transmittance of the shading object. | 2013 NR ACM 5.5.7
| VisibleReflectance | VisRefl | decimal | none | [7 empty] | Optional |  |  | From E+ Input/Output Ref:The diffuse visible reflectance of the unglazed part of the shading surface (default = 0.2). This reflectance is assumed to be the same for beam-to-diffuse and diffuse-to-diffuse reflection. Beam-to-diffuse reflection is assumed to be independent of angle of incidence of beam radiation. Diffuse-to-diffuse reflection is assumed to be independent of angular distribution of the incident of diffuse radiation. The outgoing diffuse radiation is assumed to be isotropic (hemispherically uniform). This value if used only for the daylighting calculation (ref: Daylighting:Controls). The sum of this reflectance and the shading surface transmittance should be less than or equal to 1.0. | 2013 NR ACM 5.5.7
| WindowReference | WinRef | reference | none |  | No | [5 empty] | Optional | Window
FenestrationConstruction
| AssemblyContext | AssmContext | enumerated list | none | FieldFabricated; Manufactured; SiteBuilt | [6 empty] | CondRequired |  |  | The context in which a building element was assembled for installation. | An example of how Assembly Context affects how rule targets are assigned: Title 24 Part 6 Section 116 – Mandatory Requirements For Fenestration Products And Exterior Doors are different for fenestration that os site built, manufactured or field fabricated.
| CertificationMethod | CertificationMthd | enumerated list | none | CECDefaultPerformance; COGEquations; NFRCRated | [6 empty] | Required
| Diffusing | Diffusing | boolean | none | [7 empty] | Optional
| DynamicGlazing | DynamicGlz | boolean | none | [7 empty] | Required
| FenestrationFraming | FenFrm | enumerated list | none | [7 empty] | CondRequired |  |  | The type of frame used for a fenestration product defined in the CBECC NR input data model text file.
| FenestrationPanes | FenPanes | enumerated list | none | DoublePane; GlassBlock; SinglePane; TranslucentOrTransparentPanel | [6 empty] | CondRequired
| FenestrationProductType | FenProdType | enumerated list | none | CurtainWall; FixedWindow; GlazedDoor; NotApplicable; OperableWindow; Skylight | [6 empty] | CondRequired
| FenestrationType | FenType | enumerated list | none | Skylight; VerticalFenestration | [6 empty] | Required
| GlazingTint | GlzTint | enumerated list | none | ClearGlazing; TintedGlazing | [6 empty] | CondRequired |  |  | Has values of clear and tinted and is used in assigning mandatory default SHGC values. | Glazing Tint is used to establish Solar Heat Gain Coefficient of fenestration products. Specifically Table 116-B assigns SHGC dependent on Glazing Tint value. 2013 NR ACM Glazing Tint is only mentioned in section on Switchable glazing which describes a technology of applying an electric current to liquid crystal windows to darken the window simulating a tint.
| GreenhouseGardenWindow | GreenhouseGardenWin | boolean | none | [7 empty] | CondRequired |  |  | Used in selection of default properties
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| OperableWindowConfiguration | OperableWinConfiguration | enumerated list | none | CasementAwning; Sliding | [6 empty] | CondRequired |  |  | Used in selection of Table NA-6 properties
| ShadingCredit | ShdgCred | boolean | none | [7 empty] | Required
| SHGC | SHGC | decimal | none | [7 empty] | CondRequired |  |  | The ratio of the solar heat gain entering a space, through the subject fenestration product, to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation which is then re-radiated, conducted or convected into the space. often referred to as SHGC. | SOLAR HEAT GAIN COEFFICIENT (SHGC) is the ratio of the solar heat gain entering the space through the fenestration area to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation, which is then re-radiated, conducted, or convected into the space. 2013 NR ACM Fenestration Construction includes Solar Heat Gain Coefficient as an attribute.
| SHGCCenterOfGlass | SHGCCOG | decimal | none | [7 empty] | CondRequired |  |  | The ratio of the solar heat gain entering a space, through the subject fenestration product, to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation which is then re-radiated, conducted or convected into the space. often referred to as SHGC.
| SkylightCurb | SkyltCurb | enumerated list | none | CurbMounted; DeckMounted | [6 empty] | CondRequired |  |  | Curb or No Curb. For selection of NA-6 properties | Tables 143 A/B assign U Factor dependent on whether the skylight is mounted on a curb or directly on the roof. 2013 NR ACM Fenestration Type (Skylights) includes whether the skylight has a curb or not. 2013 Title 24 Part 6 Table NA6-5
| SkylightGlazing | SkyltGlz | enumerated list | none | Glass; Plastic | [6 empty] | CondRequired |  |  | Used in selection of baseline properties
| UFactor | UFactor | decimal | Btu per h ft2 F |  |  |  |  | 0 | 2.5 |  | CondRequired |  |  | The overall coefficient of thermal transmittance through a layer or construction assembly. It includes air film resistance at both surfaces. | T24 Part 6 definition: U-FACTOR is the overall coefficient of thermal transmittance of a construction assembly, in Btu/(hr x ft² x ºF). Used in table 143 and JA 4 tables of construction assemblies
| UFactorCenterOfGlass | UFactorCOG | decimal | Btu per h ft2 F | [7 empty] | CondRequired |  |  | The overall coefficient of thermal transmittance through glass of a fenestration product.
| VisibleTransmittance | VT | decimal | none | [7 empty] | CondRequired |  |  | The fraction of incident visible radiation that is transmitted by the material. Visible radiation includes only a sub-range of solar radiation and excludes infrared and ultraviolet wavelengths. | 2088 NR ACM only refers to VT in the section5, Reference Method Comparison Tests. Title 24 part 6 has only a definition for the term but never explicitly applies it. 2013 NR ACM Table 50 – Baseline Building Criteria for Vertical Glazing for 90.1 2001 referred to as VT.
| VisibleTransmittanceCenterOfGlass | VTCOG | decimal | none | [7 empty] | CondRequired |  |  | The fraction of incident visible radiation that is transmitted by the material. Visible radiation includes only a sub-range of solar radiation and excludes infrared and ultraviolet wavelengths. | 2088 NR ACM only refers to VT in the section5, Reference Method Comparison Tests. Title 24 part 6 has only a definition for the term but never explicitly applies it. 2013 NR ACM Table 50 – Baseline Building Criteria for Vertical Glazing for 90.1 2001 referred to as VT.
| WindowDivider | WinDivider | enumerated list | none | DividerBetwnPanesGreaterThanOrEqualTo7_16in; DividerBetwnPanesLessThan7_16in; NoDivider; NotApplicable; TrueDividedLite | [6 empty] | CondRequired |  |  | Used in selection of default properties
Holiday
| Day | Day | integer | none | [7 empty] | Optional |  |  | Interger value represents the day of the month and therefore is in the range of 1-31, with limits on the high end depending on the value for the Month property
| DayOfWeek | DayOfWeek | enumerated list | none | Friday; Monday; Saturday; Sunday; Thursday; Tuesday; Wednesday | [6 empty] | Optional
| Month | Month | enumerated list | none | April; August; December; February; January; July; June; March; May; November; October; September | [6 empty] | Required
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| SpecificationMethod | SpecMthd | enumerated list | none | Date; First; Fourth; Last; Second; Third | [6 empty] | Required
InteriorFloor
| AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Space |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConstructAssembly
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
InteriorLightingSystem
| AllowanceArea | AllowArea | decimal | ft2 | [7 empty] | Defaulted
| AllowanceLength | AllowLen | decimal | ft | [7 empty] | Defaulted |  |  | Linear width of white/chalk board associated with AreaCategoryMethodAllowanceType of WhiteOrChalkBoard used to calculate power allowance. | 2013 Draft T24 140.6(c)2.G and Table 140.6-C
| AllowanceQuantity | AllowQty | decimal | none | [7 empty] | Defaulted
| AllowanceType | AllowType | enumerated list | none | AccentDisplayFeature; Decorative; Ornamental; ParkingGarageATMLighting; PrecisionCommercialIndustrial; SpecializedLabTaskWork; SpecializedTaskWork; TailoredFloorDisplayAllowance; TailoredOrnamentalAndSpecialEffectAllowance; TailoredTaskAllowance; TailoredVeryValuableDisplayCaseAllowance; TailoredWallDisplayAllowance; VideoConferencingStudioLighting; WhiteOrChalkBoard | [6 empty] | Defaulted |  |  | Combines AreaCategory and TailoredMethod Allowance Types Enums into a single enumerated list
| DaylitAreaType | DaylitAreaType | enumerated list | none | PrimarySidelit; SecondarySidelit; SkylitDaylit | [6 empty] | Defaulted |  |  | Defines whether the daylighting control area is under a skylight or next to a window or some distance from a window | 2013 NR ACM 5.4.5
| IsAcceptanceTestRequiredReport | IsAcceptanceTestReqdRpt | boolean | none | [7 empty] | Defaulted
| LightingControlCountReport | LtgCtrlCntRpt | boolean | none | [7 empty] | Defaulted
| LuminaireCount | LumCnt | integer | none |  | Yes | 0 | 5 |  |  | decimal | Defaulted |  | dtyp:IntegerNonnegative | Array of the count of upto 5 different types of luminaires
| LuminaireMountingHeight | LumMntgHgt | decimal | ft | [7 empty] | Defaulted |  |  | Distance from the finished floor to the bottom of the luminaire | 2013 Title 24 part 6 140.6(c)3 Table 140.6-E, NRCCLTI01E
| LuminaireReference | LumRef | reference | none |  | Yes | 0 | 5 |  |  |  | Optional | Luminaire |  | Reference to a luminaire object
| LuminaireStatus | LumStatus | enumerated list | none | Altered; Existing; Future; New | Yes | 0 | 5 |  |  |  | Defaulted |  |  | Defines if a construction or equipment is new, existing, modified, removed. Standards such as efficiency standards may not apply if a construction or equipment in a project is existing. equipment may be moved and reinstalled in the project.
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| NonRegulatedExclusion | NonRegExclusion | enumerated list | none | ATMLighting; CBCRequiredExitSign; CBCRequiredExitwayOrEgressNormallyOff; DanceFloorOrTheatrical; ElevatorLighting; ExamSurgicalNightOrEquipmentIntegratedInMedicalOrClinical; FilmOrPhotoStudioLightingSeparatelySwitched; HighRiseResidentialDwellingUnit; HistoricBuilding; HotelMotelGuestRoom; LightingDemonstrationEquipInLightingEducationFacilities; LightingEquipmentForSale; ManufacturerInstalledInFreezerVendingFoodPrepScientificOrIndEquip; PlantGrowthOrMaintWithMultiLevelAstroTimer; SignageLighting; SmallAgriculturalBuilding; SmallNonresidentialParkingGarage; SmallRefrigeratedCases; SmallUnconditionedAgriculturalBuilding; TemporaryExhibitSeparatelySwitchedInCivicTransConvOrHotel; TemporaryLightingSystems; ThemeParksThemeAndSpecialEffects | [6 empty] | CondRequired |  |  | Category allowing exclusion of interior lighting system power from regulated amount. | 2013 NR ACM Draft Sec.140.6(a)3 | Required when IntLtgSys:PwrReg = 0, else NotInput
| PowerRegulated | PwrReg | boolean | none | [7 empty] | Defaulted |  |  | Boolean flag regarding Regulated vs. Non-Regulated power for an interior lighting system. Defaults to TRUE=Regulated.
| VeryValuableDisplayDescription | VeryValDispDesc | string | none | [7 empty] | Optional |  |  |  | NRCCLTI01E
| WorkPlaneHeight | WorkPlaneHgt | decimal | ft | [7 empty] | Defaulted |  |  | Distance from the finished floor to the work plane. Used to calculate vertical distance from the work plane to the centerline of the lighting fixture | 2013 Title 24 part 6 Table 140.6-F
InteriorWall
| AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Space |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConstructAssembly
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Luminaire
| FixtureType | FxtrType | enumerated list | none | NotInCeiling; RecessedOrDownlight; RecessedWithLens | [6 empty] | Optional |  |  | Enumeration type for determining luminaire heat gain distribution
| HeatGainRadiantFraction | HtGnRadFrac | decimal | none |  |  |  |  | 0 | 1 |  | Required |  |  | Fraction of luminaire radiant heat gain going to space surfaces | 2013 Draft ACM Sec.5.4.3 Table 18
| HeatGainSpaceFraction | HtGnSpcFrac | decimal | none |  |  |  |  | 0 | 1 |  | Required |  |  | Fraction of luminaire heat gain going to space air. | 2013 Draft ACM Sec.5.4.3 Table 18
| LampType | LampType | enumerated list | none | CFL; HighPressureSodium; Incandescent; LED; LinearFluorescent; MercuryVapor; MetalHalide | [6 empty] | Optional |  |  | Enumeration type for determining luminaire heat gain distribution
| LuminaireDescriptionReport | LumDescRpt | string | none | [7 empty] | Optional
| LuminaireMountingHeight | LumMntgHgt | decimal | ft | [7 empty] | Defaulted |  |  | Distance from the finished floor to the bottom of the luminaire | 2013 Title 24 part 6 140.6(c)3 Table 140.6-E, NRCCLTI01E
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Power | Pwr | decimal | W |  |  |  |  | 0 |  |  | Compulsory |  | dtyp:DecimalNonnegative |  | NRCCLTI01E
| PowerNA8Default | PwrNA8Default | boolean | none | [7 empty] | Defaulted
Material
| CavityInsulation | CavityIns | decimal | h ft2 F per Btu | [7 empty] | CondRequired |  |  | The rated cavity insulation R-value of a CodeCategory = Composite material layer. The rated R-value should reflect the specified FramingDepth, including any reduction in R-vaue due to over-compression of cavity insulation materials. | 2012 JA4
| CavityInsulationOption | CavityInsOpt | enumerated list | none | R0; R10; R10_R13; R11; R13; R13_R13; R15; R16; R19; R19_R13; R20; R21; R22; R23; R24_CavNR; R25; R26; R29; R30; R32; R35; R36; R38; R5; R6; R6_R13 | [6 empty] | CondRequired
| CodeCategory | CodeCat | enumerated list | none | Air; BuildingBoardAndSiding; BuildingMembrane; Composite; Concrete; ConcreteSandwichPanel; FinishMaterials; ICFWall; InsulationBatt; InsulationBoard; InsulationLooseFill; InsulationSprayApplied; MasonryMaterials; MasonryUnitsFill; MasonryUnitsHollow; MasonryUnitsSolid; MetalInsulatedPanelWall; PlasteringMaterials; Roofing; SIPSFloor; SIPSRoof; SIPSWall; StrawBaleWall; Wood | [6 empty] | Compulsory |  |  | The name or code for a type of material used as a layer in construction assemblies. Used by the compliance software user interface to narrow list of material selections by category. | Joint Appendix 4 tables describe construction assemblies that are combinations of materials. It does not use the layer approach. 2013 NR ACM Material Type is used in Appendix of Default Construction Materials.
| CodeItem | CodeItem | enumerated list | none | AcousticTile0_375In; AcousticTile0_5In; AcousticTile0_75In; Aggregate45LbPerFt3Thickness0_5In; Aggregate45LbPerFt3Thickness0_625In; AggregateOnMetalLath45LbPerFt3Thickness0_75In; AggregatePerliteOnMetalLathThickness0_75In; AggregatePerliteThickness0_5In; AggregatePerliteThickness0_625In; AirCavityWallRoofCeiling4InPlus; AirCeiling0_5In; AirCeiling0_75In; AirCeiling1_5In; AirCeiling3_5In; AirFloor0_5In; AirFloor0_75In; AirFloor1_5In; AirFloor3_5In; AirMetalWallFraming16Or24InOC; AirRoof0_5In; AirRoof0_75In; AirRoof1_5In; AirRoof3_5In; AirWall0_5In; AirWall0_75In; AirWall1_5In; AirWall3_5In; AluminumNoThermalBreakDoubleNoLowENoIns; AluminumNoThermalBreakDoubleNoLowER10Ins; AluminumNoThermalBreakDoubleNoLowER15Ins; AluminumNoThermalBreakDoubleNoLowER20Ins; AluminumNoThermalBreakDoubleNoLowER25Ins; AluminumNoThermalBreakDoubleNoLowER30Ins; AluminumNoThermalBreakDoubleNoLowER4Ins; AluminumNoThermalBreakDoubleNoLowER7Ins; AluminumNoThermalBreakSingleGlassStoneMetalNoIns; AluminumNoThermalBreakSingleGlassStoneMetalR10Ins; AluminumNoThermalBreakSingleGlassStoneMetalR15Ins; AluminumNoThermalBreakSingleGlassStoneMetalR20Ins; AluminumNoThermalBreakSingleGlassStoneMetalR25Ins; AluminumNoThermalBreakSingleGlassStoneMetalR30Ins; AluminumNoThermalBreakSingleGlassStoneMetalR4Ins; AluminumNoThermalBreakSingleGlassStoneMetalR7Ins; AluminumNoThermalBreakTripleOrLowENoIns; AluminumNoThermalBreakTripleOrLowER10Ins; AluminumNoThermalBreakTripleOrLowER15Ins; AluminumNoThermalBreakTripleOrLowER20Ins; AluminumNoThermalBreakTripleOrLowER25Ins; AluminumNoThermalBreakTripleOrLowER30Ins; AluminumNoThermalBreakTripleOrLowER4Ins; AluminumNoThermalBreakTripleOrLowER7Ins; AluminumThermalBreakDoubleNoLowENoIns; AluminumThermalBreakDoubleNoLowER10Ins; AluminumThermalBreakDoubleNoLowER15Ins; AluminumThermalBreakDoubleNoLowER20Ins; AluminumThermalBreakDoubleNoLowER25Ins; AluminumThermalBreakDoubleNoLowER30Ins; AluminumThermalBreakDoubleNoLowER4Ins; AluminumThermalBreakDoubleNoLowER7Ins; AluminumThermalBreakSingleGlassStoneMetalNoIns; AluminumThermalBreakSingleGlassStoneMetalR10Ins; AluminumThermalBreakSingleGlassStoneMetalR15Ins; AluminumThermalBreakSingleGlassStoneMetalR20Ins; AluminumThermalBreakSingleGlassStoneMetalR25Ins; AluminumThermalBreakSingleGlassStoneMetalR30Ins; AluminumThermalBreakSingleGlassStoneMetalR4Ins; AluminumThermalBreakSingleGlassStoneMetalR7Ins; AluminumThermalBreakTripleOrLowENoIns; AluminumThermalBreakTripleOrLowER10Ins; AluminumThermalBreakTripleOrLowER15Ins; AluminumThermalBreakTripleOrLowER20Ins; AluminumThermalBreakTripleOrLowER25Ins; AluminumThermalBreakTripleOrLowER30Ins; AluminumThermalBreakTripleOrLowER4Ins; AluminumThermalBreakTripleOrLowER7Ins; AsbestosOrCementShingles0_375In; Ash1In; AsphaltBitumenInertFill100LbPerFt3Thickness0_75In; AsphaltBitumenInertFill144LbPerFt3Thickness0_75In; Birch1In; Brick48LbPerFt3Thickness3_625In; BrickFiredClay140LbPerFt3Thickness3_625In; BuildingPaper0_0625In; BuiltUpRoofing0_375In; CaliforniaRedwood1In; Carpet0_75In; CellularPolyisocyanurate0_125In_R0_7; CellularPolyisocyanurate0_25In_R1_5; CellularPolyisocyanurate0_5In_R2_9; CellularPolyisocyanurate1In_R5_9; CellularPolyisocyanurate1_5In_R8_8; CellularPolyisocyanurate2In_R12; CellularPolyisocyanurate2_5In_R15; CellularPolyisocyanurate3In_R18; CellularPolyisocyanurate3_5In_R21; CellularPolyisocyanurate4In_R23; CellularPolyisocyanurate4_5In_R26; CellularPolyisocyanurate5In_R29; CellularPolyisocyanurate5_5In_R32; CellularPolyisocyanurate6In_R35; CellularPolyisocyanurate6_5In_R38; ClayPartGrouted130LbPerFt3Thickness6In; ClayPartGrouted130LbPerFt3Thickness8In; ClayPartGroutedInsulated130LbPerFt3Thickness6In; ClayPartGroutedInsulated130LbPerFt3Thickness8In; ClaySolidGrout130LbPerFt3Thickness6In; ClaySolidGrout130LbPerFt3Thickness8In; ClayTile0_5In; ClayTileHollow1CellDeepThickness3In; ClayTileHollow1CellDeepThickness4In; ClayTileHollow2CellDeepThickness10In; ClayTileHollow2CellDeepThickness6In; ClayTileHollow2CellDeepThickness8In; ClayTileHollow3CellDeepThickness12In; ClayTilePaver; ComplianceInsulationR0_01; ComplianceInsulationR0_02; ComplianceInsulationR0_10; ComplianceInsulationR0_20; ComplianceInsulationR0_50; ComplianceInsulationR10_00; ComplianceInsulationR10_06; ComplianceInsulationR11_00; ComplianceInsulationR11_70; ComplianceInsulationR12_00; ComplianceInsulationR12_50; ComplianceInsulationR12_55; ComplianceInsulationR12_69; ComplianceInsulationR13_00; ComplianceInsulationR13_50; ComplianceInsulationR13_99; ComplianceInsulationR14_00; ComplianceInsulationR14_14; ComplianceInsulationR14_32; ComplianceInsulationR14_60; ComplianceInsulationR15_00; ComplianceInsulationR15_54; ComplianceInsulationR16_00; ComplianceInsulationR16_20; ComplianceInsulationR16_34; ComplianceInsulationR16_58; ComplianceInsulationR16_69; ComplianceInsulationR17_00; ComplianceInsulationR17_67; ComplianceInsulationR18_00; ComplianceInsulationR19_00; ComplianceInsulationR19_63; ComplianceInsulationR1_00; ComplianceInsulationR1_35; ComplianceInsulationR1_41; ComplianceInsulationR1_54; ComplianceInsulationR20_00; ComplianceInsulationR20_05; ComplianceInsulationR21_00; ComplianceInsulationR21_18; ComplianceInsulationR21_39; ComplianceInsulationR21_60; ComplianceInsulationR22_00; ComplianceInsulationR22_48; ComplianceInsulationR23_00; ComplianceInsulationR23_70; ComplianceInsulationR24_00; ComplianceInsulationR24_80; ComplianceInsulationR24_86; ComplianceInsulationR25_00; ComplianceInsulationR25_16; ComplianceInsulationR26_00; ComplianceInsulationR27_00; ComplianceInsulationR28_00; ComplianceInsulationR28_12; ComplianceInsulationR28_63; ComplianceInsulationR29_00; ComplianceInsulationR2_00; ComplianceInsulationR2_15; ComplianceInsulationR2_19; ComplianceInsulationR2_85; ComplianceInsulationR2_89; ComplianceInsulationR30_00; ComplianceInsulationR31_00; ComplianceInsulationR32_00; ComplianceInsulationR33_00; ComplianceInsulationR34_00; ComplianceInsulationR34_93; ComplianceInsulationR35_00; ComplianceInsulationR36_00; ComplianceInsulationR37_00; ComplianceInsulationR38_00; ComplianceInsulationR3_00; ComplianceInsulationR3_63; ComplianceInsulationR3_70; ComplianceInsulationR3_80; ComplianceInsulationR4_00; ComplianceInsulationR5_00; ComplianceInsulationR5_60; ComplianceInsulationR6_00; ComplianceInsulationR6_32; ComplianceInsulationR6_46; ComplianceInsulationR7_00; ComplianceInsulationR7_10; ComplianceInsulationR7_18; ComplianceInsulationR7_39; ComplianceInsulationR7_50; ComplianceInsulationR7_60; ComplianceInsulationR8_00; ComplianceInsulationR8_07; ComplianceInsulationR9_00; ComplianceInsulationR9_40; ComplianceInsulationR9_80; ComplianceInsulationR9_83; ComplianceInsulationR9_94; Concrete100LbPerFt3Thickness10In; Concrete100LbPerFt3Thickness12In; Concrete100LbPerFt3Thickness2In; Concrete100LbPerFt3Thickness4In; Concrete100LbPerFt3Thickness6In; Concrete100LbPerFt3Thickness8In; Concrete140LbPerFt3Thickness10In; Concrete140LbPerFt3Thickness12In; Concrete140LbPerFt3Thickness2In; Concrete140LbPerFt3Thickness4In; Concrete140LbPerFt3Thickness6In; Concrete140LbPerFt3Thickness8In; Concrete80LbPerFt3Thickness10In; Concrete80LbPerFt3Thickness12In; Concrete80LbPerFt3Thickness2In; Concrete80LbPerFt3Thickness4In; Concrete80LbPerFt3Thickness6In; Concrete80LbPerFt3Thickness8In; ConcretePartGrouted105LbPerFt3Thickness10In; ConcretePartGrouted105LbPerFt3Thickness12In; ConcretePartGrouted105LbPerFt3Thickness6In; ConcretePartGrouted105LbPerFt3Thickness8In; ConcretePartGrouted115LbPerFt3Thickness10In; ConcretePartGrouted115LbPerFt3Thickness12In; ConcretePartGrouted115LbPerFt3Thickness6In; ConcretePartGrouted115LbPerFt3Thickness8In; ConcretePartGrouted125LbPerFt3Thickness10In; ConcretePartGrouted125LbPerFt3Thickness12In; ConcretePartGrouted125LbPerFt3Thickness6In; ConcretePartGrouted125LbPerFt3Thickness8In; ConcretePartGroutedInsulated105LbPerFt3Thickness10In; ConcretePartGroutedInsulated105LbPerFt3Thickness12In; ConcretePartGroutedInsulated105LbPerFt3Thickness6In; ConcretePartGroutedInsulated105LbPerFt3Thickness8In; ConcretePartGroutedInsulated115LbPerFt3Thickness10In; ConcretePartGroutedInsulated115LbPerFt3Thickness12In; ConcretePartGroutedInsulated115LbPerFt3Thickness6In; ConcretePartGroutedInsulated115LbPerFt3Thickness8In; ConcretePartGroutedInsulated125LbPerFt3Thickness10In; ConcretePartGroutedInsulated125LbPerFt3Thickness12In; ConcretePartGroutedInsulated125LbPerFt3Thickness6In; ConcretePartGroutedInsulated125LbPerFt3Thickness8In; ConcreteSandAggregateThickness6In; ConcreteSandwichPanel100PercentInsulationNoSteelInsulation1_5In; ConcreteSandwichPanel100PercentInsulationNoSteelInsulation2In; ConcreteSandwichPanel100PercentInsulationNoSteelInsulation3In; ConcreteSandwichPanel100PercentInsulationNoSteelInsulation4In; ConcreteSandwichPanel100PercentInsulationNoSteelInsulation6In; ConcreteSandwichPanel100PercentInsulationSteelInsulation1_5In; ConcreteSandwichPanel100PercentInsulationSteelInsulation2In; ConcreteSandwichPanel100PercentInsulationSteelInsulation3In; ConcreteSandwichPanel100PercentInsulationSteelInsulation4In; ConcreteSandwichPanel100PercentInsulationSteelInsulation6In; ConcreteSandwichPanel80PercentInsulationNoSteelInsulation1_5In; ConcreteSandwichPanel80PercentInsulationNoSteelInsulation2In; ConcreteSandwichPanel80PercentInsulationNoSteelInsulation3In; ConcreteSandwichPanel80PercentInsulationNoSteelInsulation4In; ConcreteSandwichPanel80PercentInsulationNoSteelInsulation6In; ConcreteSandwichPanel80PercentInsulationSteelInsulation1_5In; ConcreteSandwichPanel80PercentInsulationSteelInsulation2In; ConcreteSandwichPanel80PercentInsulationSteelInsulation3In; ConcreteSandwichPanel80PercentInsulationSteelInsulation4In; ConcreteSandwichPanel80PercentInsulationSteelInsulation6In; ConcreteSandwichPanel90PercentInsulationNoSteelInsulation1_5In; ConcreteSandwichPanel90PercentInsulationNoSteelInsulation2In; ConcreteSandwichPanel90PercentInsulationNoSteelInsulation3In; ConcreteSandwichPanel90PercentInsulationNoSteelInsulation4In; ConcreteSandwichPanel90PercentInsulationNoSteelInsulation6In; ConcreteSandwichPanel90PercentInsulationSteelInsulation1_5In; ConcreteSandwichPanel90PercentInsulationSteelInsulation2In; ConcreteSandwichPanel90PercentInsulationSteelInsulation3In; ConcreteSandwichPanel90PercentInsulationSteelInsulation4In; ConcreteSandwichPanel90PercentInsulationSteelInsulation6In; ConcreteSolidGrout105LbPerFt3Thickness10In; ConcreteSolidGrout105LbPerFt3Thickness12In; ConcreteSolidGrout105LbPerFt3Thickness6In; ConcreteSolidGrout105LbPerFt3Thickness8In; ConcreteSolidGrout115LbPerFt3Thickness10In; ConcreteSolidGrout115LbPerFt3Thickness12In; ConcreteSolidGrout115LbPerFt3Thickness6In; ConcreteSolidGrout115LbPerFt3Thickness8In; ConcreteSolidGrout125LbPerFt3Thickness10In; ConcreteSolidGrout125LbPerFt3Thickness12In; ConcreteSolidGrout125LbPerFt3Thickness6In; ConcreteSolidGrout125LbPerFt3Thickness8In; Concrete_Paver; ContinuousInsulationDoubleNoLowENoIns; ContinuousInsulationDoubleNoLowER10Ins; ContinuousInsulationDoubleNoLowER15Ins; ContinuousInsulationDoubleNoLowER20Ins; ContinuousInsulationDoubleNoLowER25Ins; ContinuousInsulationDoubleNoLowER30Ins; ContinuousInsulationDoubleNoLowER4Ins; ContinuousInsulationDoubleNoLowER7Ins; ContinuousInsulationSingleGlassStoneMetalNoIns; ContinuousInsulationSingleGlassStoneMetalR10Ins; ContinuousInsulationSingleGlassStoneMetalR15Ins; ContinuousInsulationSingleGlassStoneMetalR20Ins; ContinuousInsulationSingleGlassStoneMetalR25Ins; ContinuousInsulationSingleGlassStoneMetalR30Ins; ContinuousInsulationSingleGlassStoneMetalR4Ins; ContinuousInsulationSingleGlassStoneMetalR7Ins; ContinuousInsulationTripleOrLowENoIns; ContinuousInsulationTripleOrLowER10Ins; ContinuousInsulationTripleOrLowER15Ins; ContinuousInsulationTripleOrLowER20Ins; ContinuousInsulationTripleOrLowER25Ins; ContinuousInsulationTripleOrLowER30Ins; ContinuousInsulationTripleOrLowER4Ins; ContinuousInsulationTripleOrLowER7Ins; DouglasFirLarch1In; ExpandedPerliteOrganicBonded0_75In_R2_1; ExpandedPerliteOrganicBonded1In_R2_8; ExpandedPerliteOrganicBonded1_5In_R4_2; ExpandedPerliteOrganicBonded2In_R5_6; ExpandedPerliteOrganicBonded3In_R8_3; ExpandedPerliteOrganicBonded4In_R11; ExpandedPerliteOrganicBonded6In_R17; ExpandedPolystyrene0_25In_R1; ExpandedPolystyrene0_5In_R2_1; ExpandedPolystyrene0_75In_R3_1; ExpandedPolystyrene1In_R4_2; ExpandedPolystyrene1_25In_R5_2; ExpandedPolystyrene1_5In_R6_3; ExpandedPolystyrene1_75In_R7_3; ExpandedPolystyrene1_875In_R8; ExpandedPolystyrene1_9375In_R8_1; ExpandedPolystyrene2In_R8_3; ExpandedPolystyrene2_4375In_R10; ExpandedPolystyrene2_4In_R10; ExpandedPolystyrene3In_ R13; ExpandedPolystyrene3_3333In_R14; ExpandedPolystyrene3_4In_R14; ExpandedPolystyrene3_5In_R15; ExpandedPolystyrene4_0625In_R17; ExpandedPolystyrene4_7In_R20; ExpandedPolystyrene5_4In_R22; ExpandedPolystyrene5_95In_R25; ExpandedPolystyrene6_1In_R25; ExpandedPolystyrene6_875In_R29; ExpandedPolystyrene8_6In_R35; ExpandedPolystyreneXPS0_25In_R1_25; ExpandedPolystyreneXPS0_5In_R2_50; ExpandedPolystyreneXPS0_75In_R3_75; ExpandedPolystyreneXPS1In_R5; ExpandedPolystyreneXPS1_25In_R6_25; ExpandedPolystyreneXPS1_5In_R7_50; ExpandedPolystyreneXPS1_75In_R8_75; ExpandedPolystyreneXPS1_875In_R9_37; ExpandedPolystyreneXPS2In_R10; ExpandedPolystyreneXPS2_5In_R12_50; ExpandedPolystyreneXPS3In_R15; ExpandedPolystyreneXPS3_5In_R17_50; ExpandedPolystyreneXPS4In_R20; ExpandedPolystyreneXPS4_5In_R22_50; ExpandedPolystyreneXPS5In_R25; ExpandedPolystyreneXPS5_5In_R27_50; ExpandedPolystyreneXPS6In_R30; ExpandedPolystyreneXPS6_5In_R32_50; ExpandedPolystyreneXPS8In_R40; ExpandedPolystyreneXPS8_5In_R42_50; ExpandedPolyurethane0_5In_R3_1; ExpandedPolyurethane0_75In_R4_7; ExpandedPolyurethane1In_R6_3; ExpandedPolyurethane1_25In_R7_8; ExpandedPolyurethane2In_R12_6; FiberCementBoard63LbPerFt3Thickness0_33In; FiberCementBoard88LbPerFt3Thickness0_33In; FiberCementBoard88LbPerFt3Thickness0_5In; FiberboardSheathing0_5In; GlassFiberBatt10In_ R30_CEC_Default; GlassFiberBatt12In_ R38_CEC_Default; GlassFiberBatt3_5In_ R11_CEC_Default; GlassFiberBatt3_5In_ R13_CEC_Default; GlassFiberBatt3_5In_ R15_CEC_Default; GlassFiberBatt4In; GlassFiberBatt4_5In; GlassFiberBatt5In; GlassFiberBatt5_5In_ R19_CEC_Default; GlassFiberBatt5_5In_ R21_CEC_Default; GlassFiberBatt6In; GlassFiberBatt6_5In; GlassFiberBatt7_25In_ R25_CEC_Default; GlassFiberBatt7_25In_ R30_CEC_Default; GlassFiberBatt8_25In_ R30_CEC_Default; GypsumBoard0_375In; GypsumBoard0_5In; GypsumBoard0_625In; GypsumBoard0_75In; GypsumPartitionBlock3Cell4x12x30Thickness4In; GypsumPartitionBlock4Cell3x12x30Thickness3In; GypsumPlaster80LbPerFt3Thickness0_5In; GypsumPlaster80LbPerFt3Thickness0_625In; GypsumPlasterOnMetalLath70LbPerFt3Thickness0_75In; GypsumPlasterOnMetalLath80LbPerFt3Thickness0_75In; HBPartBoard0_75In; HardBoard0_75In; HardBoardHDF50LbPerFt3Thickness0_375In; HardBoardHDF50LbPerFt3Thickness0_5In; HardBoardHDF50LbPerFt3Thickness0_625In; HardBoardHDF50LbPerFt3Thickness0_75In; Hardwood0_5In; Hardwood0_75In; Hardwood1In; ICF1_5InPolyurethaneEachSideConcrete6In; ICF1_5InPolyurethaneEachSideConcrete8In; ICF2InEPSEachSideConcrete6In; ICF2InEPSEachSideConcrete8In; ICF2InPolyurethaneEachSideConcrete6In; ICF2InPolyurethaneEachSideConcrete8In; ICF2InXPSEachSideConcrete6In; ICF2InXPSEachSideConcrete8In; ICF2_5InEPSEachSideConcrete6In; ICF2_5InEPSEachSideConcrete8In; ICF3InEPSEachSideConcrete6In; ICF3InEPSEachSideConcrete8In; ICF3InXPSEachSideConcrete6In; ICF3InXPSEachSideConcrete8In; ICF4InEPSEachSideConcrete6In; ICF4InEPSEachSideConcrete8In; ICF4InXPSEachSideConcrete6In; ICF4InXPSEachSideConcrete8In; ICF4_5InPolyurethaneEachSideConcrete6In; ICF4_5InPolyurethaneEachSideConcrete8In; LightRoof0_4In; LinoleumCorkTile0_25In; LooseFillMineralFiber2LbPerFt3Thickness13_75In; LooseFillMineralFiber2LbPerFt3Thickness4In; LooseFillMineralFiber2LbPerFt3Thickness6_5In; LooseFillMineralFiber2LbPerFt3Thickness7_5In; LooseFillMineralFiber2LbPerFt3Thickness8_25In; LooseFillMineralFiberClosedSidewallsThickness3_5In; Maple1In; MasticAsphaltHeavy20PercentGrit1In; MetalDeck0_0625In; MetalInsulatedPanel2In; MetalInsulatedPanel2_5In; MetalInsulatedPanel3In; MetalInsulatedPanel4In; MetalInsulatedPanel5In; MetalInsulatedPanel6In; MetalSiding0_0625In; MetalStandingSeam0_0625In; MortarCementThickness1In; MortarCementThickness1_75In; Oak1In; OrientedStrandBoard0_5In; OrientedStrandBoard0_625In; OrientedStrandBoard0_75In; PerliteBoard0_75In_R1_9; PerliteBoard1In_R2_5; PerliteBoard1_5In_R3_8; PerliteBoard2In_R5_0; PerlitePlaster25LbPerFt3Thickness0_5In; PerlitePlaster38LbPerFt3Thickness0_5In; PineOvenDried1In; PlasterSandAggregateThickness1In; Plywood0_25In; Plywood0_375In; Plywood0_5In; Plywood0_625In; Plywood0_75In; Plywood1In; Plywood1_25In; Plywood1_5In; PulpboardOrPaperPlasterThickness0_5In; R24BattWall8In_R24; RammedEarth; Roof10LbPerFt2Thickness1In; Roof15LbPerFt2Thickness1_5In; Roof25LbPerFt2Thickness2_5In; Roof5LbPerFt2Thickness0_5In; RoofGravel0_5In; RoofGravel1In; RoofingFelt0_125In; RubberTile1In; SIPSCrawlSpaceR22Double2xSpline6_5In; SIPSCrawlSpaceR22IJoistSpline6_5In; SIPSCrawlSpaceR22Single2xSpline6_5In; SIPSCrawlSpaceR28Double2xSpline8_25In; SIPSCrawlSpaceR28IJoistSpline8_25In; SIPSCrawlSpaceR28Single2xSpline8_25In; SIPSCrawlSpaceR33Double2xSpline6_5In; SIPSCrawlSpaceR33IJoistSpline6_5In; SIPSCrawlSpaceR33Single2xSpline6_5In; SIPSCrawlSpaceR36IJoistSpline10_25In; SIPSCrawlSpaceR36Single2xSpline10_25In; SIPSFloor; SIPSNoCrawlSpaceR22Double2xSpline6_5In; SIPSNoCrawlSpaceR22IJoistSpline6_5In; SIPSNoCrawlSpaceR22Single2xSpline6_5In; SIPSNoCrawlSpaceR28Double2xSpline8_25In; SIPSNoCrawlSpaceR28IJoistSpline8_25In; SIPSNoCrawlSpaceR28Single2xSpline8_25In; SIPSNoCrawlSpaceR33Double2xSpline6_5In; SIPSNoCrawlSpaceR33IJoistSpline6_5In; SIPSNoCrawlSpaceR33Single2xSpline6_5In; SIPSNoCrawlSpaceR36IJoistSpline10_25In; SIPSNoCrawlSpaceR36Single2xSpline10_25In; SIPSR14Double2xSpline4_5In; SIPSR14IJoistSpline4_5In; SIPSR14MetalSpline48In; SIPSR14OSBSpline4_5In; SIPSR14Single2xSpline4_5In; SIPSR18Double2xSpline4_5In; SIPSR18IJoistSpline4_5In; SIPSR18OSBSpline4_5In; SIPSR18Single2xSpline4_5In; SIPSR22Double2xSpline6_5In; SIPSR22IJoistSpline6_5In; SIPSR22MetalSpline48In; SIPSR22OSBSpline6_5In; SIPSR22Single2xSpline6_5In; SIPSR28Double2xSpline8_25In; SIPSR28Double2xSpline8_5In; SIPSR28IJoistSpline8_25In; SIPSR28IJoistSpline8_5In; SIPSR28MetalSpline48In; SIPSR28OSBSpline8_25In; SIPSR28OSBSpline8_5In; SIPSR28Single2xSpline8_25In; SIPSR28Single2xSpline8_5In; SIPSR33Double2xSpline6_5In; SIPSR33IJoistSpline6_5In; SIPSR33OSBSpline6_5In; SIPSR33Single2xSpline6_5In; SIPSR36Double2xSpline10_25In; SIPSR36IJoistSpline10_25In; SIPSR36MetalSpline48In; SIPSR36OSBSpline10_25In; SIPSR36Single2xSpline10_25In; SIPSR44Double2xSpline12_25In; SIPSR44IJoistSpline12_25In; SIPSR44OSBSpline12_25In; SIPSR44Single2xSpline12_25In; SIPSR55Double2xSpline10_25In; SIPSR55IJoistSpline10_25In; SIPSR55OSBSpline10_25In; SIPSR55Single2xSpline10_25In; SIPS_CrawlSpaceR36Double2xSpline10_25In; SIPS_NoCrawlSpaceR36Double2xSpline10_25In; SandAggregateOnMetalLathThickness0_75In; SandAggregateThickness0_375In; SandAggregateThickness0_5In; SandAggregateThickness0_625In; SandAggregateThickness0_75In; ShinglesAsbestosCementLapped0_25In; ShinglesAsphaltRollSiding0_25In; ShinglesWood16In7_5InExposure0_5In; ShinglesWoodInsulatedBackerBoardSiding0_3125In; SidingAsphaltInsulating0_5InBed0_5In; SidingWoodBevel10_0InLapped0_75In; SinglePlyRoofing0_25In; Slate0_5In; SlateOrTile0_5In; SprayCellulosicFiber4_6LbPerFt3Thickness3_5In; SprayCellulosicFiber4_6LbPerFt3Thickness4In; SprayCellulosicFiber4_6LbPerFt3Thickness4_5In; SprayCellulosicFiber4_6LbPerFt3Thickness5In; SprayCellulosicFiber4_6LbPerFt3Thickness5_5In; SprayCellulosicFiber4_6LbPerFt3Thickness6In; SprayCellulosicFiber4_6LbPerFt3Thickness6_5In; SprayGlassFiber3_9LbPerFt3Thickness3_5In; SprayGlassFiber3_9LbPerFt3Thickness4In; SprayGlassFiber3_9LbPerFt3Thickness4_5In; SprayGlassFiber3_9LbPerFt3Thickness5In; SprayGlassFiber3_9LbPerFt3Thickness5_5In; SprayGlassFiber3_9LbPerFt3Thickness6In; SprayGlassFiber3_9LbPerFt3Thickness6_5In; SprayPolyurethaneFoam0_5LbPerFt3Thickness3_5In; SprayPolyurethaneFoam0_5LbPerFt3Thickness4In; SprayPolyurethaneFoam0_5LbPerFt3Thickness4_5In; SprayPolyurethaneFoam0_5LbPerFt3Thickness5In; SprayPolyurethaneFoam0_5LbPerFt3Thickness5_5In; SprayPolyurethaneFoam0_5LbPerFt3Thickness6In; SprayPolyurethaneFoam0_5LbPerFt3Thickness6_5In; SprayPolyurethaneFoam3_0LbPerFt3Thickness3_5In; SprayPolyurethaneFoam3_0LbPerFt3Thickness4In; SprayPolyurethaneFoam3_0LbPerFt3Thickness4_5In; SprayPolyurethaneFoam3_0LbPerFt3Thickness5In; SprayPolyurethaneFoam3_0LbPerFt3Thickness5_5In; SprayPolyurethaneFoam3_0LbPerFt3Thickness6In; SprayPolyurethaneFoam3_0LbPerFt3Thickness6_5In; Stone1In; StrawBaleIntExtStucco18In; StructuralGlazingDoubleNoLowENoIns; StructuralGlazingDoubleNoLowER10Ins; StructuralGlazingDoubleNoLowER15Ins; StructuralGlazingDoubleNoLowER20Ins; StructuralGlazingDoubleNoLowER25Ins; StructuralGlazingDoubleNoLowER30Ins; StructuralGlazingDoubleNoLowER4Ins; StructuralGlazingDoubleNoLowER7Ins; StructuralGlazingSingleGlassStoneMetalNoIns; StructuralGlazingSingleGlassStoneMetalR10Ins; StructuralGlazingSingleGlassStoneMetalR15Ins; StructuralGlazingSingleGlassStoneMetalR20Ins; StructuralGlazingSingleGlassStoneMetalR25Ins; StructuralGlazingSingleGlassStoneMetalR30Ins; StructuralGlazingSingleGlassStoneMetalR4Ins; StructuralGlazingSingleGlassStoneMetalR7Ins; StructuralGlazingTripleOrLowENoIns; StructuralGlazingTripleOrLowER10Ins; StructuralGlazingTripleOrLowER15Ins; StructuralGlazingTripleOrLowER20Ins; StructuralGlazingTripleOrLowER25Ins; StructuralGlazingTripleOrLowER30Ins; StructuralGlazingTripleOrLowER4Ins; StructuralGlazingTripleOrLowER7Ins; Stucco0_375In; Stucco0_875In; Stucco1Coat; Stucco3Coat; StuccoSyntheticEIFS_Finish1In; Terrazzo1In; TileGap0_75In; VaporPermeableFelt0_125In; VaporSeal2LayerMopped15LbFelt0_25In; VaporSealPlasticFilm0_0625In; VermiculiteAggregate45LbPerFt3Thickness0_5In; Wood0_5In; Wood1In; Wood2In; Wood4In; WoodShingles0_75In; WoodShinglesPlainAndPlasticFilmFaced0_75In; WoodSiding0_5In | [6 empty] | Compulsory |  | dtyp:EnumerationConstantPermissive
| FramingConfiguration | FrmConfig | enumerated list | none | Floor16inOC; Floor24inOC; Roof16inOC; Roof24inOC; Roof48inOC; RoofMetalScrewDown; RoofMetalStandingSeam; RoofMetalStandingSeamFilledCavity; Wall16inOC; Wall24inOC; WallAWS24inOC; WallAWS48inOC; WallMetalDoubleLayerBatt; WallMetalSingleLayerBatt | [6 empty] | CondRequired |  |  | The frame member spacing or other geometric configuration of a CodeCategory = Composite material. | 2013 JA4, referenced in various sections
| FramingDepth | FrmDepth | enumerated list | none | 0_5In; 0_75In; 11_25In; 1In; 1_5In; 2In; 2_5In; 3In; 3_5In; 4In; 4_5In; 5In; 5_5In; 7_25In; 9_25In | [6 empty] | CondRequired |  |  | The frame member depth of a CodeCategory = Composite material. | 2013 JA4, referenced in various sections
| FramingMaterial | FrmMat | enumerated list | none | Metal; Wood | [6 empty] | CondRequired |  |  | The framing material used in a CodeCategory = Composite material. | 2013 JA4, referenced in various sections
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
PolyLoop
Roof
| AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Space |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative | The two dimensional extent of a roof surface. |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConstructAssembly
| CRRCAgedEmittance | CRRCAgedEmit | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated 3-year aged thermal emittance of a roofing material. | NACM-5.5.1, Reflectance
| CRRCAgedReflectance | CRRCAgedRefl | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated 3-year aged solar reflectance of a roofing material. | NACM-5.5.1, Reflectance
| CRRCAgedSRI | CRRCAgedSRI | integer | none | [7 empty] | CondRequired |  |  | The CRRC rated 3-year aged Solar Reflective Index (SRI) of a roofing material.The SRIis a measure defined by the Lawrence Berkeley National Laboratory as the roof's ability to reject solar heat, as shown by a small temperature rise. | 2013 T24 Part 6, 110.8(i)3
| CRRCInitialEmittance | CRRCInitialEmit | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated initial thermal emittance of a roofing material. | NACM-5.5.1, Reflectance
| CRRCInitialReflectance | CRRCInitialRefl | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated initial solar reflectance of a roofing material. | NACM-5.5.1, Reflectance
| CRRCInitialSRI | CRRCInitialSRI | integer | none | [7 empty] | CondRequired |  |  | The CRRC rated initial Solar Reflective Index (SRI) of a roofing material.The SRIis a measure defined by the Lawrence Berkeley National Laboratory as the roof's ability to reject solar heat, as shown by a small temperature rise. | 2013 T24 Part 6, 110.8(i)3
| CRRCProductID | CRRCProdID | string | none | [7 empty] | CondRequired |  |  | The CRRC product identification number for the roofing product
| FieldAppliedCoating | FieldAppliedCoating | boolean | none | [7 empty] | CondRequired |  |  | Defines whether a roof coating is field or factory applied. Required for ACM aged reflectance equation. | NACM-5.5.1, Reflectance
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Schedule
| EndDay | EndDay | integer | none |  | Yes | 53 | 53 |  |  |  | Required |  |  | The day of the month, that the Schedule week ends on
| EndMonth | EndMonth | integer | none |  | Yes | 53 | 53 |  |  |  | Required |  |  | The month of the year that the Schedule week ends on
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| ScheduleWeekReference | SchWeekRef | reference | none |  | Yes | 53 | 53 |  |  |  | Compulsory | ScheduleWeek
| Type | Type | enumerated list | none | Fraction; OnOff; Temperature; ThrmlEngyStorMode | [6 empty] | Compulsory |  |  | A list of schedule control mechanisms
ScheduleDay
| Hour | Hr | decimal | none |  | Yes | 24 | 24 |  |  |  | Compulsory |  |  | The percentage of a full load to be applied for a specified hour of the day. | Load Percentage Hourly is the value used in the schedule tables N2-8 through N2-12
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Type | Type | enumerated list | none | Fraction; OnOff; Temperature; ThrmlEngyStorMode | [6 empty] | Compulsory |  |  | A list of schedule control mechanisms
ScheduleWeek
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| ScheduleDayAllDaysReference | SchDayAllRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayCoolingDesignDayReference | SchDayClgDDRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayFridayReference | SchDayFriRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayHeatingDesignDayReference | SchDayHtgDDRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayHolidayReference | SchDayHolRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayMondayReference | SchDayMonRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDaySaturdayReference | SchDaySatRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDaySundayReference | SchDaySunRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayThursdayReference | SchDayThuRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayTuesdayReference | SchDayTueRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayWednesdayReference | SchDayWedRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayWeekdaysReference | SchDayWDRef | reference | none | [7 empty] | Optional | ScheduleDay
| ScheduleDayWeekendsReference | SchDayWERef | reference | none | [7 empty] | Optional | ScheduleDay
| Type | Type | enumerated list | none | Fraction; OnOff; Temperature; ThrmlEngyStorMode | [6 empty] | Compulsory |  |  | A list of schedule control mechanisms
Skylight
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative | This is the area of the rough opening for the skylight | Used in calculating skyight roof ratio. | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| FenestrationConstructionReference | FenConsRef | reference | none | [7 empty] | Compulsory | FenestrationConstruction
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
Space
| Area | Area | decimal | ft2 |  |  |  |  | 1 |  |  | Compulsory |  | dtyp:DecimalNonnegative |  | NRCCLTI01E | Compulsory when Proj:GeometryInpType = 'Simplified', else NotInput
| CommercialRefrigerationLatentFraction | CommRfrgLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| CommercialRefrigerationLostFraction | CommRfrgLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| CommercialRefrigerationRadiationFraction | CommRfrgRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ConditioningType | CondgType | enumerated list | none | DirectlyConditioned; IndirectlyConditioned; Plenum; Unconditioned | [6 empty] | Required |  |  | One of a list of categories which characterize the type of conditioning for a space. | There are definitions for the following types of space conditioning in the Standards: Conditioned Space, DirectlyConditioned Space, IndirectlyProcess SpaceRefrigerated SpaceUnconditioned Space Plenum in T24 is handled as conditioned space. Ref: NR ACM 2.3.1.1 Directly Conditioned Space Return Air Plenums 2013 NR ACM This maps to Thermal Block Type an attribute of building descriptor, Thermal Block which has the value of directly conditioned, indirectly conditioned, unconditioned or plenum. 90.1 2007 Sec 3.2 Definitions; Table 5.5.1-8
| DaylightingControlType | DayltgCtrlType | enumerated list | none | Continuous; ContinuousPlusOff; None; SteppedSwitching | [6 empty] | Defaulted |  |  | The type of control that is used to control the electric lighting in response to daylight available at the reference point. | 2013 NR ACM
| DwellingUnitTypeArea | DwellingUnitTypeArea | decimal | ft2 |  | Yes | 0 | 6 |  |  |  | CondRequired |  | dtyp:DecimalNonnegative
| DwellingUnitTypeCount | DwellingUnitTypeCnt | integer | none |  | Yes | 0 | 6 |  |  |  | CondRequired |  | dtyp:IntegerNonnegative
| ElevatorCount | ElevCnt | integer | none | [7 empty] | Optional |  |  | The number of elevators. | 2013 NR ACM
| ElevatorLatentFraction | ElevLatFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| ElevatorLostFraction | ElevLostFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| ElevatorPower | ElevPwr | decimal | W | [7 empty] | Optional |  |  | The power for each elevator in the associated elevator count | 2013 NR ACM | NOTE that this is the power per elevator rather than the total elevator power in a space.
| ElevatorRadiationFraction | ElevRadFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| ElevatorScheduleReference | ElevSchRef | reference | none | [7 empty] | Defaulted | Schedule |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| EnclosedSpace | EnclosedSpc | boolean | none | [7 empty] | Optional
| EnvelopeStatus | EnvStatus | enumerated list | none | Altered; Existing; New | [6 empty] | Defaulted |  |  |  | 2013 NR ACM
| EscalatorCount | EscalCnt | integer | [8 empty] | Optional |  |  | The number of escalators. | 2013 NR ACM
| EscalatorLatentFraction | EscalLatFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| EscalatorLostFraction | EscalLostFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| EscalatorPower | EscalPwr | decimal | W | [7 empty] | Optional |  |  | The power for each escalator in the associated escalator count for a space. | 2013 NR ACM | NOTE that this is the power per escalator rather than the total escalator power in a space.
| EscalatorRadiationFraction | EscalRadFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| EscalatorScheduleReference | EscalSchRef | reference | none | [7 empty] | Defaulted | Schedule |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ExhaustAirChangesPerHour | ExhACH | decimal | ACH | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
| ExhaustPerArea | ExhPerArea | decimal | ft3 per min ft2 | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
| ExhaustPerSpace | ExhPerSpc | decimal | ft3 per min | [7 empty] | Optional
| FixedSeating | FxdSeat | boolean | none | [7 empty] | Defaulted
| FloorArea | FlrArea | decimal | ft2 | [7 empty] | Optional
| FloorToCeilingHeight | FlrToCeilingHgt | decimal | ft |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative | The measurement of height from the top surface of the floor to the bottom surface of the ceiling in an enclosed space. | Floor to Ceiling Height measurement is used in several places in the Standards e.g. in Section Section 131 Indoor Lighting Controls That Shall Be Installed, Floor to Ceiling Height is used in calculating skylit daylight areas.
| FloorZ | FlrZ | decimal | ft | [7 empty] | Optional |  |  | Need definition | 2013 NR ACM | Required when Project:GeometryInputType = 'Simplified', else NotInput
| GasEquipmentLatentFraction | GasEqpLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| GasEquipmentLostFraction | GasEqpLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| GasEquipmentPowerDensity | GasEqpPwrDens | decimal | Btu per h ft2 | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| GasEquipmentRadiationFraction | GasEqpRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| GlareAzimuth | GlrAz | decimal | deg arc | [7 empty] | Optional |  |  | View angle for calculating glare index
| HasProcessExhaust | HasProcExh | boolean | none | [7 empty] | Defaulted
| HighRiseResidentialConditionedFloorArea | HighRiseResCondFlrArea | decimal | ft2 | [7 empty] | Optional
| HotelModelGuestRoomConditionedFloorArea | HotelMotelGuestRmCondFlrArea | decimal | ft2 | [7 empty] | Optional
| HotelMotelGuestRoomCount | HotelMotelGuestRmCnt | integer | none |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:IntegerNonnegative
| HotWaterHeatingTotal | HotWtrHtgTot | decimal | gal per h | [7 empty] | Optional
| HotWaterSupplyTemperatureScheduleReference | HotWtrSupTempSchRef | reference | none | [7 empty] | Optional | Schedule
| InteriorLightingNonRegulatedHeatGainRadiantFraction | IntLtgNonRegHtGnRadFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of non-regulated interior lighting radiant heat gain going to space surfaces | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingNonRegulatedHeatGainSpaceFraction | IntLtgNonRegHtGnSpcFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of non-regulated interior lighting heat gain going to space air | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingNonRegulatedScheduleReference | IntLtgNonRegSchRef | reference | none | [7 empty] | Defaulted | Schedule |  | Reference to a unique identification name for a Schedule of interior lighting type |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingRegulatedHeatGainRadiantFraction | IntLtgRegHtGnRadFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of regulated interior lighting radiant heat gain going to space surfaces | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingRegulatedHeatGainSpaceFraction | IntLtgRegHtGnSpcFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of regulated interior lighting heat gain going to space air | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingSpecificationMethod | IntLtgSpecMthd | enumerated list | none | AreaCategoryMethod; TailoredMethod | [6 empty] | Defaulted |  |  | Selection of interior lighting specification method.
| IsAtriumGreaterThan55Feet | IsAtriumGT55Ft | boolean | none | [7 empty] | Defaulted
| IsPlenumReturn | IsPlenumRet | boolean | none | [7 empty] | Optional
| KitchenExhaustHoodDuty | KitExhHoodDuty | enumerated list | none | ExtraHeavy; Heavy; Light; Medium; None | Yes | 0 | 5 |  |  |  | CondRequired
| KitchenExhaustHoodFlow | KitExhHoodFlow | decimal | ft3 per min |  | Yes | 0 | 5 |  |  |  | Defaulted |  | dtyp:DecimalNonnegative
| KitchenExhaustHoodLength | KitchenExhHoodLen | decimal | ft |  | Yes | 0 | 5 |  |  |  | CondRequired |  | dtyp:DecimalNonnegative
| KitchenExhaustHoodStyle | KitchenExhHoodStyle | enumerated list | none | BackshelfOrPassover; DoubleIsland; Eyebrow; None; SingleIsland; WallMountedCanopy | Yes | 0 | 5 |  |  |  | Optional
| LaboratoryExhaustRateType | LabExhRtType | enumerated list | none | HoodDominated; LoadDominated | [6 empty] | Defaulted |  |  | The type of load that dictates lab exhaust rate requirements | 2013 NR ACM 5.6.5.3
| LightingStatus | LtgStatus | enumerated list | none | Altered; Existing; Future; New | [6 empty] | Defaulted |  |  |  | 2013 NR ACM
| MaximumGlareIndex | MaxGlrIdx | decimal | none | [7 empty] | Optional |  |  | Maximum glare index for daylighting control
| MinimumDimmingLightFraction | MinDimLtgFrac | decimal | none | [7 empty] | Defaulted |  |  | Minimum light output of controlled lighting when fully dimmed. Minimum light fraction = (Minimum light output) / (Rated light output). | 2013 NR ACM
| MinimumDimmingPowerFraction | MinDimPwrFrac | decimal | none | [7 empty] | Defaulted |  |  | The minimum power fraction when controlled lighting is fully dimmed. Minimum power fraction = (Minimum power) / (Full rated power). | 2013 NR ACM
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| NumberOfControlSteps | NumOfCtrlSteps | integer | none | [7 empty] | Defaulted |  |  | For step switching, this term defines even steps of light output and even steps of rated power fractions. | 2013 NR ACM
| OccupantFraction | OccFrac | decimal | none |  |  |  |  | 0.5 | 5 |  | Defaulted |  |  | This is the percentage of BuildingTotalGrossFloorArea that is occupied and operational
| OccupantNumberFixedSeating | OccNumFxdSeat | decimal | person | [7 empty] | Defaulted
| Perimeter | Perim | decimal | ft | [7 empty] | Optional |  |  |  |  | Optional when Proj:GeometryInpType = 'Simplified', else NotInput
| PrimarySideDaylightingControlledLightingPower | PriSideDayltgCtrlLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
| PrimarySideDaylightingIlluminanceSetPoint | PriSideDayltgIllumSetpt | decimal | lux |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:DecimalNonnegative
| PrimarySideDaylightingInstalledLightingPower | PriSideDayltgInstalledLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
| PrimarySidelit100PercentControlled | PriSide100PctControlled | boolean | none | [7 empty] | Optional
| ProcessElectricalLatentFraction | ProcElecLatFrac | decimal | none | [7 empty] | Optional
| ProcessElectricalLostFraction | ProcElecLostFrac | decimal | none | [7 empty] | Optional
| ProcessElectricalRadiationFraction | ProcElecRadFrac | decimal | none | [7 empty] | Optional
| ProcessElectricalScheduleReference | ProcElecSchRef | reference | none | [7 empty] | Optional | Schedule |  | Reference to a unique identification name for a schedule in a library of process electrical type
| ProcessGasLatentFraction | ProcGasLatFrac | decimal | none | [7 empty] | Optional
| ProcessGasLostFraction | ProcGasLostFrac | decimal | none | [7 empty] | Optional
| ProcessGasPowerDensity | ProcGasPwrDens | decimal | Btu per h ft2 | [7 empty] | Optional |  | dtyp:DecimalNonnegative | Commercial gas power density is the average power density for all commercial gas equipment, assuming constant year-round operation. | 2013 Draft NR ACM
| ProcessGasRadiationFraction | ProcGasRadFrac | decimal | none | [7 empty] | Optional |  |  | The fraction of heat gain to Space to appliance energy use | 2013 Draft NR ACM
| ProcessGasScheduleReference | ProcGasSchRef | reference | none | [7 empty] | Optional | Schedule |  | Reference to a unique identification name for a schedule in a library of process gas type
| ReceptacleLatentFraction | RecptLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ReceptacleLostFraction | RecptLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ReceptacleRadiationFraction | RecptRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ResidentialDHWSystemReference | ResDHWSysRef | reference | none | [7 empty] | Optional
| ResidentialHotWaterHeatingRate | ResHotWtrHtgRt | decimal | gal per h person | [7 empty] | Optional
| ReturnPlenumSpaceReference | RetPlenumSpcRef | reference | none | [7 empty] | Optional | Space
| SecondarySideDaylightingControlledLightingPower | SecSideDayltgCtrlLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
| SecondarySideDaylightingIlluminanceSetPoint | SecSideDayltgIllumSetpt | decimal | lux |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:DecimalNonnegative
| SecondarySideDaylightingInstalledLightingPower | SecSideDayltgInstalledLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
| SecondarySidelit100PercentControlled | SecSide100PctControlled | boolean | none | [7 empty] | Optional
| SHWFluidSegmentReference | SHWFluidSegRef | reference | none | [7 empty] | Optional
| SkylightRequirementException | SkyltReqExcpt | enumerated list | none | Auditorium; Church; ExistingWalls; FutureCeilings; FutureWalls; MovieTheater; Museum; RefrigeratedWarehouse | [6 empty] | CondRequired |  |  |  |  | Required when Spc:SkyltReqExcptFrac > 0, else NotInput
| SkylightRequirementExceptionArea | SkyltReqExcptArea | decimal | ft2 |  |  |  |  | 0 | 1000000 |  | CondRequired
| SkylightRequirementExceptionFraction | SkyltReqExcptFrac | decimal | none | [7 empty] | Defaulted
| Skylit100PercentControlled | Skylit100PctControlled | binary | none | [7 empty] | Optional
| SkylitDaylightingControlledLightingPower | SkylitDayltgCtrlLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
| SkylitDaylightingIlluminanceSetPoint | SkylitDayltgIllumSetpt | decimal | lux |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:DecimalNonnegative
| SkylitDaylightingInstalledLightingPower | SkylitDayltgInstalledLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
| SpaceFunction | SpcFunc | enumerated list | none | AuditoriumArea; AutoRepairArea; BarCocktailLoungeCasinoArea; BeautySalonArea; CivicMeetingPlaceArea; ClassroomLectureTrainingVocationalAreas; CommercialIndustrialStorageArea; CommercialIndustrialStorageAreaRefrigerated; ComputerRoom; ConventionConferenceMultipurposeMeetingCenterArea; CorridorRestroomStairsSupportArea; DiningArea; DryCleanCoinOperated; DryCleaningFullServiceCommercial; ElectricalMechancialTelephoneRoom; ExerciseRoom; ExhibitMuseumArea; FinancialTransactionsArea; GeneralCommercialIndustrialWorkAreaHighBay; GeneralCommercialIndustrialWorkAreaLowBay; GeneralCommercialIndustrialWorkAreaPrecision; GrocerySalesArea; GymnasiumSportsArena; HighRiseResidentialLivingSpace; HotelFunctionArea; HotelMotelGuestRoom; HousingPublicCommonAreaMultifamilyDormitory; HousingPublicCommonAreaSeniorHousing; KitchenCommercialFoodPreparation; KitchenetteResidentialKitchen; LaboratoryEquipmentRoom; LaboratoryScientific; Laundry; LibraryReadingArea; LibraryStacks; LobbyHotel; LobbyMainEntry; LockerDressingRoom; LoungeRecreational; MallAndAtria; MedicalAndClinicalCare; NurseriesForChildrenDayCare; Office250FtOrLess; OfficeGreaterThan250Ft; ParkingGarageAreaDaylightAdaptationZone; ParkingGarageAreaDedicatedRamp; ParkingGarageBuildingParkingArea; PoliceStationFireStation; ReligiousWorshipArea; RetailMerchandiseSalesWholesaleShowroom; TheaterMotionPicture; TheaterPerformance; TransportationFunction; TransportationFunctionConcourseBaggage; TransportationFunctionTicketing; UnleasedTenantArea; UnoccupiedExcludeInGrossFloorArea; UnoccupiedIncludeInGrossFloorArea; VideoConferencingStudio; WaitingArea | [6 empty] | Compulsory |  |  | One of a list of occupancies assigned to the OccupancyArea | Title 24 Part 6 has definitions for occupancy types listed in the definitions in Section 101 under Nonresidential Function Area Or Type Of Use. Many of these types are used in lighting tables to assign values to rule targets such as lighting power adjustment factor. 2008 NR ACM has Tables N2-5 and N2-6 that use occupancy types for loads and schedules. 2013 NR ACM Appendix A has space-by-space occupancy types.
| SpaceFunctionDefaultsReference | SpcFuncDefaultsRef | reference | none | [7 empty] | Optional |  |  | Reference to a unique SpaceFunctionDefaults object name
| SupplyPlenumSpaceReference | SupPlenumSpcRef | reference | none | [7 empty] | Optional | Space
| ThermalZoneReference | ThrmlZnRef | reference | none | [7 empty] | Required |  |  | This is a reference to the thermal zone that serves a given space.
| VentilationAirChangesPerHour | VentACH | decimal | ft3 per min | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
| VentilationPerArea | VentPerArea | decimal | ft3 per min ft2 | [7 empty] | Defaulted
| VentilationPerPerson | VentPerPerson | decimal | ft3 per min person | [7 empty] | Defaulted
| VentilationPerSpace | VentPerSpc | decimal | ft3 per min | [7 empty] | Optional
| Volume | Vol | decimal | ft3 | [7 empty] | Required |  |  | The measurement of space or object calculated by multiplying the three dimensions of the space: length, width, and height. | Title 24 and JA II have a definition for conditioned volume as follows: CONDITIONED VOLUME is the total volume (in cubic feet) of the conditioned space within a building
SpaceFunctionDefaults
| CommercialRefrigerationLatentFraction | CommRfrgLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| CommercialRefrigerationLostFraction | CommRfrgLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| CommercialRefrigerationRadiationFraction | CommRfrgRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| DesignInfiltrationRate | DsgnInfRt | decimal | ft3 per min ft2 |  | Yes | 0 | 4 |  |  |  | Defaulted |  |  | Design infiltration airflow | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ElevatorCount | ElevCnt | integer | none | [7 empty] | Optional |  |  | The number of elevators. | 2013 NR ACM
| ElevatorLatentFraction | ElevLatFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| ElevatorLostFraction | ElevLostFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| ElevatorPower | ElevPwr | decimal | W | [7 empty] | Optional |  |  | The power for each elevator in the associated elevator count | 2013 NR ACM | NOTE that this is the power per elevator rather than the total elevator power in a space.
| ElevatorRadiationFraction | ElevRadFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| ElevatorScheduleReference | ElevSchRef | reference | none | [7 empty] | Defaulted | Schedule |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| EscalatorCount | EscalCnt | integer | [8 empty] | Optional |  |  | The number of escalators. | 2013 NR ACM
| EscalatorLatentFraction | EscalLatFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| EscalatorLostFraction | EscalLostFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| EscalatorPower | EscalPwr | decimal | W | [7 empty] | Optional |  |  | The power for each escalator in the associated escalator count for a space. | 2013 NR ACM | NOTE that this is the power per escalator rather than the total escalator power in a space.
| EscalatorRadiationFraction | EscalRadFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
| EscalatorScheduleReference | EscalSchRef | reference | none | [7 empty] | Defaulted | Schedule |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ExhaustAirChangesPerHour | ExhACH | decimal | ACH | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
| ExhaustPerArea | ExhPerArea | decimal | ft3 per min ft2 | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
| ExhaustPerSpace | ExhPerSpc | decimal | ft3 per min | [7 empty] | Optional
| FunctionScheduleGroup | FuncSchGrp | enumerated list | none | Assembly; Data; Health; Laboratory; Manufacturing; Office; Parking; ResidentialCommon; ResidentialLiving; Restaurant; Retail; School; Warehouse | [6 empty] | Optional |  |  | A type specifying occupancy function categories used to determine schedules. | 2008 NR ACM tables N2-8 through N2-12 are defined by these Load Schedule Occupancy types 2013 NR ACM Appendix C schedules in tables C12 - C16 use the same occupancy types
| GasEquipmentLatentFraction | GasEqpLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| GasEquipmentLostFraction | GasEqpLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| GasEquipmentPowerDensity | GasEqpPwrDens | decimal | Btu per h ft2 | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| GasEquipmentRadiationFraction | GasEqpRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| HotWaterSupplyTemperature | HotWtrSupTemp | decimal | F | [7 empty] | Optional
| HotWaterSupplyTemperatureScheduleReference | HotWtrSupTempSchRef | reference | none | [7 empty] | Optional | Schedule
| InfiltrationMethod | InfMthd | enumerated list | none | AirChangesPerHour; FlowArea; FlowExteriorArea; FlowExteriorWallArea; FlowSpace | Yes | 0 | 4 |  |  |  | Defaulted |  |  | Method used for modeling uncontrolled air leakage or infiltration. | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InfiltrationModelCoefficientA | InfModelCoefA | decimal | none |  | Yes | 0 | 4 |  |  |  | Required |  |  | infiltration overall coefficient | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InfiltrationModelCoefficientB | InfModelCoefB | decimal | F |  | Yes | 0 | 4 |  |  |  | Required |  |  | infiltration temperature coefficient | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InfiltrationModelCoefficientC | InfModelCoefC | decimal | h per mi |  | Yes | 0 | 4 |  |  |  | Required |  |  | infiltration windspeed coefficient | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InfiltrationModelCoefficientD | InfModelCoefD | decimal | h2 per mi2 |  | Yes | 0 | 4 |  |  |  | Required |  |  | infiltration windspeed squared coefficient | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InfiltrationScheduleReference | InfSchRef | reference | none |  | Yes | 0 | 4 |  |  |  | Defaulted | Schedule |  | Reference to a schedule when needed by the selected infiltration method. | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingNonRegulatedHeatGainRadiantFraction | IntLtgNonRegHtGnRadFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of non-regulated interior lighting radiant heat gain going to space surfaces | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingNonRegulatedHeatGainSpaceFraction | IntLtgNonRegHtGnSpcFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of non-regulated interior lighting heat gain going to space air | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingNonRegulatedScheduleReference | IntLtgNonRegSchRef | reference | none | [7 empty] | Defaulted | Schedule |  | Reference to a unique identification name for a Schedule of interior lighting type |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingRegulatedHeatGainRadiantFraction | IntLtgRegHtGnRadFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of regulated interior lighting radiant heat gain going to space surfaces | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| InteriorLightingRegulatedHeatGainSpaceFraction | IntLtgRegHtGnSpcFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of regulated interior lighting heat gain going to space air | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| OccupantFraction | OccFrac | decimal | none |  |  |  |  | 0.5 | 5 |  | Defaulted |  |  | This is the percentage of BuildingTotalGrossFloorArea that is occupied and operational
| OccupantLatentHeatRate | OccLatHtRt | decimal | Btu per h person | [7 empty] | Optional |  |  | The rate of latent heat released per person which is a function of activity | 2008 NR ACM Table Table N2-5 and N2-6 assign values for Latent Heat per person 2013 NR ACM Latent and sensible heat generated by occupants are one descriptor, "Occupant Heat Rate".
| OccupantSensibleHeatRate | OccSensHtRt | decimal | Btu per h person | [7 empty] | Optional |  |  | The rate of sensible heat released per person which is a function of activity | 2008 NR ACM Table Table N2-5 and N2-6 assign values for Sensible Heat per person 2013 NR ACM Latent and sensible heat generated by occupants are one descriptor, "Occupant Heat Rate".
| ProcessElectricalLatentFraction | ProcElecLatFrac | decimal | none | [7 empty] | Optional
| ProcessElectricalLostFraction | ProcElecLostFrac | decimal | none | [7 empty] | Optional
| ProcessElectricalRadiationFraction | ProcElecRadFrac | decimal | none | [7 empty] | Optional
| ProcessElectricalScheduleReference | ProcElecSchRef | reference | none | [7 empty] | Optional | Schedule |  | Reference to a unique identification name for a schedule in a library of process electrical type
| ProcessGasLatentFraction | ProcGasLatFrac | decimal | none | [7 empty] | Optional
| ProcessGasLostFraction | ProcGasLostFrac | decimal | none | [7 empty] | Optional
| ProcessGasPowerDensity | ProcGasPwrDens | decimal | Btu per h ft2 | [7 empty] | Optional |  | dtyp:DecimalNonnegative | Commercial gas power density is the average power density for all commercial gas equipment, assuming constant year-round operation. | 2013 Draft NR ACM
| ProcessGasRadiationFraction | ProcGasRadFrac | decimal | none | [7 empty] | Optional |  |  | The fraction of heat gain to Space to appliance energy use | 2013 Draft NR ACM
| ProcessGasScheduleReference | ProcGasSchRef | reference | none | [7 empty] | Optional | Schedule |  | Reference to a unique identification name for a schedule in a library of process gas type
| ReceptacleLatentFraction | RecptLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ReceptacleLostFraction | RecptLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ReceptacleRadiationFraction | RecptRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
| ResidentialDHWSystemReference | ResDHWSysRef | reference | none | [7 empty] | Optional
| SHWFluidSegmentReference | SHWFluidSegRef | reference | none | [7 empty] | Optional
| SpaceFunction | SpcFunc | enumerated list | none | AuditoriumArea; AutoRepairArea; BarCocktailLoungeCasinoArea; BeautySalonArea; CivicMeetingPlaceArea; ClassroomLectureTrainingVocationalAreas; CommercialIndustrialStorageArea; CommercialIndustrialStorageAreaRefrigerated; ComputerRoom; ConventionConferenceMultipurposeMeetingCenterArea; CorridorRestroomStairsSupportArea; DiningArea; DryCleanCoinOperated; DryCleaningFullServiceCommercial; ElectricalMechancialTelephoneRoom; ExerciseRoom; ExhibitMuseumArea; FinancialTransactionsArea; GeneralCommercialIndustrialWorkAreaHighBay; GeneralCommercialIndustrialWorkAreaLowBay; GeneralCommercialIndustrialWorkAreaPrecision; GrocerySalesArea; GymnasiumSportsArena; HighRiseResidentialLivingSpace; HotelFunctionArea; HotelMotelGuestRoom; HousingPublicCommonAreaMultifamilyDormitory; HousingPublicCommonAreaSeniorHousing; KitchenCommercialFoodPreparation; KitchenetteResidentialKitchen; LaboratoryEquipmentRoom; LaboratoryScientific; Laundry; LibraryReadingArea; LibraryStacks; LobbyHotel; LobbyMainEntry; LockerDressingRoom; LoungeRecreational; MallAndAtria; MedicalAndClinicalCare; NurseriesForChildrenDayCare; Office250FtOrLess; OfficeGreaterThan250Ft; ParkingGarageAreaDaylightAdaptationZone; ParkingGarageAreaDedicatedRamp; ParkingGarageBuildingParkingArea; PoliceStationFireStation; ReligiousWorshipArea; RetailMerchandiseSalesWholesaleShowroom; TheaterMotionPicture; TheaterPerformance; TransportationFunction; TransportationFunctionConcourseBaggage; TransportationFunctionTicketing; UnleasedTenantArea; UnoccupiedExcludeInGrossFloorArea; UnoccupiedIncludeInGrossFloorArea; VideoConferencingStudio; WaitingArea | [6 empty] | Compulsory |  |  | One of a list of occupancies assigned to the OccupancyArea | Title 24 Part 6 has definitions for occupancy types listed in the definitions in Section 101 under Nonresidential Function Area Or Type Of Use. Many of these types are used in lighting tables to assign values to rule targets such as lighting power adjustment factor. 2008 NR ACM has Tables N2-5 and N2-6 that use occupancy types for loads and schedules. 2013 NR ACM Appendix A has space-by-space occupancy types.
| VentilationAirChangesPerHour | VentACH | decimal | ft3 per min | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
| VentilationPerArea | VentPerArea | decimal | ft3 per min ft2 | [7 empty] | Defaulted
| VentilationPerPerson | VentPerPerson | decimal | ft3 per min person | [7 empty] | Defaulted
| VentilationPerSpace | VentPerSpc | decimal | ft3 per min | [7 empty] | Optional
ThermalEnergyStorageModeScheduleDay
| Hour | Hr | enumerated list | none | Charge; Discharge; Off | No | 24 | 24 |  |  |  | Compulsory
| Type | Type | enumerated list | none | ThrmlEngyStorMode | No | [5 empty] | Compulsory
UndergroundFloor
| AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Space |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConstructAssembly
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| PerimeterExposed | PerimExposed | decimal | ft | [7 empty] | Defaulted |  |  | Describes the exposed (direct contact with ambient air) perimeter of a slab-on-grade or underground floor. | 2013 NACM 5.5.9, Slab Floor Geometry
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
UndergroundWall
| AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Space |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConstructAssembly
| Height | Hgt | decimal | ft | [7 empty] | CondRequired |  |  | Describes the height of the underground wall, i.e. the depth to the ground surface. | 2013 NACM 5.5.9, Slab Floor Geometry
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Window
| Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
| EnableWindowShades | EnableWinShades | boolean | none | [7 empty] | Defaulted
| FenestrationConstructionReference | FenConsRef | reference | none | [7 empty] | Compulsory | FenestrationConstruction
| Height | Hgt | decimal | ft | [7 empty] | CondRequired |  |  | Measures the vertical extent of a vertical rectangular surface such as a wall or door or a space. Units: feet. | Height is used in the Standards to measure the vertical extent of a building component e.g. Wall, or the vertical distance between two building components e.g. between the ceiling and the roof. | Required when GeometryInpType = Simplified and window shades specified, else NotInput
| LeftFinAngle | LeftFinAngle | decimal | deg arc | [7 empty] | Optional
| LeftFinDepth | LeftFinDepth | decimal | ft | [7 empty] | Optional
| LeftFinDistance | LeftFinDistance | decimal | ft | [7 empty] | Optional
| LeftFinDistanceAbove | LeftFinDistanceAbove | decimal | ft | [7 empty] | Optional
| LeftFinDistanceBelow | LeftFinDistanceBelow | decimal | ft | [7 empty] | Optional
| LeftFinTransmittance | LeftFinTrans | decimal | none | [7 empty] | Optional
| LeftFinTransmittanceOption | LeftFinTransOption | enumerated list | none | Constant; Scheduled | [6 empty] | Optional
| LeftFinTransmittanceScheduleReference | LeftFinTransSchRef | reference | none | [7 empty] | Optional | Schedule
| Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
| OverhangAngle | OverhangAngle | decimal | deg arc | [7 empty] | Optional
| OverhangDepth | OverhangDepth | decimal | ft | [7 empty] | Optional
| OverhangDistance | OverhangDistance | decimal | ft | [7 empty] | Optional
| OverhangLeftExtension | OverhangLeftExtension | decimal | ft | [7 empty] | Optional
| OverhangRightExtension | OverhangRightExtension | decimal | ft | [7 empty] | Optional
| OverhangTransmittance | OverhangTrans | decimal | none | [7 empty] | Optional
| OverhangTransmittanceOption | OverhangTransOption | enumerated list | none | Constant; Scheduled | [6 empty] | Optional
| OverhangTransmittanceScheduleReference | OverhangTransmittanceScheduleReference | reference | none | [7 empty] | Optional | Schedule
| RightFinAngle | RightFinAngle | decimal | deg arc | [7 empty] | Optional
| RightFinDepth | RightFinDepth | decimal | ft | [7 empty] | Optional
| RightFinDistance | RightFinDistance | decimal | ft | [7 empty] | Optional
| RightFinDistanceAbove | RightFinDistanceAbove | decimal | ft | [7 empty] | Optional
| RightFinDistanceBelow | RightFinDistanceBelow | decimal | ft | [7 empty] | Optional
| RightFinTransmittance | RightFinTrans | decimal | none | [7 empty] | Optional
| RightFinTransmittanceOption | RightFinTransOption | enumerated list | none | Constant; Scheduled | [6 empty] | Optional
| RightFinTransmittanceScheduleReference | RightFinTransSchRef | reference | none | [7 empty] | Optional | Schedule
| Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
| Width | Wd | decimal | ft | [7 empty] | CondRequired |  |  | The shorter of the two dimensions of a horizontal rectangular surface or the horizontal extent of a vertical rectangular surface Units: feet | The Standards use length and width interchangeably. For example the Display Perimeter which is the horizontal dimension of a vertical surface is defined as the length of an exterior wall, but the horizontal dimension for window which is also a vertical surface is referred to as width. | Required when GeometryInpType = Simplified and window shades specified, else NotInput
| X | X | decimal | ft | [7 empty] | CondRequired |  |  | A member of a CartesianPoint representing the length along the X axis from the origin. |  | For CBECC-Com nonresidential simulations, this is required when GeometryInpType = Simplified and window shades specified and multiple windows or doors, else NotInput
| Y | Y | decimal | ft | [7 empty] | CondRequired |  |  | A member of a CartesianPoint representing the length along the Y axis from the origin. |  | For CBECC-Com nonresidential simulations, this is required when GeometryInpType = Simplified and window shades specified and multiple windows or doors, else NotInput

## Properties
CBECC NR Term | CBECC NR Term Short Form | DataType | Units | Enumerations | CBECC NR Array | XSD ELEMATTRIB minOccurs | XSD ELEMATTRIB maxOccurs | CBECC NR minInclusive | CBECC NR maxInclusive | CBECC NR Different Data Type | Compliance Use | Referenced Objects | XSD Base Type | Definition | Standards Reference | Calculations And Rules
AboveGradeStoryCount | AboveGrdStoryCnt | integer | none |  |  |  |  | 1 |  |  | Required |  | dtyp:IntegerNonnegative | An attribute of the Building object for recording the number of above grade stories in the building which is used in several rules. | T24/CBC/Nonres Compliance Manual: The total number of stories in the building that have the finished floor surface entirely above the plane of grade or 50% of its volume above grade. Table N2-13 Standard Design HVAC System Selection tests if building has 3 or fewer stories above grade.
AboveGradeStoryCountAltered | AboveGrdStoryCntAltered | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The number of altered above grade stories in an alterations/additions building which is used in several rules. | 2013 NR ACM
AboveGradeStoryCountExisting | AboveGrdStoryCntExisting | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The number of existing above grade stories in an alterations/additions building which is used in several rules. | 2013 NR ACM
AboveGradeStoryCountNew | AboveGrdStoryCntNew | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The number of new above grade stories in an alterations/additions building which is used in several rules. | 2013 NR ACM
AdjacentSpaceReference | AdjacentSpcRef | reference | none | [7 empty] | CondRequired | Spc |  | This references the space on the other side of an interior partition. | 2013 NR ACM section 2.2.4 Software Modeling Requirements for Zones
Air | Air | enumerated list |  | AirCavityWallRoofCeiling4InPlus
AirCeiling0_5In
AirCeiling0_75In
AirCeiling1_5In
AirCeiling3_5In
AirFloor0_5In
AirFloor0_75In
AirFloor1_5In
AirFloor3_5In
AirMetalWallFraming16Or24InOC
AirRoof0_5In
AirRoof0_75In
AirRoof1_5In
AirRoof3_5In
AirWall0_5In
AirWall0_75In
AirWall1_5In
AirWall3_5In
AllowanceArea | AllowArea | decimal | ft2 | [7 empty] | Defaulted
AllowanceLength | AllowLen | decimal | ft | [7 empty] | Defaulted |  |  | Linear width of white/chalk board associated with AreaCategoryMethodAllowanceType of WhiteOrChalkBoard used to calculate power allowance. | 2013 Draft T24 140.6(c)2.G and Table 140.6-C
AllowanceQuantity | AllowQty | decimal | none | [7 empty] | Defaulted
AllowanceType | AllowType | enumerated list | none | AccentDisplayFeature | [6 empty] | Defaulted |  |  | Combines AreaCategory and TailoredMethod Allowance Types Enums into a single enumerated list
Decorative
Ornamental
ParkingGarageATMLighting
PrecisionCommercialIndustrial
SpecializedLabTaskWork
SpecializedTaskWork
TailoredFloorDisplayAllowance
TailoredOrnamentalAndSpecialEffectAllowance
TailoredTaskAllowance
TailoredVeryValuableDisplayCaseAllowance
TailoredWallDisplayAllowance
VideoConferencingStudioLighting
WhiteOrChalkBoard
AnnualWeatherFile | AnnualWeatherFile | string | none | [7 empty] | Required |  |  | Filename of the annual weather file with hourly weather data
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative | The two dimensional extent of a roof surface. |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 1 |  |  | Compulsory |  | dtyp:DecimalNonnegative |  | NRCCLTI01E | Compulsory when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative | This is the area of the rough opening for the skylight | Used in calculating skyight roof ratio. | Required when Proj:GeometryInpType = 'Simplified', else NotInput
Area | Area | decimal | ft2 |  |  |  |  | 0.01 |  |  | Required |  | dtyp:DecimalNonnegative |  |  | Required when Proj:GeometryInpType = 'Simplified', else NotInput
AssemblyContext | AssmContext | enumerated list | none | FieldFabricated | [6 empty] | CondRequired |  |  | The context in which a building element was assembled for installation. | An example of how Assembly Context affects how rule targets are assigned: Title 24 Part 6 Section 116 – Mandatory Requirements For Fenestration Products And Exterior Doors are different for fenestration that os site built, manufactured or field fabricated.
Manufactured
SiteBuilt
AverageDryBulbTemperature | AvgDBTemp | decimal | F | [7 empty] | Optional |  |  | This is required for EnergyPlus Site:WaterMainsTemperature object
AverageElectricityCost | AvgElecCost | decimal | cents per kW h | [7 empty] | Optional
AverageLivingUnitFloorArea | AvgLivingUnitFlrArea | decimal | ft | [10 empty] | This is floor area of a typical living unit served by the water heater. | 2013 NR ACM 5.9.1
AverageOtherFuelCost | AvgOtherFuelCost | decimal | dollar per unit | [7 empty] | Optional
Azimuth | Az | decimal | deg arc | [7 empty] | Required |  | dtyp:Azimuth | A measure of the orientation of a planar surface. The azimuth of any planar building surface element is measured in the plane upon which the building sits (the base plane). It is the angle, measured clockwise, between the true North vector and the outward pointing normal to the building surface element. The azimuth of a North-facing building surface is thus 0 degrees. Units: degrees Cardinal orientation of north, south, east and west can be derived from the Azimuth | 2013 NR ACM: 5.5.3 Roofs Roof Geometry, 5.5.4 Exterior Walls Wall Geometry, 5.5.5 Exterior Floors Floor Geometry | Required when Proj:GeometryInpType = 'Simplified', else NotInput
BallastedRoof | BallastedRoof | boolean | none | [7 empty] | Defaulted
BelowGradeStoryCount | BelowGrdStoryCnt | integer | none
BuildingAzimuth | BldgAz | decimal | deg arc |  |  |  |  | 0 | 360 |  | Required |  | dtyp:Decimal | the angle between the model Y axis and True North, measured clockwise from the Y Axis in Degrees
BuildingBoardAndSiding | BuildingBoardAndSiding | enumerated list |  | FiberCementBoard63LbPerFt3Thickness0_33In
FiberCementBoard88LbPerFt3Thickness0_33In
FiberCementBoard88LbPerFt3Thickness0_5In
FiberboardSheathing0_5In
GypsumBoard0_375In
GypsumBoard0_5In
GypsumBoard0_625In
GypsumBoard0_75In
HBPartBoard0_75In
HardBoard0_75In
HardBoardHDF50LbPerFt3Thickness0_375In
HardBoardHDF50LbPerFt3Thickness0_5In
HardBoardHDF50LbPerFt3Thickness0_625In
HardBoardHDF50LbPerFt3Thickness0_75In
MetalDeck0_0625In
MetalSiding0_0625In
OrientedStrandBoard0_5In
OrientedStrandBoard0_625In
OrientedStrandBoard0_75In
Plywood0_25In
Plywood0_375In
Plywood0_5In
Plywood0_625In
Plywood0_75In
Plywood1In
ShinglesAsbestosCementLapped0_25In
ShinglesAsphaltRollSiding0_25In
ShinglesWood16In7_5InExposure0_5In
ShinglesWoodInsulatedBackerBoardSiding0_3125In
SidingAsphaltInsulating0_5InBed0_5In
SidingWoodBevel10_0InLapped0_75In
WoodShingles0_75In
WoodShinglesPlainAndPlasticFilmFaced0_75In
BuildingTerrain | BldgTerrain | enumerated list | none | City | [6 empty] | Optional |  |  | This describes the terrain in which the building is located and has an affect on design day and annual simulations.
Country
Ocean
Suburbs
Urban
BuildingUniqueID_CEC |  | string | none |  | No | [7 empty] | xsd:string | This token uniquely identifies a whole building, developed by the California Energy Commission.
BuiltUpRoof | BuiltUpRoof | boolean | none | [7 empty] | Defaulted
CavityInsulation | CavityIns | decimal | h ft2 F per Btu | [7 empty] | CondRequired |  |  | The rated cavity insulation R-value of a CodeCategory = Composite material layer. The rated R-value should reflect the specified FramingDepth, including any reduction in R-vaue due to over-compression of cavity insulation materials. | 2012 JA4
CavityInsulationOption | CavityInsOpt | enumerated list | none | R0 | [6 empty] | CondRequired
R10
R10_R13
R11
R13
R13_R13
R15
R16
R19
R19_R13
R20
R21
R22
R23
R24_CavNR
R25
R26
R29
R30
R32
R35
R36
R38
R5
R6
R6_R13
CertificationMethod | CertificationMthd | enumerated list | none | COGEquations | [6 empty] | Required
DefaultPerformance
NFRCRated
CertificationMethod | CertificationMthd | enumerated list | none | CECDefaultPerformance_Door | [6 empty] | Required
NFRCRated_Door
ClimateZone | CliZn | enumerated list | none | ClimateZone1 | [6 empty] | Required |  |  | Defined geographic area that has a similar climate is defined as a climate zone. In the Title 24 Building Energy Standards covering the state of California there are sixteen different climate zones | 2013 T24: Climate zones are the 16 geographic areas of California for which the Commission has established typical weather data, prescriptive packages and energy budgets. Climate zone boundary descriptions are in the document "California Climate Zone Descriptions" (July 1995), incorporated herein by reference.
ClimateZone10
ClimateZone11
ClimateZone12
ClimateZone13
ClimateZone14
ClimateZone15
ClimateZone16
ClimateZone2
ClimateZone3
ClimateZone4
ClimateZone5
ClimateZone6
ClimateZone7
ClimateZone8
ClimateZone9
ClimateZoneCounty | CliZnCounty |  | none | Alameda | [6 empty] | Required |  |  | The California county where the climate zone city is located | 2013 Appendix JA2 Reference Weather/Climate Data defines the city, zipcode county locations in the different climate zones.
Alpine
Amador
Butte
Calaveras
Colusa
ContraCosta
DelNorte
ElDorado
Fresno
Glenn
Humboldt
Imperial
Inyo
Kern
Kings
Lake
Lassen
LosAngeles
Madera
Marin
Mariposa
Mendocino
Merced
Modoc
Mono
Monterey
Napa
Nevada
Orange
Placer
Plumas
Riverside
Sacramento
SanBenito
SanBernardino
SanDiego
SanFrancisco
SanJoaquin
SanLuisObispo
SanMateo
SantaBarbara
SantaClara
SantaCruz
Shasta
Sierra
Siskiyou
Solano
Sonoma
Stanislaus
Sutter
Tehama
Trinity
Tulare
Tuolumne
Ventura
Yolo
Yuba
ClimateZoneNumber | CliZnNum | integer | none | 1 | [6 empty] | Required |  |  | Numeric representation of the climate zone used in table lookups
10
11
12
13
14
15
16
2
3
4
5
6
7
8
9
CodeCategory | CodeCat | enumerated list | none | Air | [6 empty] | Compulsory |  |  | The name or code for a type of material used as a layer in construction assemblies. Used by the compliance software user interface to narrow list of material selections by category. | Joint Appendix 4 tables describe construction assemblies that are combinations of materials. It does not use the layer approach. 2013 NR ACM Material Type is used in Appendix of Default Construction Materials.
BoardAndSiding
Composite
Concrete
ConcreteSandwichPanel
FinishMaterials
ICFWall
InsulationBatt
InsulationBoard
InsulationLooseFill
InsulationSprayApplied
MasonryMaterials
MasonryUnitsFill
MasonryUnitsHollow
MasonryUnitsSolid
Membrane
MetalInsulatedPanelWall
Plastering
Roofing
SIPS Floor
SIPSRoof
SIPSWall
StrawBaleWall
Wood
CodeItem | CodeItem | enumerated list | none | AcousticTile0_375In | [6 empty] | Compulsory |  | dtyp:EnumerationConstantPermissive
AcousticTile0_5In
AcousticTile0_75In
Aggregate45LbPerFt3Thickness0_5In
Aggregate45LbPerFt3Thickness0_625In
AggregateOnMetalLath45LbPerFt3Thickness0_75In
AggregatePerliteOnMetalLathThickness0_75In
AggregatePerliteThickness0_5In
AggregatePerliteThickness0_625In
AirCavityWallRoofCeiling4InPlus
AirCeiling0_5In
AirCeiling0_75In
AirCeiling1_5In
AirCeiling3_5In
AirFloor0_5In
AirFloor0_75In
AirFloor1_5In
AirFloor3_5In
AirMetalWallFraming16Or24InOC
AirRoof0_5In
AirRoof0_75In
AirRoof1_5In
AirRoof3_5In
AirWall0_5In
AirWall0_75In
AirWall1_5In
AirWall3_5In
AluminumNoThermalBreakDoubleNoLowENoIns
AluminumNoThermalBreakDoubleNoLowER10Ins
AluminumNoThermalBreakDoubleNoLowER15Ins
AluminumNoThermalBreakDoubleNoLowER20Ins
AluminumNoThermalBreakDoubleNoLowER25Ins
AluminumNoThermalBreakDoubleNoLowER30Ins
AluminumNoThermalBreakDoubleNoLowER4Ins
AluminumNoThermalBreakDoubleNoLowER7Ins
AluminumNoThermalBreakSingleGlassStoneMetalNoIns
AluminumNoThermalBreakSingleGlassStoneMetalR10Ins
AluminumNoThermalBreakSingleGlassStoneMetalR15Ins
AluminumNoThermalBreakSingleGlassStoneMetalR20Ins
AluminumNoThermalBreakSingleGlassStoneMetalR25Ins
AluminumNoThermalBreakSingleGlassStoneMetalR30Ins
AluminumNoThermalBreakSingleGlassStoneMetalR4Ins
AluminumNoThermalBreakSingleGlassStoneMetalR7Ins
AluminumNoThermalBreakTripleOrLowENoIns
AluminumNoThermalBreakTripleOrLowER10Ins
AluminumNoThermalBreakTripleOrLowER15Ins
AluminumNoThermalBreakTripleOrLowER20Ins
AluminumNoThermalBreakTripleOrLowER25Ins
AluminumNoThermalBreakTripleOrLowER30Ins
AluminumNoThermalBreakTripleOrLowER4Ins
AluminumNoThermalBreakTripleOrLowER7Ins
AluminumThermalBreakDoubleNoLowENoIns
AluminumThermalBreakDoubleNoLowER10Ins
AluminumThermalBreakDoubleNoLowER15Ins
AluminumThermalBreakDoubleNoLowER20Ins
AluminumThermalBreakDoubleNoLowER25Ins
AluminumThermalBreakDoubleNoLowER30Ins
AluminumThermalBreakDoubleNoLowER4Ins
AluminumThermalBreakDoubleNoLowER7Ins
AluminumThermalBreakSingleGlassStoneMetalNoIns
AluminumThermalBreakSingleGlassStoneMetalR10Ins
AluminumThermalBreakSingleGlassStoneMetalR15Ins
AluminumThermalBreakSingleGlassStoneMetalR20Ins
AluminumThermalBreakSingleGlassStoneMetalR25Ins
AluminumThermalBreakSingleGlassStoneMetalR30Ins
AluminumThermalBreakSingleGlassStoneMetalR4Ins
AluminumThermalBreakSingleGlassStoneMetalR7Ins
AluminumThermalBreakTripleOrLowENoIns
AluminumThermalBreakTripleOrLowER10Ins
AluminumThermalBreakTripleOrLowER15Ins
AluminumThermalBreakTripleOrLowER20Ins
AluminumThermalBreakTripleOrLowER25Ins
AluminumThermalBreakTripleOrLowER30Ins
AluminumThermalBreakTripleOrLowER4Ins
AluminumThermalBreakTripleOrLowER7Ins
AsbestosOrCementShingles0_375In
Ash1In
AsphaltBitumenInertFill100LbPerFt3Thickness0_75In
AsphaltBitumenInertFill144LbPerFt3Thickness0_75In
Birch1In
Brick48LbPerFt3Thickness3_625In
BrickFiredClay140LbPerFt3Thickness3_625In
BuildingPaper0_0625In
BuiltUpRoofing0_375In
CaliforniaRedwood1In
Carpet0_75In
CellularPolyisocyanurate0_125In_R0_7
CellularPolyisocyanurate0_25In_R1_5
CellularPolyisocyanurate0_5In_R2_9
CellularPolyisocyanurate1In_R5_9
CellularPolyisocyanurate1_5In_R8_8
CellularPolyisocyanurate2In_R12
CellularPolyisocyanurate2_5In_R15
CellularPolyisocyanurate3In_R18
CellularPolyisocyanurate3_5In_R21
CellularPolyisocyanurate4In_R23
CellularPolyisocyanurate4_5In_R26
CellularPolyisocyanurate5In_R29
CellularPolyisocyanurate5_5In_R32
CellularPolyisocyanurate6In_R35
CellularPolyisocyanurate6_5In_R38
ClayPartGrouted130LbPerFt3Thickness6In
ClayPartGrouted130LbPerFt3Thickness8In
ClayPartGroutedInsulated130LbPerFt3Thickness6In
ClayPartGroutedInsulated130LbPerFt3Thickness8In
ClaySolidGrout130LbPerFt3Thickness6In
ClaySolidGrout130LbPerFt3Thickness8In
ClayTile0_5In
ClayTileHollow1CellDeepThickness3In
ClayTileHollow1CellDeepThickness4In
ClayTileHollow2CellDeepThickness10In
ClayTileHollow2CellDeepThickness6In
ClayTileHollow2CellDeepThickness8In
ClayTileHollow3CellDeepThickness12In
ClayTilePaver
ComplianceInsulationR0_01
ComplianceInsulationR0_02
ComplianceInsulationR0_10
ComplianceInsulationR0_20
ComplianceInsulationR0_50
ComplianceInsulationR10_00
ComplianceInsulationR10_06
ComplianceInsulationR11_00
ComplianceInsulationR11_70
ComplianceInsulationR12_00
ComplianceInsulationR12_50
ComplianceInsulationR12_55
ComplianceInsulationR12_69
ComplianceInsulationR13_00
ComplianceInsulationR13_50
ComplianceInsulationR13_99
ComplianceInsulationR14_00
ComplianceInsulationR14_14
ComplianceInsulationR14_32
ComplianceInsulationR14_60
ComplianceInsulationR15_00
ComplianceInsulationR15_54
ComplianceInsulationR16_00
ComplianceInsulationR16_20
ComplianceInsulationR16_34
ComplianceInsulationR16_58
ComplianceInsulationR16_69
ComplianceInsulationR17_00
ComplianceInsulationR17_67
ComplianceInsulationR18_00
ComplianceInsulationR19_00
ComplianceInsulationR19_63
ComplianceInsulationR1_00
ComplianceInsulationR1_35
ComplianceInsulationR1_41
ComplianceInsulationR1_54
ComplianceInsulationR20_00
ComplianceInsulationR20_05
ComplianceInsulationR21_00
ComplianceInsulationR21_18
ComplianceInsulationR21_39
ComplianceInsulationR21_60
ComplianceInsulationR22_00
ComplianceInsulationR22_48
ComplianceInsulationR23_00
ComplianceInsulationR23_70
ComplianceInsulationR24_00
ComplianceInsulationR24_80
ComplianceInsulationR24_86
ComplianceInsulationR25_00
ComplianceInsulationR25_16
ComplianceInsulationR26_00
ComplianceInsulationR27_00
ComplianceInsulationR28_00
ComplianceInsulationR28_12
ComplianceInsulationR28_63
ComplianceInsulationR29_00
ComplianceInsulationR2_00
ComplianceInsulationR2_15
ComplianceInsulationR2_19
ComplianceInsulationR2_85
ComplianceInsulationR2_89
ComplianceInsulationR30_00
ComplianceInsulationR31_00
ComplianceInsulationR32_00
ComplianceInsulationR33_00
ComplianceInsulationR34_00
ComplianceInsulationR34_93
ComplianceInsulationR35_00
ComplianceInsulationR36_00
ComplianceInsulationR37_00
ComplianceInsulationR38_00
ComplianceInsulationR3_00
ComplianceInsulationR3_63
ComplianceInsulationR3_70
ComplianceInsulationR3_80
ComplianceInsulationR4_00
ComplianceInsulationR5_00
ComplianceInsulationR5_60
ComplianceInsulationR6_00
ComplianceInsulationR6_32
ComplianceInsulationR6_46
ComplianceInsulationR7_00
ComplianceInsulationR7_10
ComplianceInsulationR7_18
ComplianceInsulationR7_39
ComplianceInsulationR7_50
ComplianceInsulationR7_60
ComplianceInsulationR8_00
ComplianceInsulationR8_07
ComplianceInsulationR9_00
ComplianceInsulationR9_40
ComplianceInsulationR9_80
ComplianceInsulationR9_83
ComplianceInsulationR9_94
Concrete100LbPerFt3Thickness10In
Concrete100LbPerFt3Thickness12In
Concrete100LbPerFt3Thickness2In
Concrete100LbPerFt3Thickness4In
Concrete100LbPerFt3Thickness6In
Concrete100LbPerFt3Thickness8In
Concrete140LbPerFt3Thickness10In
Concrete140LbPerFt3Thickness12In
Concrete140LbPerFt3Thickness2In
Concrete140LbPerFt3Thickness4In
Concrete140LbPerFt3Thickness6In
Concrete140LbPerFt3Thickness8In
Concrete80LbPerFt3Thickness10In
Concrete80LbPerFt3Thickness12In
Concrete80LbPerFt3Thickness2In
Concrete80LbPerFt3Thickness4In
Concrete80LbPerFt3Thickness6In
Concrete80LbPerFt3Thickness8In
ConcretePartGrouted105LbPerFt3Thickness10In
ConcretePartGrouted105LbPerFt3Thickness12In
ConcretePartGrouted105LbPerFt3Thickness6In
ConcretePartGrouted105LbPerFt3Thickness8In
ConcretePartGrouted115LbPerFt3Thickness10In
ConcretePartGrouted115LbPerFt3Thickness12In
ConcretePartGrouted115LbPerFt3Thickness6In
ConcretePartGrouted115LbPerFt3Thickness8In
ConcretePartGrouted125LbPerFt3Thickness10In
ConcretePartGrouted125LbPerFt3Thickness12In
ConcretePartGrouted125LbPerFt3Thickness6In
ConcretePartGrouted125LbPerFt3Thickness8In
ConcretePartGroutedInsulated105LbPerFt3Thickness10In
ConcretePartGroutedInsulated105LbPerFt3Thickness12In
ConcretePartGroutedInsulated105LbPerFt3Thickness6In
ConcretePartGroutedInsulated105LbPerFt3Thickness8In
ConcretePartGroutedInsulated115LbPerFt3Thickness10In
ConcretePartGroutedInsulated115LbPerFt3Thickness12In
ConcretePartGroutedInsulated115LbPerFt3Thickness6In
ConcretePartGroutedInsulated115LbPerFt3Thickness8In
ConcretePartGroutedInsulated125LbPerFt3Thickness10In
ConcretePartGroutedInsulated125LbPerFt3Thickness12In
ConcretePartGroutedInsulated125LbPerFt3Thickness6In
ConcretePartGroutedInsulated125LbPerFt3Thickness8In
ConcreteSandAggregateThickness6In
ConcreteSandwichPanel100PercentInsulationNoSteelInsulation1_5In
ConcreteSandwichPanel100PercentInsulationNoSteelInsulation2In
ConcreteSandwichPanel100PercentInsulationNoSteelInsulation3In
ConcreteSandwichPanel100PercentInsulationNoSteelInsulation4In
ConcreteSandwichPanel100PercentInsulationNoSteelInsulation6In
ConcreteSandwichPanel100PercentInsulationSteelInsulation1_5In
ConcreteSandwichPanel100PercentInsulationSteelInsulation2In
ConcreteSandwichPanel100PercentInsulationSteelInsulation3In
ConcreteSandwichPanel100PercentInsulationSteelInsulation4In
ConcreteSandwichPanel100PercentInsulationSteelInsulation6In
ConcreteSandwichPanel80PercentInsulationNoSteelInsulation1_5In
ConcreteSandwichPanel80PercentInsulationNoSteelInsulation2In
ConcreteSandwichPanel80PercentInsulationNoSteelInsulation3In
ConcreteSandwichPanel80PercentInsulationNoSteelInsulation4In
ConcreteSandwichPanel80PercentInsulationNoSteelInsulation6In
ConcreteSandwichPanel80PercentInsulationSteelInsulation1_5In
ConcreteSandwichPanel80PercentInsulationSteelInsulation2In
ConcreteSandwichPanel80PercentInsulationSteelInsulation3In
ConcreteSandwichPanel80PercentInsulationSteelInsulation4In
ConcreteSandwichPanel80PercentInsulationSteelInsulation6In
ConcreteSandwichPanel90PercentInsulationNoSteelInsulation1_5In
ConcreteSandwichPanel90PercentInsulationNoSteelInsulation2In
ConcreteSandwichPanel90PercentInsulationNoSteelInsulation3In
ConcreteSandwichPanel90PercentInsulationNoSteelInsulation4In
ConcreteSandwichPanel90PercentInsulationNoSteelInsulation6In
ConcreteSandwichPanel90PercentInsulationSteelInsulation1_5In
ConcreteSandwichPanel90PercentInsulationSteelInsulation2In
ConcreteSandwichPanel90PercentInsulationSteelInsulation3In
ConcreteSandwichPanel90PercentInsulationSteelInsulation4In
ConcreteSandwichPanel90PercentInsulationSteelInsulation6In
ConcreteSolidGrout105LbPerFt3Thickness10In
ConcreteSolidGrout105LbPerFt3Thickness12In
ConcreteSolidGrout105LbPerFt3Thickness6In
ConcreteSolidGrout105LbPerFt3Thickness8In
ConcreteSolidGrout115LbPerFt3Thickness10In
ConcreteSolidGrout115LbPerFt3Thickness12In
ConcreteSolidGrout115LbPerFt3Thickness6In
ConcreteSolidGrout115LbPerFt3Thickness8In
ConcreteSolidGrout125LbPerFt3Thickness10In
ConcreteSolidGrout125LbPerFt3Thickness12In
ConcreteSolidGrout125LbPerFt3Thickness6In
ConcreteSolidGrout125LbPerFt3Thickness8In
Concrete_Paver
ContinuousInsulationDoubleNoLowENoIns
ContinuousInsulationDoubleNoLowER10Ins
ContinuousInsulationDoubleNoLowER15Ins
ContinuousInsulationDoubleNoLowER20Ins
ContinuousInsulationDoubleNoLowER25Ins
ContinuousInsulationDoubleNoLowER30Ins
ContinuousInsulationDoubleNoLowER4Ins
ContinuousInsulationDoubleNoLowER7Ins
ContinuousInsulationSingleGlassStoneMetalNoIns
ContinuousInsulationSingleGlassStoneMetalR10Ins
ContinuousInsulationSingleGlassStoneMetalR15Ins
ContinuousInsulationSingleGlassStoneMetalR20Ins
ContinuousInsulationSingleGlassStoneMetalR25Ins
ContinuousInsulationSingleGlassStoneMetalR30Ins
ContinuousInsulationSingleGlassStoneMetalR4Ins
ContinuousInsulationSingleGlassStoneMetalR7Ins
ContinuousInsulationTripleOrLowENoIns
ContinuousInsulationTripleOrLowER10Ins
ContinuousInsulationTripleOrLowER15Ins
ContinuousInsulationTripleOrLowER20Ins
ContinuousInsulationTripleOrLowER25Ins
ContinuousInsulationTripleOrLowER30Ins
ContinuousInsulationTripleOrLowER4Ins
ContinuousInsulationTripleOrLowER7Ins
DouglasFirLarch1In
ExpandedPerliteOrganicBonded0_75In_R2_1
ExpandedPerliteOrganicBonded1In_R2_8
ExpandedPerliteOrganicBonded1_5In_R4_2
ExpandedPerliteOrganicBonded2In_R5_6
ExpandedPerliteOrganicBonded3In_R8_3
ExpandedPerliteOrganicBonded4In_R11
ExpandedPerliteOrganicBonded6In_R17
ExpandedPolystyrene0_25In_R1
ExpandedPolystyrene0_5In_R2_1
ExpandedPolystyrene0_75In_R3_1
ExpandedPolystyrene1In_R4_2
ExpandedPolystyrene1_25In_R5_2
ExpandedPolystyrene1_5In_R6_3
ExpandedPolystyrene1_75In_R7_3
ExpandedPolystyrene1_875In_R8
ExpandedPolystyrene1_9375In_R8_1
ExpandedPolystyrene2In_R8_3
ExpandedPolystyrene2_4375In_R10
ExpandedPolystyrene2_4In_R10
ExpandedPolystyrene3In_ R13
ExpandedPolystyrene3_3333In_R14
ExpandedPolystyrene3_4In_R14
ExpandedPolystyrene3_5In_R15
ExpandedPolystyrene4_0625In_R17
ExpandedPolystyrene4_7In_R20
ExpandedPolystyrene5_4In_R22
ExpandedPolystyrene5_95In_R25
ExpandedPolystyrene6_1In_R25
ExpandedPolystyrene6_875In_R29
ExpandedPolystyrene8_6In_R35
ExpandedPolystyreneXPS0_25In_R1_25
ExpandedPolystyreneXPS0_5In_R2_50
ExpandedPolystyreneXPS0_75In_R3_75
ExpandedPolystyreneXPS1In_R5
ExpandedPolystyreneXPS1_25In_R6_25
ExpandedPolystyreneXPS1_5In_R7_50
ExpandedPolystyreneXPS1_75In_R8_75
ExpandedPolystyreneXPS1_875In_R9_37
ExpandedPolystyreneXPS2In_R10
ExpandedPolystyreneXPS2_5In_R12_50
ExpandedPolystyreneXPS3In_R15
ExpandedPolystyreneXPS3_5In_R17_50
ExpandedPolystyreneXPS4In_R20
ExpandedPolystyreneXPS4_5In_R22_50
ExpandedPolystyreneXPS5In_R25
ExpandedPolystyreneXPS5_5In_R27_50
ExpandedPolystyreneXPS6In_R30
ExpandedPolystyreneXPS6_5In_R32_50
ExpandedPolystyreneXPS8In_R40
ExpandedPolystyreneXPS8_5In_R42_50
ExpandedPolyurethane0_5In_R3_1
ExpandedPolyurethane0_75In_R4_7
ExpandedPolyurethane1In_R6_3
ExpandedPolyurethane1_25In_R7_8
ExpandedPolyurethane2In_R12_6
FiberCementBoard63LbPerFt3Thickness0_33In
FiberCementBoard88LbPerFt3Thickness0_33In
FiberCementBoard88LbPerFt3Thickness0_5In
FiberboardSheathing0_5In
GlassFiberBatt10In_ R30_CEC_Default
GlassFiberBatt12In_ R38_CEC_Default
GlassFiberBatt3_5In_ R11_CEC_Default
GlassFiberBatt3_5In_ R13_CEC_Default
GlassFiberBatt3_5In_ R15_CEC_Default
GlassFiberBatt4In
GlassFiberBatt4_5In
GlassFiberBatt5In
GlassFiberBatt5_5In_ R19_CEC_Default
GlassFiberBatt5_5In_ R21_CEC_Default
GlassFiberBatt6In
GlassFiberBatt6_5In
GlassFiberBatt7_25In_ R25_CEC_Default
GlassFiberBatt7_25In_ R30_CEC_Default
GlassFiberBatt8_25In_ R30_CEC_Default
GypsumBoard0_375In
GypsumBoard0_5In
GypsumBoard0_625In
GypsumBoard0_75In
GypsumPartitionBlock3Cell4x12x30Thickness4In
GypsumPartitionBlock4Cell3x12x30Thickness3In
GypsumPlaster80LbPerFt3Thickness0_5In
GypsumPlaster80LbPerFt3Thickness0_625In
GypsumPlasterOnMetalLath70LbPerFt3Thickness0_75In
GypsumPlasterOnMetalLath80LbPerFt3Thickness0_75In
HBPartBoard0_75In
HardBoard0_75In
HardBoardHDF50LbPerFt3Thickness0_375In
HardBoardHDF50LbPerFt3Thickness0_5In
HardBoardHDF50LbPerFt3Thickness0_625In
HardBoardHDF50LbPerFt3Thickness0_75In
Hardwood0_5In
Hardwood0_75In
Hardwood1In
ICF1_5InPolyurethaneEachSideConcrete6In
ICF1_5InPolyurethaneEachSideConcrete8In
ICF2InEPSEachSideConcrete6In
ICF2InEPSEachSideConcrete8In
ICF2InPolyurethaneEachSideConcrete6In
ICF2InPolyurethaneEachSideConcrete8In
ICF2InXPSEachSideConcrete6In
ICF2InXPSEachSideConcrete8In
ICF2_5InEPSEachSideConcrete6In
ICF2_5InEPSEachSideConcrete8In
ICF3InEPSEachSideConcrete6In
ICF3InEPSEachSideConcrete8In
ICF3InXPSEachSideConcrete6In
ICF3InXPSEachSideConcrete8In
ICF4InEPSEachSideConcrete6In
ICF4InEPSEachSideConcrete8In
ICF4InXPSEachSideConcrete6In
ICF4InXPSEachSideConcrete8In
ICF4_5InPolyurethaneEachSideConcrete6In
ICF4_5InPolyurethaneEachSideConcrete8In
LightRoof0_4In
LinoleumCorkTile0_25In
LooseFillMineralFiber2LbPerFt3Thickness13_75In
LooseFillMineralFiber2LbPerFt3Thickness4In
LooseFillMineralFiber2LbPerFt3Thickness6_5In
LooseFillMineralFiber2LbPerFt3Thickness7_5In
LooseFillMineralFiber2LbPerFt3Thickness8_25In
LooseFillMineralFiberClosedSidewallsThickness3_5In
Maple1In
MasticAsphaltHeavy20PercentGrit1In
MetalDeck0_0625In
MetalInsulatedPanel2In
MetalInsulatedPanel2_5In
MetalInsulatedPanel3In
MetalInsulatedPanel4In
MetalInsulatedPanel5In
MetalInsulatedPanel6In
MetalSiding0_0625In
MetalStandingSeam0_0625In
MortarCementThickness1In
MortarCementThickness1_75In
Oak1In
OrientedStrandBoard0_5In
OrientedStrandBoard0_625In
OrientedStrandBoard0_75In
PerliteBoard0_75In_R1_9
PerliteBoard1In_R2_5
PerliteBoard1_5In_R3_8
PerliteBoard2In_R5_0
PerlitePlaster25LbPerFt3Thickness0_5In
PerlitePlaster38LbPerFt3Thickness0_5In
PineOvenDried1In
PlasterSandAggregateThickness1In
Plywood0_25In
Plywood0_375In
Plywood0_5In
Plywood0_625In
Plywood0_75In
Plywood1In
Plywood1_25In
Plywood1_5In
PulpboardOrPaperPlasterThickness0_5In
R24BattWall8In_R24
RammedEarth
Roof10LbPerFt2Thickness1In
Roof15LbPerFt2Thickness1_5In
Roof25LbPerFt2Thickness2_5In
Roof5LbPerFt2Thickness0_5In
RoofGravel0_5In
RoofGravel1In
RoofingFelt0_125In
RubberTile1In
SIPS Floor
SIPSCrawlSpaceR22Double2xSpline6_5In
SIPSCrawlSpaceR22IJoistSpline6_5In
SIPSCrawlSpaceR22Single2xSpline6_5In
SIPSCrawlSpaceR28Double2xSpline8_25In
SIPSCrawlSpaceR28IJoistSpline8_25In
SIPSCrawlSpaceR28Single2xSpline8_25In
SIPSCrawlSpaceR33Double2xSpline6_5In
SIPSCrawlSpaceR33IJoistSpline6_5In
SIPSCrawlSpaceR33Single2xSpline6_5In
SIPSCrawlSpaceR36IJoistSpline10_25In
SIPSCrawlSpaceR36Single2xSpline10_25In
SIPSNoCrawlSpaceR22Double2xSpline6_5In
SIPSNoCrawlSpaceR22IJoistSpline6_5In
SIPSNoCrawlSpaceR22Single2xSpline6_5In
SIPSNoCrawlSpaceR28Double2xSpline8_25In
SIPSNoCrawlSpaceR28IJoistSpline8_25In
SIPSNoCrawlSpaceR28Single2xSpline8_25In
SIPSNoCrawlSpaceR33Double2xSpline6_5In
SIPSNoCrawlSpaceR33IJoistSpline6_5In
SIPSNoCrawlSpaceR33Single2xSpline6_5In
SIPSNoCrawlSpaceR36IJoistSpline10_25In
SIPSNoCrawlSpaceR36Single2xSpline10_25In
SIPSR14Double2xSpline4_5In
SIPSR14IJoistSpline4_5In
SIPSR14MetalSpline48In
SIPSR14OSBSpline4_5In
SIPSR14Single2xSpline4_5In
SIPSR18Double2xSpline4_5In
SIPSR18IJoistSpline4_5In
SIPSR18OSBSpline4_5In
SIPSR18Single2xSpline4_5In
SIPSR22Double2xSpline6_5In
SIPSR22IJoistSpline6_5In
SIPSR22MetalSpline48In
SIPSR22OSBSpline6_5In
SIPSR22Single2xSpline6_5In
SIPSR28Double2xSpline8_25In
SIPSR28Double2xSpline8_5In
SIPSR28IJoistSpline8_25In
SIPSR28IJoistSpline8_5In
SIPSR28MetalSpline48In
SIPSR28OSBSpline8_25In
SIPSR28OSBSpline8_5In
SIPSR28Single2xSpline8_25In
SIPSR28Single2xSpline8_5In
SIPSR33Double2xSpline6_5In
SIPSR33IJoistSpline6_5In
SIPSR33OSBSpline6_5In
SIPSR33Single2xSpline6_5In
SIPSR36Double2xSpline10_25In
SIPSR36IJoistSpline10_25In
SIPSR36MetalSpline48In
SIPSR36OSBSpline10_25In
SIPSR36Single2xSpline10_25In
SIPSR44Double2xSpline12_25In
SIPSR44IJoistSpline12_25In
SIPSR44OSBSpline12_25In
SIPSR44Single2xSpline12_25In
SIPSR55Double2xSpline10_25In
SIPSR55IJoistSpline10_25In
SIPSR55OSBSpline10_25In
SIPSR55Single2xSpline10_25In
SIPS_CrawlSpaceR36Double2xSpline10_25In
SIPS_NoCrawlSpaceR36Double2xSpline10_25In
SandAggregateOnMetalLathThickness0_75In
SandAggregateThickness0_375In
SandAggregateThickness0_5In
SandAggregateThickness0_625In
SandAggregateThickness0_75In
ShinglesAsbestosCementLapped0_25In
ShinglesAsphaltRollSiding0_25In
ShinglesWood16In7_5InExposure0_5In
ShinglesWoodInsulatedBackerBoardSiding0_3125In
SidingAsphaltInsulating0_5InBed0_5In
SidingWoodBevel10_0InLapped0_75In
SinglePlyRoofing0_25In
Slate0_5In
SlateOrTile0_5In
SprayCellulosicFiber4_6LbPerFt3Thickness3_5In
SprayCellulosicFiber4_6LbPerFt3Thickness4In
SprayCellulosicFiber4_6LbPerFt3Thickness4_5In
SprayCellulosicFiber4_6LbPerFt3Thickness5In
SprayCellulosicFiber4_6LbPerFt3Thickness5_5In
SprayCellulosicFiber4_6LbPerFt3Thickness6In
SprayCellulosicFiber4_6LbPerFt3Thickness6_5In
SprayGlassFiber3_9LbPerFt3Thickness3_5In
SprayGlassFiber3_9LbPerFt3Thickness4In
SprayGlassFiber3_9LbPerFt3Thickness4_5In
SprayGlassFiber3_9LbPerFt3Thickness5In
SprayGlassFiber3_9LbPerFt3Thickness5_5In
SprayGlassFiber3_9LbPerFt3Thickness6In
SprayGlassFiber3_9LbPerFt3Thickness6_5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness3_5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness4In
SprayPolyurethaneFoam0_5LbPerFt3Thickness4_5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness5_5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness6In
SprayPolyurethaneFoam0_5LbPerFt3Thickness6_5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness3_5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness4In
SprayPolyurethaneFoam3_0LbPerFt3Thickness4_5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness5_5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness6In
SprayPolyurethaneFoam3_0LbPerFt3Thickness6_5In
Stone1In
StrawBaleIntExtStucco18In
StructuralGlazingDoubleNoLowENoIns
StructuralGlazingDoubleNoLowER10Ins
StructuralGlazingDoubleNoLowER15Ins
StructuralGlazingDoubleNoLowER20Ins
StructuralGlazingDoubleNoLowER25Ins
StructuralGlazingDoubleNoLowER30Ins
StructuralGlazingDoubleNoLowER4Ins
StructuralGlazingDoubleNoLowER7Ins
StructuralGlazingSingleGlassStoneMetalNoIns
StructuralGlazingSingleGlassStoneMetalR10Ins
StructuralGlazingSingleGlassStoneMetalR15Ins
StructuralGlazingSingleGlassStoneMetalR20Ins
StructuralGlazingSingleGlassStoneMetalR25Ins
StructuralGlazingSingleGlassStoneMetalR30Ins
StructuralGlazingSingleGlassStoneMetalR4Ins
StructuralGlazingSingleGlassStoneMetalR7Ins
StructuralGlazingTripleOrLowENoIns
StructuralGlazingTripleOrLowER10Ins
StructuralGlazingTripleOrLowER15Ins
StructuralGlazingTripleOrLowER20Ins
StructuralGlazingTripleOrLowER25Ins
StructuralGlazingTripleOrLowER30Ins
StructuralGlazingTripleOrLowER4Ins
StructuralGlazingTripleOrLowER7Ins
Stucco0_375In
Stucco0_875In
Stucco1Coat
Stucco3Coat
StuccoSyntheticEIFS_Finish1In
Terrazzo1In
TileGap0_75In
VaporPermeableFelt0_125In
VaporSeal2LayerMopped15LbFelt0_25In
VaporSealPlasticFilm0_0625In
VermiculiteAggregate45LbPerFt3Thickness0_5In
Wood0_5In
Wood1In
Wood2In
Wood4In
WoodShingles0_75In
WoodShinglesPlainAndPlasticFilmFaced0_75In
WoodSiding0_5In
CoilCoolingCapacity | CoilClgCap | decimal | Btu per h |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
CoilCoolingCapacityHydronic | CoilClgCapHydronic | decimal | Btu per h |  | No | [5 empty] | Defaulted |  | dtyp:DecimalNonnegative
CoilHeatingCapacity | CoilHtgCap | decimal | Btu per h |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
CoilHeatingCapacityHydronic | CoilHtgCapHydronic | decimal | Btu per h |  | No | [5 empty] | Defaulted |  | dtyp:DecimalNonnegative
CoincidentWetBulb | CoinWB | decimal | F | [7 empty] | Required |  |  | The wet bulb termperature occuring coincident with a specific dry bulb temperature | 2013 Appendix JA2 Reference Weather/Climate Data has the mean coincident wet bulb termperature for every dry bulb measurement used for cooling calulations
CommercialRefrigerationLatentFraction | CommRfrgLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
CommercialRefrigerationLostFraction | CommRfrgLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
CommercialRefrigerationRadiationFraction | CommRfrgRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
CommercialRefrigerationRemoteCondenserFraction | CommRfrgRemCndsrFrac | decimal | none | [7 empty] | Optional
CompatibleSurfaceType | CompatibleSurfType | enumerated list | none | Ceiling | [6 empty] | Required |  |  | Identifies the valid surface object type that the ConstructionAssembly can be assigned to. | None. Used to QC valid object assignments in UI/compliance ruleset.
ExteriorFloor
ExteriorWall
InteriorFloor
InteriorWall
Roof
UndergroundFloor
UndergroundWall
ConditioningType | CondgType | enumerated list | none | DirectlyConditioned | [6 empty] | Required |  |  | One of a list of categories which characterize the type of conditioning for a space. | There are definitions for the following types of space conditioning in the Standards: Conditioned Space, DirectlyConditioned Space, IndirectlyProcess SpaceRefrigerated SpaceUnconditioned Space Plenum in T24 is handled as conditioned space. Ref: NR ACM 2.3.1.1 Directly Conditioned Space Return Air Plenums 2013 NR ACM This maps to Thermal Block Type an attribute of building descriptor, Thermal Block which has the value of directly conditioned, indirectly conditioned, unconditioned or plenum. 90.1 2007 Sec 3.2 Definitions; Table 5.5.1-8
IndirectlyConditioned
Plenum
Unconditioned
ConstructAssemblyReference | ConsAssmRef | reference | none | [7 empty] | Required | ConsAssm
ConstructionAssemblyNotes | ConsAssmNotes | string | none | [7 empty] | CondRequired
ControlSystemType | CtrlSysType | enumerated list | none | DirectDigitalControlsToZoneLevel | [9 empty] | This defines what type of control system is used in the building to control energy use. | 2013 NR ACM 5.6.1
NoControlSystem
OtherControlSystem
Coordinate | Coord | decimal | ft |  | Yes | 3 | 3 |  |  |  | Required |  |  | The x, y or z length measured from an origin.
CRRCAgedEmittance | CRRCAgedEmit | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated 3-year aged thermal emittance of a roofing material. | NACM-5.5.1, Reflectance
CRRCAgedReflectance | CRRCAgedRefl | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated 3-year aged solar reflectance of a roofing material. | NACM-5.5.1, Reflectance
CRRCAgedSRI | CRRCAgedSRI | integer | none | [7 empty] | CondRequired |  |  | The CRRC rated 3-year aged Solar Reflective Index (SRI) of a roofing material.The SRIis a measure defined by the Lawrence Berkeley National Laboratory as the roof's ability to reject solar heat, as shown by a small temperature rise. | 2013 T24 Part 6, 110.8(i)3
CRRCInitialEmittance | CRRCInitialEmit | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated initial thermal emittance of a roofing material. | NACM-5.5.1, Reflectance
CRRCInitialReflectance | CRRCInitialRefl | decimal | none |  |  |  |  | 0 | 1 |  | CondRequired |  |  | The CRRC rated initial solar reflectance of a roofing material. | NACM-5.5.1, Reflectance
CRRCInitialSRI | CRRCInitialSRI | integer | none | [7 empty] | CondRequired |  |  | The CRRC rated initial Solar Reflective Index (SRI) of a roofing material.The SRIis a measure defined by the Lawrence Berkeley National Laboratory as the roof's ability to reject solar heat, as shown by a small temperature rise. | 2013 T24 Part 6, 110.8(i)3
CRRCProductID | CRRCProdID | string | none | [7 empty] | CondRequired |  |  | The CRRC product identification number for the roofing product
CRRCSolarReflectanceIndex | CRRCSRI | decimal | none | [7 empty] | Optional
Day | Day | integer | none | [7 empty] | Optional |  |  | Interger value represents the day of the month and therefore is in the range of 1-31, with limits on the high end depending on the value for the Month property
DaylightingControlType | DayltgCtrlType | enumerated list | none | Continuous | [6 empty] | Defaulted |  |  | The type of control that is used to control the electric lighting in response to daylight available at the reference point. | 2013 NR ACM
ContinuousPlusOff
None
SteppedSwitching
DaylitAreaType | DaylitAreaType | enumerated list | none | PrimarySidelit | [6 empty] | Defaulted |  |  | Defines whether the daylighting control area is under a skylight or next to a window or some distance from a window | 2013 NR ACM 5.4.5
SecondarySidelit
SkylitDaylit
DayOfWeek | DayOfWeek | enumerated list | none | Friday | [6 empty] | Optional
Monday
Saturday
Sunday
Thursday
Tuesday
Wednesday
DefaultDaylightingControls | DefaultDayltgCtrls | boolean | none | [7 empty] | Optional
DesignDayWeatherFile | DDWeatherFile | string | none | [7 empty] | Required |  |  | Name of file containing design day information
DesignDryBulb | DsgnDB | decimal | F | [7 empty] | Required |  |  | The design dry bulb temperature is the used for equipment sizing calculations | 2013 T24 Section 140.4 and Joint Appendix 2
DesignDryBulbRange | DsgnDBRng | decimal | F | [7 empty] | Required |  |  |  | 2013 NR ACM section 5.2.3 Geographic and Climate Data Design Day Data
DesignInfiltrationRate | DsgnInfRt | decimal | ft3 per min ft2 |  | Yes | 0 | 4 |  |  |  | Defaulted |  |  | Design infiltration airflow | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
Diffusing | Diffusing | boolean | none | [7 empty] | Optional
DisableDaylightingControls | DisableDayltgCtrls | boolean | none | [7 empty] | Optional
DisplayPerimeter | DisplayPerim | decimal | ft | [7 empty] | Optional |  |  | The length of an exterior wall in a building of CBC Occupancy Group B; F Div1, or M, that immediately abuts a public sidewalk, measured at the sidewalk level for each story that abuts a public sidewalk. It can be derived using the CBC Occupancy type and the Width dimension of the Exterior Wall. | T24 definition: DISPLAY PERIMETER is the length of an exterior wall in a building of CBC Occupancy Group B; F Div1, or M, that immediately abuts a public sidewalk, measured at the sidewalk level for each story that abuts a public sidewalk.
DoorAutomaticCloser | DrAutoCloser | boolean | none |  | No | [5 empty] | Defaulted
DoorConstructionReference | DrConsRef | reference | none | [7 empty] | Optional | DrCons
DwellingUnitTypeArea | DwellingUnitTypeArea | decimal | ft2 |  | Yes | 0 | 6 |  |  |  | CondRequired |  | dtyp:DecimalNonnegative
DwellingUnitTypeCount | DwellingUnitTypeCnt | integer | none |  | Yes | 0 | 6 |  |  |  | CondRequired |  | dtyp:IntegerNonnegative
DynamicGlazing | DynamicGlz | boolean | none | [7 empty] | Required
Elevation | Elevation | decimal | ft |  |  |  |  | -300 | 8899 |  | Required |  |  | The height of a land surface above sea level | Joint Appendix 2 defines climate data and includes latitude, longitude and elevation for the selected representative city in each of the 16 climate zones.
ElevatorCount | ElevCnt | integer | none | [7 empty] | Optional |  |  | The number of elevators. | 2013 NR ACM
ElevatorLatentFraction | ElevLatFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
ElevatorLostFraction | ElevLostFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
ElevatorPower | ElevPwr | decimal | W | [7 empty] | Optional |  |  | The power for each elevator in the associated elevator count | 2013 NR ACM | NOTE that this is the power per elevator rather than the total elevator power in a space.
ElevatorRadiationFraction | ElevRadFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
ElevatorScheduleReference | ElevSchRef | reference | none | [7 empty] | Defaulted | Sch |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
EnableWindowShades | EnableWinShades | boolean | none | [7 empty] | Defaulted
EnclosedSpace | EnclosedSpc | boolean | none | [7 empty] | Optional
EndDay | EndDay | integer | none |  | Yes | 53 | 53 |  |  |  | Required |  |  | The day of the month, that the Schedule week ends on
EndMonth | EndMonth | integer | none |  | Yes | 53 | 53 |  |  |  | Required |  |  | The month of the year that the Schedule week ends on
EnvelopeStatus | EnvStatus | enumerated list | none | Altered | [6 empty] | Defaulted |  |  |  | 2013 NR ACM
Existing
New
EscalatorCount | EscalCnt | integer | [8 empty] | Optional |  |  | The number of escalators. | 2013 NR ACM
EscalatorLatentFraction | EscalLatFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
EscalatorLostFraction | EscalLostFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
EscalatorPower | EscalPwr | decimal | W | [7 empty] | Optional |  |  | The power for each escalator in the associated escalator count for a space. | 2013 NR ACM | NOTE that this is the power per escalator rather than the total escalator power in a space.
EscalatorRadiationFraction | EscalRadFrac | decimal | none | [7 empty] | Optional |  |  |  | 2013 NR ACM
EscalatorScheduleReference | EscalSchRef | reference | none | [7 empty] | Defaulted | Sch |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
ExhaustAirChangesPerHour | ExhACH | decimal | ACH | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
ExhaustPerArea | ExhPerArea | decimal | ft3 per min ft2 | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
ExhaustPerSpace | ExhPerSpc | decimal | ft3 per min | [7 empty] | Optional
ExteriorSolarAbsorptance | ExtSolAbs | decimal | none | [7 empty] | Optional |  |  | Represents the fraction of incident solar radiation that is absorbed by the outward facing surface of the overall ConstructionAssembly, with respect to the Space that the surface is assigned to. For roof, calculated from CRRCAgedReflectance. For other surfaces, The value is defaulted based on specification of OutsideFinish or OutsideColor, or the following values if those properties are not defined: ExtWall/IntWall: 0.7 Ceilings: 0.7 ExtFlr/IntFlr: 0.7
ExteriorSolarAbsorptance | ExtSolAbs | decimal | none | [7 empty] | Required |  |  | Represents the fraction of incident solar radiation that is absorbed by the outward facing surface of the overall ConstructionAssembly, with respect to the Space that the surface is assigned to. For roof, calculated from CRRCAgedReflectance. For other surfaces, The value is defaulted based on specification of OutsideFinish or OutsideColor, or the following values if those properties are not defined: ExtWall/IntWall: 0.7 Ceilings: 0.7 ExtFlr/IntFlr: 0.7
ExteriorThermalAbsorptance | ExtThrmlAbs | decimal | none | [7 empty] | Optional |  |  | Represents the fraction of incident long wavelength radiation that is absorbed by the outward facing surface of the overall ConstructionAssembly, with respect to the Space that the surface is assigned to. For roof, calculated from CRRCAgedEmittance. For other surfaces, the value is defaulted based on specification of OutsideFinish or OutsideColor, or the following values if those properties are not defined: ExtWall/IntWall: 0.9 Ceilings: 0.9 ExtFlr/IntFlr: 0.9
ExteriorThermalAbsorptance | ExtThrmlAbs | decimal | none | [7 empty] | Required |  |  | Represents the fraction of incident long wavelength radiation that is absorbed by the outward facing surface of the overall ConstructionAssembly, with respect to the Space that the surface is assigned to. For roof, calculated from CRRCAgedEmittance. For other surfaces, the value is defaulted based on specification of OutsideFinish or OutsideColor, or the following values if those properties are not defined: ExtWall/IntWall: 0.9 Ceilings: 0.9 ExtFlr/IntFlr: 0.9
ExteriorVisibleAbsorptance | ExtVisAbs | decimal | none | [7 empty] | Optional |  |  | Represents the fraction of incident visible wavelength radiation that is absorbed by the outward facing surface of the overall ConstructionAssembly, with respect to the Space that the surface is assigned to. The value is defaulted based on specification of OutsideFinish or OutsideColor, or the following values if those properties are not defined: ExtWall/IntWall: 0.5 Ceilings: 0.3 ExtFlr/IntFlr: 0.8
ExteriorVisibleAbsorptance | ExtVisAbs | decimal | none | [7 empty] | Required |  |  | Represents the fraction of incident visible wavelength radiation that is absorbed by the outward facing surface of the overall ConstructionAssembly, with respect to the Space that the surface is assigned to. The value is defaulted based on specification of OutsideFinish or OutsideColor, or the following values if those properties are not defined: ExtWall/IntWall: 0.5 Ceilings: 0.3 ExtFlr/IntFlr: 0.8
FenestrationConstructionReference | FenConsRef | reference | none | [7 empty] | Compulsory | FenCons
FenestrationFraming | FenFrm | enumerated list | none | [7 empty] | CondRequired |  |  | The type of frame used for a fenestration product defined in the CBECC NR input data model text file.
FenestrationPanes | FenPanes | enumerated list | none | DoublePane | [6 empty] | CondRequired
GlassBlock
SinglePane
TranslucentOrTransparentPanel
FenestrationProductType | FenProdType | enumerated list | none | CurtainWall | [6 empty] | CondRequired
FixedWindow
GlazedDoor
NotApplicable
OperableWindow
Skylight
FenestrationType | FenType | enumerated list | none | Skylight | [6 empty] | Required
VerticalFenestration
FieldAppliedCoating | FieldAppliedCoating | boolean | none | [7 empty] | CondRequired |  |  | Defines whether a roof coating is field or factory applied. Required for ACM aged reflectance equation. | NACM-5.5.1, Reflectance
FixedSeating | FxdSeat | boolean | none | [7 empty] | Defaulted
FixtureType | FxtrType | enumerated list | none | NotInCeiling | [6 empty] | Optional |  |  | Enumeration type for determining luminaire heat gain distribution
RecessedOrDownlight
RecessedWithLens
FloorArea | FlrArea | decimal | ft2 | [7 empty] | Optional
FloorAreaGross |  | decimal | ft2 | [10 empty] | The total floor area inside the building envelope, including the external walls, and excluding the roof
FloorToCeilingHeight | FlrToCeilingHgt | decimal | ft | [7 empty] | Required |  |  | The measurement of height from the top surface of the floor to the bottom surface of the ceiling in an enclosed space. | Floor to Ceiling Height measurement is used in several places in the Standards e.g. in Section Section 131 Indoor Lighting Controls That Shall Be Installed, Floor to Ceiling Height is used in calculating skylit daylight areas. | Required when Project:GeometryInputType = 'Simplified', else NotInput
FloorToCeilingHeight | FlrToCeilingHgt | decimal | ft |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative | The measurement of height from the top surface of the floor to the bottom surface of the ceiling in an enclosed space. | Floor to Ceiling Height measurement is used in several places in the Standards e.g. in Section Section 131 Indoor Lighting Controls That Shall Be Installed, Floor to Ceiling Height is used in calculating skylit daylight areas.
FloorToFloorHeight | FlrToFlrHgt | decimal | ft | [7 empty] | Required |  |  | The measurement of height from the top surface of the floor to the top surface of the floor in the above story space. | 2013 NR ACM | Required when Project:GeometryInputType = 'Simplified', else NotInput
FloorZ | FlrZ | decimal | ft | [7 empty] | Optional |  |  | Need definition | 2013 NR ACM | Required when Project:GeometryInputType = 'Simplified', else NotInput
FramingConfiguration | FrmConfig | enumerated list | none | Floor16inOC | [6 empty] | CondRequired |  |  | The frame member spacing or other geometric configuration of a CodeCategory = Composite material. | 2013 JA4, referenced in various sections
Floor24inOC
Roof16inOC
Roof24inOC
Roof48inOC
RoofMetalScrewDown
RoofMetalStandingSeam
RoofMetalStandingSeamFilledCavity
Wall16inOC
Wall24inOC
WallAWS24inOC
WallAWS48inOC
WallMetalDoubleLayerBatt
WallMetalSingleLayerBatt
FramingDepth | FrmDepth | enumerated list | none | 0_5In | [6 empty] | CondRequired |  |  | The frame member depth of a CodeCategory = Composite material. | 2013 JA4, referenced in various sections
0_75In
11_25In
1In
1_5In
2In
2_5In
3In
3_5In
4In
4_5In
5In
5_5In
7_25In
9_25In
FramingMaterial | FrmMat | enumerated list | none | Metal | [6 empty] | CondRequired |  |  | The framing material used in a CodeCategory = Composite material. | 2013 JA4, referenced in various sections
Wood
FunctionClassificationMethod | FuncClassMthd | enumerated list | none | AreaCategoryMethod | [6 empty] | Optional |  |  | One of two methods of assigning building occupancy for the project - either complete building or at the space level. This is dependent on whether the user have submitted lighting plans for the whole building or not. | 2013 NR ACM building classification method assigns whole building or space by space occupancy type. 2008 Title 24 Part 6) Tables 146E and 146F) and 2008 NR ACM Tables N2-5, N2-6 and N2-7 - in lighting compliance there are two levels that are similar: the complete buildng or area occupancy.
FunctionScheduleGroup | FuncSchGrp | enumerated list | none | Assembly | [6 empty] | Optional |  |  | A type specifying occupancy function categories used to determine schedules. | 2008 NR ACM tables N2-8 through N2-12 are defined by these Load Schedule Occupancy types 2013 NR ACM Appendix C schedules in tables C12 - C16 use the same occupancy types
Data
Health
Laboratory
Manufacturing
Office
Parking
ResidentialCommon
ResidentialLiving
Restaurant
Retail
School
Warehouse
GasEquipmentLatentFraction | GasEqpLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
GasEquipmentLostFraction | GasEqpLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
GasEquipmentPower | GasEqpPwr | decimal | Btu per h
GasEquipmentPowerDensity | GasEqpPwrDens | decimal | Btu per h ft2 | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
GasEquipmentRadiationFraction | GasEqpRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
GasType | GasType | enumerated list | none | [7 empty] | Required
GlareAzimuth | GlrAz | decimal | deg arc | [7 empty] | Optional |  |  | View angle for calculating glare index
GlazingTint | GlzTint | enumerated list | none | ClearGlazing | [6 empty] | CondRequired |  |  | Has values of clear and tinted and is used in assigning mandatory default SHGC values. | Glazing Tint is used to establish Solar Heat Gain Coefficient of fenestration products. Specifically Table 116-B assigns SHGC dependent on Glazing Tint value. 2013 NR ACM Glazing Tint is only mentioned in section on Switchable glazing which describes a technology of applying an electric current to liquid crystal windows to darken the window simulating a tint.
TintedGlazing
GreenhouseGardenWindow | GreenhouseGardenWin | boolean | none | [7 empty] | CondRequired |  |  | Used in selection of default properties
HasProcessExhaust | HasProcExh | boolean | none | [7 empty] | Defaulted
HeatCapacity | HtCap | decimal | Btu per ft2 F | [10 empty] | Used in rules derived from the JA IV tables that assign Heat Capacity, the amount of heat necessary to raise the temperature in unit area of all the components of a construction assembly by 1degree F. | Title 24 and JA II both define Heat Capacity as the amount of heat necessary to raise the temperature of all the components of a unit area in an assembly by 1°F. In JA IV Heat capacity (HC) values are provided in Tables 4.3.5 to Table 4.3.12 and HC units are defined in Table 4.6.2 New 2013 NR ACM states: ... use volume, density, and specific heat of the component wall materials to calculate the heat capacity
HeatGainRadiantFraction | HtGnRadFrac | decimal | none |  |  |  |  | 0 | 1 |  | Required |  |  | Fraction of luminaire radiant heat gain going to space surfaces | 2013 Draft ACM Sec.5.4.3 Table 18
HeatGainSpaceFraction | HtGnSpcFrac | decimal | none |  |  |  |  | 0 | 1 |  | Required |  |  | Fraction of luminaire heat gain going to space air. | 2013 Draft ACM Sec.5.4.3 Table 18
Height | Hgt | decimal | ft | [7 empty] | CondRequired |  |  | Measures the vertical extent of a vertical rectangular surface such as a wall or door or a space. Units: feet. | Height is used in the Standards to measure the vertical extent of a building component e.g. Wall, or the vertical distance between two building components e.g. between the ceiling and the roof. | Required when GeometryInpType = Simplified and window shades specified, else NotInput
Height | Hgt | decimal | ft | [7 empty] | CondRequired |  |  | Describes the height of the underground wall, i.e. the depth to the ground surface. | 2013 NACM 5.5.9, Slab Floor Geometry
HighRiseResidentialConditionedFloorArea | HighRiseResCondFlrArea | decimal | ft2 | [7 empty] | Optional
HighRiseResidentialLivingUnitCount | HighRiseResLivingUnitCnt | integer | none |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:IntegerNonnegative | The total number of high-rise residential or hotel/motel living units in the building
HolidayReference | HolidayReference | reference | none |  | Yes | 0 | 15 |  |  |  | Optional | Holiday
HotelModelGuestRoomConditionedFloorArea | HotelMotelGuestRmCondFlrArea | decimal | ft2 | [7 empty] | Optional
HotelMotelGuestRoomCount | HotelMotelGuestRmCnt | integer | none |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:IntegerNonnegative
HotWaterHeatingScheduleReference | HotWtrHtgSchRef | reference | none | [7 empty] | Optional | Sch |  | Reference to a unique identification name for a schedule in a library of hot water heating type
HotWaterHeatingTotal | HotWtrHtgTot | decimal | gal per h | [7 empty] | Optional
HotWaterSupplyTemperature | HotWtrSupTemp | decimal | F | [7 empty] | Optional
HotWaterSupplyTemperatureScheduleReference | HotWtrSupTempSchRef | reference | none | [7 empty] | Optional | Sch
Hour | Hr | decimal | none |  | Yes | 24 | 24 |  |  |  | Compulsory |  |  | The percentage of a full load to be applied for a specified hour of the day. | Load Percentage Hourly is the value used in the schedule tables N2-8 through N2-12
Hour | Hr | enumerated list | none | Charge | No | 24 | 24 |  |  |  | Compulsory
Discharge
Off
HVACAutoSizing | HVACAutoSizing | boolean | none | [7 empty] | Optional
ICF Wall | CF Wall | enumerated list |  | ICF1_5InPolyurethaneEachSideConcrete6In
ICF1_5InPolyurethaneEachSideConcrete8In
ICF2InEPSEachSideConcrete6In
ICF2InEPSEachSideConcrete8In
ICF2InPolyurethaneEachSideConcrete6In
ICF2InPolyurethaneEachSideConcrete8In
ICF2InXPSEachSideConcrete6In
ICF2InXPSEachSideConcrete8In
ICF3InEPSEachSideConcrete6In
ICF3InEPSEachSideConcrete8In
ICF3InXPSEachSideConcrete6In
ICF3InXPSEachSideConcrete8In
ICF4InEPSEachSideConcrete6In
ICF4InEPSEachSideConcrete8In
ICF4InXPSEachSideConcrete6In
ICF4InXPSEachSideConcrete8In
ICF4_5InPolyurethaneEachSideConcrete6In
ICF4_5InPolyurethaneEachSideConcrete8In
InfiltrationMethod | InfMthd | enumerated list | none | AirChangesPerHour | Yes | 0 | 4 |  |  |  | Defaulted |  |  | Method used for modeling uncontrolled air leakage or infiltration. | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
FlowArea
FlowExteriorArea
FlowExteriorWallArea
FlowSpace
InfiltrationModelCoefficientA | InfModelCoefA | decimal | none |  | Yes | 0 | 4 |  |  |  | Required |  |  | infiltration overall coefficient | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InfiltrationModelCoefficientB | InfModelCoefB | decimal | F |  | Yes | 0 | 4 |  |  |  | Required |  |  | infiltration temperature coefficient | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InfiltrationModelCoefficientC | InfModelCoefC | decimal | h per mi |  | Yes | 0 | 4 |  |  |  | Required |  |  | infiltration windspeed coefficient | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InfiltrationModelCoefficientD | InfModelCoefD | decimal | h2 per mi2 |  | Yes | 0 | 4 |  |  |  | Required |  |  | infiltration windspeed squared coefficient | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InfiltrationScheduleReference | InfSchRef | reference | none |  | Yes | 0 | 4 |  |  |  | Defaulted | Sch |  | Reference to a schedule when needed by the selected infiltration method. | 2013 NR ACM 5.4 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InsulationBatt | InsulationBatt | enumerated list |  | GlassFiberBatt3_5In_ R11_CEC_Default | [8 empty] | dtyp:EnumerationConstantPermissive
GlassFiberBatt4In
GlassFiberBatt4_5In
GlassFiberBatt5In
GlassFiberBatt5_5In_ R19_CEC_Default
GlassFiberBatt6_5In
InsulationBoard | InsulationBoard | enumerated list |  | CellularPolyisocyanurate3_5In_R21 | [8 empty] | dtyp:EnumerationConstantPermissive
CellularPolyisocyanurate4In_R23
CellularPolyisocyanurate4_5In_R26
CellularPolyisocyanurate5In_R29
CellularPolyisocyanurate5_5In_R32
CellularPolyisocyanurate6In_R35
CellularPolyisocyanurate6_5In_R38
ComplianceInsulationR0_01
ComplianceInsulationR0_02
ComplianceInsulationR0_10
ComplianceInsulationR10_06
ComplianceInsulationR12_55
ComplianceInsulationR12_69
ComplianceInsulationR13_99
ComplianceInsulationR14_14
ComplianceInsulationR14_32
ComplianceInsulationR14_60
ComplianceInsulationR15_54
ComplianceInsulationR16_58
ComplianceInsulationR16_69
ComplianceInsulationR17_67
ComplianceInsulationR19_63
ComplianceInsulationR1_35
ComplianceInsulationR1_41
ComplianceInsulationR1_54
ComplianceInsulationR20_05
ComplianceInsulationR21_18
ComplianceInsulationR21_39
ComplianceInsulationR22_48
ComplianceInsulationR24_86
ComplianceInsulationR25_16
ComplianceInsulationR28_63
ComplianceInsulationR2_15
ComplianceInsulationR2_19
ComplianceInsulationR2_85
ComplianceInsulationR2_89
ComplianceInsulationR34_93
ComplianceInsulationR3_63
ComplianceInsulationR3_70
ComplianceInsulationR6_32
ComplianceInsulationR6_46
ComplianceInsulationR7_10
ComplianceInsulationR7_18
ComplianceInsulationR7_39
ComplianceInsulationR8_00
ComplianceInsulationR8_07
ComplianceInsulationR9_83
ComplianceInsulationR9_94
ExpandedPerliteOrganicBonded0_75In_R2_1
ExpandedPerliteOrganicBonded1In_R2_8
ExpandedPerliteOrganicBonded1_5In_R4_2
ExpandedPerliteOrganicBonded2In_R5_6
ExpandedPerliteOrganicBonded3In_R8_3
ExpandedPerliteOrganicBonded4In_R11
ExpandedPerliteOrganicBonded6In_R17
ExpandedPolystyrene0_5In_R2_1
ExpandedPolystyrene0_75In_R3_1
ExpandedPolystyrene1In_R4_2
ExpandedPolystyrene1_25In_R5_2
ExpandedPolystyrene1_5In_R6_3
ExpandedPolystyrene1_75In_R7_3
ExpandedPolystyrene1_875In_R8
ExpandedPolystyrene1_9375In_R8_1
ExpandedPolystyrene2In_R8_3
ExpandedPolystyrene2_4375In_R10
ExpandedPolystyrene2_4In_R10
ExpandedPolystyrene3In_ R13
ExpandedPolystyrene3_3333In_R14
ExpandedPolystyrene3_4In_R14
ExpandedPolystyrene3_5In_R15
ExpandedPolystyrene4_0625In_R17
ExpandedPolystyrene4_7In_R20
ExpandedPolystyrene5_4In_R22
ExpandedPolystyrene5_95In_R25
ExpandedPolystyrene6_1In_R25
ExpandedPolystyrene6_875In_R29
ExpandedPolystyrene8_6In_R35
ExpandedPolyurethane0_5In_R3_1
ExpandedPolyurethane0_75In_R4_7
ExpandedPolyurethane1In_R6_3
ExpandedPolyurethane1_25In_R7_8
ExpandedPolyurethane2In_R12_6
PerliteBoard0_75In_R1_9
PerliteBoard1In_R2_5
PerliteBoard1_5In_R3_8
PerliteBoard2In_R5_0
R24BattWall8In_R24
InsulationForm | InsForm | enumerated list | none | Batt | [9 empty] | One of several descriptors defining whether the insulation is rigid board, foam or batt. | In Joint Appendix 4 some tables for roofs and walls assign different U Factors for cavity insulation depending on two forms of insulation: batt or foamed plastic or cellulose. Rigid board is the form used for continuous insulation. Thermal blocks are used on some metal building roofs. 2013 NR ACM Qualities of Insulation are defined in Materials library Appendix . There are over 60 different entries for Insulation which include in the name a description of the form..
Block
Foam
RigidBoard
InsulationLooseFill | InsulationLooseFill | enumerated list | none | LooseFillMineralFiber2LbPerFt3Thickness13_75In
LooseFillMineralFiber2LbPerFt3Thickness4In
LooseFillMineralFiber2LbPerFt3Thickness6_5In
LooseFillMineralFiber2LbPerFt3Thickness7_5In
LooseFillMineralFiber2LbPerFt3Thickness8_25In
LooseFillMineralFiberClosedSidewallsThickness3_5In
InsulationOther | InsulationOther | enumerated list | none | RammedEarth
InsulationPlacement | InsPlcmt | enumerated list | none | CavityAttic | [9 empty] | An enumeration of possible placements of insulation in a construction assembly. | JA 4 tables specify RValues specific to the placement of the insulation in the construction assembly.
CavityFraming
CavityFurring
ContinuousAboveDeckNoSleepers
ContinuousAboveDeckSleepers
ContinuousAboveWaterproofMembrane
ContinuousBelowDeck
OverSuspendedCeiling
SlabFullyInsulated
SlabHorizontal
SlabVertical
InsulationRValue | InsRVal | decimal | h ft2 F per Btu | [7 empty] | Required |  |  | A measure of thermal resistance of an insulating material used in a pre-defined ConstructionAssembly or individual construction layer or used to insulate ducts or equipment like a water heater. It is usually expressed in whole number units of (hr x ft2 x degrees F)/Btu but can be a decimal value | JA 4 tables list InsulationRValue for different types of roof, wall and floor constructions 2013 NR ACM R-Value is defined in the construction assemblies for different envelope components (roof, wall, floor).
InsulationSprayApplied | InsulationOther | enumerated list | none | SprayCellulosicFiber4_6LbPerFt3Thickness3_5In
SprayCellulosicFiber4_6LbPerFt3Thickness4In
SprayCellulosicFiber4_6LbPerFt3Thickness4_5In
SprayCellulosicFiber4_6LbPerFt3Thickness5In
SprayCellulosicFiber4_6LbPerFt3Thickness5_5In
SprayCellulosicFiber4_6LbPerFt3Thickness6In
SprayCellulosicFiber4_6LbPerFt3Thickness6_5In
SprayGlassFiber3_9LbPerFt3Thickness3_5In
SprayGlassFiber3_9LbPerFt3Thickness4In
SprayGlassFiber3_9LbPerFt3Thickness4_5In
SprayGlassFiber3_9LbPerFt3Thickness5In
SprayGlassFiber3_9LbPerFt3Thickness5_5In
SprayGlassFiber3_9LbPerFt3Thickness6In
SprayGlassFiber3_9LbPerFt3Thickness6_5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness3_5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness4In
SprayPolyurethaneFoam0_5LbPerFt3Thickness4_5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness5_5In
SprayPolyurethaneFoam0_5LbPerFt3Thickness6In
SprayPolyurethaneFoam0_5LbPerFt3Thickness6_5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness3_5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness4In
SprayPolyurethaneFoam3_0LbPerFt3Thickness4_5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness5_5In
SprayPolyurethaneFoam3_0LbPerFt3Thickness6In
SprayPolyurethaneFoam3_0LbPerFt3Thickness6_5In
InsulationType | InsType | enumerated list | none | Cellulose | [6 empty] | Required |  |  | One of several defined types used in the Joint Appendix 4 construction assembly tables. | Joint Appendix 4: A number of tables assign UFactor that depend on the type of insulating material in the construction.
Fiberglass
MineralWool
PlasticPolystyrene
UreaFormaldehyde
InteriorLightingNonRegulatedHeatGainRadiantFraction | IntLtgNonRegHtGnRadFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of non-regulated interior lighting radiant heat gain going to space surfaces | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InteriorLightingNonRegulatedHeatGainSpaceFraction | IntLtgNonRegHtGnSpcFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of non-regulated interior lighting heat gain going to space air | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InteriorLightingNonRegulatedScheduleReference | IntLtgNonRegSchRef | reference | none | [7 empty] | Defaulted | Sch |  | Reference to a unique identification name for a Schedule of interior lighting type |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InteriorLightingRegulatedHeatGainRadiantFraction | IntLtgRegHtGnRadFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of regulated interior lighting radiant heat gain going to space surfaces | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InteriorLightingRegulatedHeatGainSpaceFraction | IntLtgRegHtGnSpcFrac | decimal | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative | Fraction of regulated interior lighting heat gain going to space air | 2013 Draft ACM Sec.5.4.3 Table 18 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InteriorLightingRegulatedScheduleReference | IntLtgRegSchRef | reference | none | [7 empty] | Defaulted | Sch |  | Reference to a unique identification name for a Schedule of interior lighting type | 2013 Draft ACM Sec.5.4.3 | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
InteriorLightingSpecificationMethod | IntLtgSpecMthd | enumerated list | none | AreaCategoryMethod | [6 empty] | Defaulted |  |  | Selection of interior lighting specification method.
TailoredMethod
InteriorLightingSystemPower | Power | decimal | W | [7 empty] | Optional
IsAcceptanceTestRequiredReport | IsAcceptanceTestReqdRpt | boolean | none | [7 empty] | Defaulted
IsAtriumGreaterThan55Feet | IsAtriumGT55Ft | boolean | none | [7 empty] | Defaulted
IsPlenumReturn | IsPlenumRet | boolean | none | [7 empty] | Optional
KitchenExhaustHoodDuty | KitExhHoodDuty | enumerated list | none | ExtraHeavy | Yes | 0 | 5 |  |  |  | CondRequired
Heavy
Light
Medium
None
KitchenExhaustHoodFlow | KitExhHoodFlow | decimal | ft3 per min |  | Yes | 0 | 5 |  |  |  | Defaulted |  | dtyp:DecimalNonnegative
KitchenExhaustHoodLength | KitchenExhHoodLen | decimal | ft |  | Yes | 0 | 5 |  |  |  | CondRequired |  | dtyp:DecimalNonnegative
KitchenExhaustHoodStyle | KitchenExhHoodStyle | enumerated list | none | BackshelfOrPassover | Yes | 0 | 5 |  |  |  | Optional
DoubleIsland
Eyebrow
None
SingleIsland
WallMountedCanopy
LaboratoryExhaustRateType | LabExhRtType | enumerated list | none | HoodDominated | [6 empty] | Defaulted |  |  | The type of load that dictates lab exhaust rate requirements | 2013 NR ACM 5.6.5.3
LoadDominated
LampType | LampType | enumerated list | none | CFL | [6 empty] | Optional |  |  | Enumeration type for determining luminaire heat gain distribution
HighPressureSodium
Incandescent
LED
LinearFluorescent
MercuryVapor
MetalHalide
Latitude | Lat | decimal | deg arc |  |  |  |  | -90 | 90 |  | Required |  | dtyp:Latitude | The angular distance of a place north or south of the earth's equator, usually expressed in degrees and minutes. | Joint Appendix 2 defines climate data and includes latitude, longitude and elevation for the selected representative city in each of the 16 climate zones.
LeftFinAngle | LeftFinAngle | decimal | deg arc | [7 empty] | Optional
LeftFinDepth | LeftFinDepth | decimal | ft | [7 empty] | Optional
LeftFinDistance | LeftFinDistance | decimal | ft | [7 empty] | Optional
LeftFinDistanceAbove | LeftFinDistanceAbove | decimal | ft | [7 empty] | Optional
LeftFinDistanceBelow | LeftFinDistanceBelow | decimal | ft | [7 empty] | Optional
LeftFinTransmittance | LeftFinTrans | decimal | none | [7 empty] | Optional
LeftFinTransmittanceOption | LeftFinTransOption | enumerated list | none | Constant | [6 empty] | Optional
Scheduled
LeftFinTransmittanceScheduleReference | LeftFinTransSchRef | reference | none | [7 empty] | Optional | Sch
LightingControlCountReport | LtgCtrlCntRpt | boolean | none | [7 empty] | Defaulted
LightingStatus | LtgStatus | enumerated list | none | Altered | [6 empty] | Defaulted |  |  |  | 2013 NR ACM
Existing
Future
New
LightOutputFraction | LightOutputFrac | decimal | none | [7 empty] | Optional |  |  | For a stepped dimming control point, the fraction of rated light output paired with a fraction of rated power input. | 2013 Draft NR ACM
LivingUnitCount | LivingUnitCnt | integer | none | [10 empty] | The total number of Residential or Hotel/Motel living units in the building. | 2013 NR ACM 5.9.1
LivingUnitCountAltered | LivingUnitCntAltered | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of altered high-rise residential or hotel/motel living units in an alterations/additions building | 2013 2016 NR ACM
LivingUnitCountExisting | LivingUnitCntExisting | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of existing high-rise residential or hotel/motel living units in an alterations/additions building | 2013 2016 NR ACM
LivingUnitCountNew | LivingUnitCntNew | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of new high-rise residential or hotel/motel living units in an alterations/additions building | 2013 2016 NR ACM
Longitude | Long | decimal | deg arc |  |  |  |  | -180 | 180 |  | Required |  | dtyp:Longitude | The angular distance of a place east or west of the meridian at Greenwich, England. | Joint Appendix 2 defines climate data and includes latitude, longitude and elevation for the selected representative city in each of the 16 climate zones.
LuminaireCount | LumCnt | integer | none |  | Yes | 0 | 5 |  |  | decimal | Defaulted |  | dtyp:IntegerNonnegative | Array of the count of upto 5 different types of luminaires
LuminaireDescriptionReport | LumDescRpt | string | none | [7 empty] | Optional
LuminaireMountingHeight | LumMntgHgt | decimal | ft | [7 empty] | Defaulted |  |  | Distance from the finished floor to the bottom of the luminaire | 2013 Title 24 part 6 140.6(c)3 Table 140.6-E, NRCCLTI01E
LuminaireReference | LumRef | reference | none |  | Yes | 0 | 5 |  |  |  | Optional | Lum |  | Reference to a luminaire object
LuminaireStatus | LumStatus | enumerated list | none | Altered | Yes | 0 | 5 |  |  |  | Defaulted |  |  | Defines if a construction or equipment is new, existing, modified, removed. Standards such as efficiency standards may not apply if a construction or equipment in a project is existing. equipment may be moved and reinstalled in the project.
Existing
Future
New
MasonryGrout | MsnryGrout | enumerated list | none | PartialGrout | [9 empty] | Describes how the grout is applied in hollow masonry walls. Values include solid (every cell is grouted), partial (some cells are grouted) and partial insulated (cells not grouted are filled with insulation). | Masonry Grout value effects thermal factors assigned to hollow unit masonry walls in Joint Appendix 4
PartialInsulatedGrout
SolidGrout
MasonryMaterials | MasonryMaterials | enumerated list |  | Brick48LbPerFt3Thickness3_625In
BrickFiredClay140LbPerFt3Thickness3_625In
ClayTileHollow1CellDeepThickness3In
ClayTileHollow1CellDeepThickness4In
ClayTileHollow2CellDeepThickness10In
ClayTileHollow2CellDeepThickness6In
ClayTileHollow2CellDeepThickness8In
ClayTileHollow3CellDeepThickness12In
ClayTilePaver
Concrete_Paver
GypsumPartitionBlock3Cell4x12x30Thickness4In
GypsumPartitionBlock4Cell3x12x30Thickness3In
Stone1In
Stucco3Coat
StuccoSyntheticEIFS_Finish1In
Terrazzo1In
MasonryType | MsnryType | enumerated list | none | ClayBrick | [9 empty] | Will be an attribute of some types of Construction Assembly for walls. The values cover solid and hollow units. | In Joint Appendix 4 some tables include Masonry Type defined as Hollow Masonry Units: lightweight concrete masonry units (CMU), medium weight CMU, normal weight CMU, and hollow clay masonry units. (defined by ASTM C-90) NR ACM Table N2-1 includes masonry type Solid Unit Masonry: light weight CMU, medium weight CMU, normal weight CMU, clay brick and concrete
ClayHollowUnit
Concrete
ConcreteMasonryUnitLightWeight
ConcreteMasonryUnitMediumWeight
ConcreteMasonryUnitNormalWeight
ICFWall
InsulatingConcreteForms
MasonryUnitsFill | MasonryUnitsFill | enumerated list |  | ClayPartGroutedInsulated130LbPerFt3Thickness6In
ClayPartGroutedInsulated130LbPerFt3Thickness8In
ConcretePartGroutedInsulated105LbPerFt3Thickness10In
ConcretePartGroutedInsulated105LbPerFt3Thickness12In
ConcretePartGroutedInsulated105LbPerFt3Thickness6In
ConcretePartGroutedInsulated105LbPerFt3Thickness8In
ConcretePartGroutedInsulated115LbPerFt3Thickness10In
ConcretePartGroutedInsulated115LbPerFt3Thickness12In
ConcretePartGroutedInsulated115LbPerFt3Thickness6In
ConcretePartGroutedInsulated115LbPerFt3Thickness8In
ConcretePartGroutedInsulated125LbPerFt3Thickness10In
ConcretePartGroutedInsulated125LbPerFt3Thickness12In
ConcretePartGroutedInsulated125LbPerFt3Thickness6In
ConcretePartGroutedInsulated125LbPerFt3Thickness8In
MasonryUnitsHollow | MasonryUnitsHollow | enumerated list |  | ClayPartGrouted130LbPerFt3Thickness6In
ClayPartGrouted130LbPerFt3Thickness8In
ConcretePartGrouted105LbPerFt3Thickness10In
ConcretePartGrouted105LbPerFt3Thickness12In
ConcretePartGrouted105LbPerFt3Thickness6In
ConcretePartGrouted105LbPerFt3Thickness8In
ConcretePartGrouted115LbPerFt3Thickness10In
ConcretePartGrouted115LbPerFt3Thickness12In
ConcretePartGrouted115LbPerFt3Thickness6In
ConcretePartGrouted115LbPerFt3Thickness8In
ConcretePartGrouted125LbPerFt3Thickness10In
ConcretePartGrouted125LbPerFt3Thickness12In
ConcretePartGrouted125LbPerFt3Thickness6In
ConcretePartGrouted125LbPerFt3Thickness8In
MasonryUnitsSolid | MasonryUnitsSolid | enumerated list |  | ClaySolidGrout130LbPerFt3Thickness6In
ClaySolidGrout130LbPerFt3Thickness8In
ConcreteSolidGrout105LbPerFt3Thickness10In
ConcreteSolidGrout105LbPerFt3Thickness12In
ConcreteSolidGrout105LbPerFt3Thickness6In
ConcreteSolidGrout105LbPerFt3Thickness8In
ConcreteSolidGrout115LbPerFt3Thickness10In
ConcreteSolidGrout115LbPerFt3Thickness12In
ConcreteSolidGrout115LbPerFt3Thickness6In
ConcreteSolidGrout115LbPerFt3Thickness8In
ConcreteSolidGrout125LbPerFt3Thickness10In
ConcreteSolidGrout125LbPerFt3Thickness12In
ConcreteSolidGrout125LbPerFt3Thickness6In
ConcreteSolidGrout125LbPerFt3Thickness8In
MaterialReference | MatRef | reference | none |  | Yes | 0 | 10 |  |  |  | CondRequired | Mat
MaximumGlareIndex | MaxGlrIdx | decimal | none | [7 empty] | Optional |  |  | Maximum glare index for daylighting control
MetalBuildingRoof | MetalBuildingRoof | enumerated list
MetalBuildingWall | MetalBuildingWall | enumerated list
MetalInsulatedPanelWall | MetalInsulatedPanelWall | enumerated list |  | MetalInsulatedPanel2In
MetalInsulatedPanel2_5In
MetalInsulatedPanel3In
MetalInsulatedPanel4In
MetalInsulatedPanel5In
MetalInsulatedPanel6In
MinimumDimmingLightFraction | MinDimLtgFrac | decimal | none | [7 empty] | Defaulted |  |  | Minimum light output of controlled lighting when fully dimmed. Minimum light fraction = (Minimum light output) / (Rated light output). | 2013 NR ACM
MinimumDimmingPowerFraction | MinDimPwrFrac | decimal | none | [7 empty] | Defaulted |  |  | The minimum power fraction when controlled lighting is fully dimmed. Minimum power fraction = (Minimum power) / (Full rated power). | 2013 NR ACM
Month | Month | integer | none |  |  |  |  | 1 | 12 |  | Required |  |  | Interger value represents the month of the year and therefore is in the range of 1-12
Month | Month | enumerated list | none | April | [6 empty] | Required
August
December
February
January
July
June
March
May
November
October
September
MonthDay | Day | integer | none |  |  |  |  | 1 | 31 |  | Required |  |  | Integer value represents the day of the month and therefore is in the range of 1-31, with limits on the high end depending on the value for the Month property
MonthlyAverageTemperatureMaximumDifference | MoAvgTempMaxDiff | decimal | F | [7 empty] | Optional |  |  | This is required for EnergyPlus Site:WaterMainsTemperature object
Multiplier | Mult | integer | none |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:IntegerNonnegative | The number of duplicate building stories to be simulated in the model. This value must be consistent with the multipliers for thermal zones and the number of HVAC systems that serve zones on floors with multipliers | 2013 NR ACM sections 2.3.1 and 5.3
Name | Name | string | none | [7 empty] | Required |  |  | A string that uniquely defines an object in the data model. It can be assigned in other objects as a Reference to the object, similar to a foreign key in relational database tables.
NaturalGasAvailable | NatGasAvail | boolean | none | [11 empty] | CF1R-PRF
NonRegulatedExclusion | NonRegExclusion | enumerated list | none | ATMLighting | [6 empty] | CondRequired |  |  | Category allowing exclusion of interior lighting system power from regulated amount. | 2013 NR ACM Draft Sec.140.6(a)3 | Required when IntLtgSys:PwrReg = 0, else NotInput
CBCRequiredExitSign
CBCRequiredExitwayOrEgressNormallyOff
DanceFloorOrTheatrical
ElevatorLighting
ExamSurgicalNightOrEquipmentIntegratedInMedicalOrClinical
FilmOrPhotoStudioLightingSeparatelySwitched
HighRiseResidentialDwellingUnit
HistoricBuilding
HotelMotelGuestRoom
LightingDemonstrationEquipInLightingEducationFacilities
LightingEquipmentForSale
ManufacturerInstalledInFreezerVendingFoodPrepScientificOrIndEquip
PlantGrowthOrMaintWithMultiLevelAstroTimer
SignageLighting
SmallAgriculturalBuilding
SmallNonresidentialParkingGarage
SmallRefrigeratedCases
SmallUnconditionedAgriculturalBuilding
TemporaryExhibitSeparatelySwitchedInCivicTransConvOrHotel
TemporaryLightingSystems
ThemeParksThemeAndSpecialEffects
NonresidentialFloorArea | NonResFlrArea | decimal | ft2 |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
NonresidentialStoryCountElectricHeat | NonResStoryCntElecHt | integer | none | [7 empty] | Optional
NonresidentialStoryCountFossilHeat | NonResStoryCntFossilHt | integer | none | [7 empty] | Optional
NumberOfControlSteps | NumOfCtrlSteps | integer | none | [7 empty] | Defaulted |  |  | For step switching, this term defines even steps of light output and even steps of rated power fractions. | 2013 NR ACM
NumberOfIdenticalDwellingUnits | NumOfIdenticalDwellingUnits | decimal | none | [7 empty] | Optional
OccupantFraction | OccFrac | decimal | none |  |  |  |  | 0.5 | 5 |  | Defaulted |  |  | This is the percentage of BuildingTotalGrossFloorArea that is occupied and operational
OccupantLatentHeatRate | OccLatHtRt | decimal | Btu per h person | [7 empty] | Optional |  |  | The rate of latent heat released per person which is a function of activity | 2008 NR ACM Table Table N2-5 and N2-6 assign values for Latent Heat per person 2013 NR ACM Latent and sensible heat generated by occupants are one descriptor, "Occupant Heat Rate".
OccupantNumberFixedSeating | OccNumFxdSeat | decimal | person | [7 empty] | Defaulted
OccupantSensibleHeatRate | OccSensHtRt | decimal | Btu per h person | [7 empty] | Optional |  |  | The rate of sensible heat released per person which is a function of activity | 2008 NR ACM Table Table N2-5 and N2-6 assign values for Sensible Heat per person 2013 NR ACM Latent and sensible heat generated by occupants are one descriptor, "Occupant Heat Rate".
Open | Open | enumerated list | none | NonSwinging | [6 empty] | Optional |  |  | An enumeration with values of swinging and non-swinging. Non-swinging would include sliding doors and roll-up doors. | Title 24 Table 143-A/B and C assign U-Factor based on whether the door is swinging or non swinging. 2013 NR ACM Maps to Door Type with same two values of swinging and non-swinging.
Swinging
OperableWindowConfiguration | OperableWinConfiguration | enumerated list | none | CasementAwning | [6 empty] | CondRequired |  |  | Used in selection of Table NA-6 properties
Sliding
Operation | Oper | enumerated list | none | NonSwinging | [6 empty] | Optional |  |  | An enumeration with values of swinging and non-swinging. Non-swinging would include sliding doors and roll-up doors.
Swinging
OverhangAngle | OverhangAngle | decimal | deg arc | [7 empty] | Optional
OverhangDepth | OverhangDepth | decimal | ft | [7 empty] | Optional
OverhangDistance | OverhangDistance | decimal | ft | [7 empty] | Optional
OverhangLeftExtension | OverhangLeftExtension | decimal | ft | [7 empty] | Optional
OverhangRightExtension | OverhangRightExtension | decimal | ft | [7 empty] | Optional
OverhangTransmittance | OverhangTrans | decimal | none | [7 empty] | Optional
OverhangTransmittanceOption | OverhangTransOption | enumerated list | none | Constant | [6 empty] | Optional
Scheduled
OverhangTransmittanceScheduleReference | OverhangTransmittanceScheduleReference | reference | none | [7 empty] | Optional | Sch
PartitionRelativePosition | RelativePosition | enumerated list | none
Perimeter | Perim | decimal | ft | [7 empty] | Optional |  |  |  |  | Optional when Proj:GeometryInpType = 'Simplified', else NotInput
PerimeterExposed | PerimExposed | decimal | ft | [7 empty] | Defaulted |  |  | Describes the exposed (direct contact with ambient air) perimeter of a slab-on-grade or underground floor. | 2013 NACM 5.5.9, Slab Floor Geometry
PermitScope | PermitScope | enumerated list | none | PermitNonresidentialAll | [6 empty] | Required |  |  | Defines what compliance the project covers and depends on what plans will be submitted for a permit. | 2013 NR ACM 1.6.2 Scope of Compliance Calculations
PermitNonresidentialEnvelope
PermitNonresidentialEnvelopeLighting
PermitNonresidentialEnvelopeMechanical
PermitNonresidentialLighting
PermitNonresidentialLightingMechanical
PermitNonresidentialMechanical
PlantCoolingCapacity | PlantClgCap | decimal | Btu per h |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
PlantHeatingCapacity | PlantHtgCap | decimal | Btu per h |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
Plastering | Plastering | enumerated list |  | Aggregate45LbPerFt3Thickness0_5In
Aggregate45LbPerFt3Thickness0_625In
AggregateOnMetalLath45LbPerFt3Thickness0_75In
AggregatePerliteOnMetalLathThickness0_75In
AggregatePerliteThickness0_5In
AggregatePerliteThickness0_625In
ConcreteSandAggregateThickness6In
GypsumPlaster80LbPerFt3Thickness0_5In
GypsumPlaster80LbPerFt3Thickness0_625In
GypsumPlasterOnMetalLath70LbPerFt3Thickness0_75In
GypsumPlasterOnMetalLath80LbPerFt3Thickness0_75In
MortarCementThickness1In
MortarCementThickness1_75In
PerlitePlaster25LbPerFt3Thickness0_5In
PerlitePlaster38LbPerFt3Thickness0_5In
PlasterSandAggregateThickness1In
PulpboardOrPaperPlasterThickness0_5In
SandAggregateOnMetalLathThickness0_75In
SandAggregateThickness0_375In
SandAggregateThickness0_5In
SandAggregateThickness0_625In
SandAggregateThickness0_75In
Stucco0_375In
Stucco0_875In
StuccoSyntheticEIFS_Finish1In
VermiculiteAggregate45LbPerFt3Thickness0_5In
Power | Pwr | decimal | W |  |  |  |  | 0 |  |  | Compulsory |  | dtyp:DecimalNonnegative |  | NRCCLTI01E
PowerNA8Default | PwrNA8Default | boolean | none | [7 empty] | Defaulted
PowerRegulated | PwrReg | boolean | none | [7 empty] | Defaulted |  |  | Boolean flag regarding Regulated vs. Non-Regulated power for an interior lighting system. Defaults to TRUE=Regulated.
PrimarySideDaylightingControlledLightingPower | PriSideDayltgCtrlLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
PrimarySideDaylightingIlluminanceSetPoint | PriSideDayltgIllumSetpt | decimal | lux |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:DecimalNonnegative
PrimarySideDaylightingInstalledLightingPower | PriSideDayltgInstalledLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
PrimarySidelit100PercentControlled | PriSide100PctControlled | boolean | none | [7 empty] | Optional
PrimarySidelitDaylitArea | PriSidelitDaylitArea | decimal | ft2 | [10 empty] | The primary daylighted area is the portion that is closest to the daylighting source and receives the most illumination. | 2013 NR ACM 5.4.5
ProcessElectricalLatentFraction | ProcElecLatFrac | decimal | none | [7 empty] | Optional
ProcessElectricalLostFraction | ProcElecLostFrac | decimal | none | [7 empty] | Optional
ProcessElectricalRadiationFraction | ProcElecRadFrac | decimal | none | [7 empty] | Optional
ProcessElectricalScheduleReference | ProcElecSchRef | reference | none | [7 empty] | Optional | Sch |  | Reference to a unique identification name for a schedule in a library of process electrical type
ProcessGasLatentFraction | ProcGasLatFrac | decimal | none | [7 empty] | Optional
ProcessGasLostFraction | ProcGasLostFrac | decimal | none | [7 empty] | Optional
ProcessGasPowerDensity | ProcGasPwrDens | decimal | Btu per h ft2 | [7 empty] | Optional |  | dtyp:DecimalNonnegative | Commercial gas power density is the average power density for all commercial gas equipment, assuming constant year-round operation. | 2013 Draft NR ACM
ProcessGasRadiationFraction | ProcGasRadFrac | decimal | none | [7 empty] | Optional |  |  | The fraction of heat gain to Space to appliance energy use | 2013 Draft NR ACM
ProcessGasScheduleReference | ProcGasSchRef | reference | none | [7 empty] | Optional | Sch |  | Reference to a unique identification name for a schedule in a library of process gas type
ProjectCounty |  | enumerated list | none | Alameda | [9 empty] | CaliforniaCounty is one of the counties in the state of California and is the base property for geograpic data as well as for specific applications such as the climate zone county.
Alpine
Amador
Butte
Calaveras
Colusa
ContraCosta
DelNorte
ElDorado
Fresno
Glenn
Humboldt
Imperial
Inyo
Kern
Kings
Lake
Lassen
LosAngeles
Madera
Marin
Mariposa
Mendocino
Merced
Modoc
Mono
Monterey
Napa
Nevada
Orange
Placer
Plumas
Riverside
Sacramento
SanBenito
SanBernardino
SanDiego
SanFrancisco
SanJoaquin
SanLuisObispo
SanMateo
SantaBarbara
SantaClara
SantaCruz
Shasta
Sierra
Siskiyou
Solano
Sonoma
Stanislaus
Sutter
Tehama
Trinity
Tulare
Tuolumne
Ventura
Yolo
Yuba
ReceptacleLatentFraction | RecptLatFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
ReceptacleLostFraction | RecptLostFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
ReceptacleRadiationFraction | RecptRadFrac | decimal | none | [7 empty] | Defaulted |  |  |  |  | Compliance Use value assigned is for the Space object. When this property is assigned to SpaceFunctionDefaults object, its Compliance Use value is Optional
RelocatablePublicSchoolBuilding | RelocPubSchoolBldg | boolean | none | [7 empty] | Optional
ResidentialDHWSystemReference | ResDHWSysRef | reference | none | [7 empty] | Optional
ResidentialFloorArea | ResFlrArea | decimal | ft2 |  |  |  |  | 0 |  |  | Defaulted |  | dtyp:DecimalNonnegative
ResidentialHotWaterHeatingRate | ResHotWtrHtgRt | decimal | gal per h person | [7 empty] | Optional
ResidentialStoryCountElectricHeat | ResStoryCntElecHt | integer | none | [7 empty] | Optional
ResidentialStoryCountFossilHeat | ResStoryCntFossilHt | integer | none | [7 empty] | Optional
ReturnPlenumSpaceReference | RetPlenumSpcRef | reference | none | [7 empty] | Optional | Spc
RightFinAngle | RightFinAngle | decimal | deg arc | [7 empty] | Optional
RightFinDepth | RightFinDepth | decimal | ft | [7 empty] | Optional
RightFinDistance | RightFinDistance | decimal | ft | [7 empty] | Optional
RightFinDistanceAbove | RightFinDistanceAbove | decimal | ft | [7 empty] | Optional
RightFinDistanceBelow | RightFinDistanceBelow | decimal | ft | [7 empty] | Optional
RightFinTransmittance | RightFinTrans | decimal | none | [7 empty] | Optional
RightFinTransmittanceOption | RightFinTransOption | enumerated list | none | Constant | [6 empty] | Optional
Scheduled
RightFinTransmittanceScheduleReference | RightFinTransSchRef | reference | none | [7 empty] | Optional | Sch
RoofDensity | RoofDens | boolean | none | [7 empty] | Defaulted
Roofing | Roofing | enumerated list |  | AsbestosOrCementShingles0_375In
AsphaltBitumenInertFill100LbPerFt3Thickness0_75In
AsphaltBitumenInertFill144LbPerFt3Thickness0_75In
AsphaltRollRoofing0_25In
AsphaltShingles0_25In
BuiltUpRoofing0_375In
ClayTile0_5In
LightRoof0_4In
MasticAsphaltHeavy20PercentGrit1In
MetalStandingSeam0_0625In
Roof10LbPerFt2Thickness1In
Roof15LbPerFt2Thickness1_5In
Roof25LbPerFt2Thickness2_5In
Roof5LbPerFt2Thickness0_5In
RoofGravel0_5In
RoofGravel1In
Slate0_5In
TileGap0_75In
WoodShingles0_75In
WoodShinglesPlainAndPlasticFilmFaced0_75In
RValue | RVal | decimal | h ft2 F per Btu | [7 empty] | NotInput |  |  | A measure of thermal resistance of a type of Material found in construction layers or Insulation in a pre-defined ConstructionAssembly. It is usually expressed in whole number units of (hr x ft2 x degrees F)/Btu but can be a decimal value e.g. JA IV 4.1.5 Wood Based Sheathing R-values | T24 Definition: THERMAL RESISTANCE (R) is the resistance of a material or building component to the passage of heat in (hr x ft² x ºF)/Btu. Usuage: T24 Table 126-A Refrigerated Warehouse Insulation; Table 149-A Insulation Requirements For Roof Alterations Joint Appendix 4 Tables evaluate insulation RValues in order to assign UFactor
ScheduleDayAllDaysReference | SchDayAllRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayCoolingDesignDayReference | SchDayClgDDRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayFridayReference | SchDayFriRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayHeatingDesignDayReference | SchDayHtgDDRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayHolidayReference | SchDayHolRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayMondayReference | SchDayMonRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDaySaturdayReference | SchDaySatRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDaySundayReference | SchDaySunRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayThursdayReference | SchDayThuRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayTuesdayReference | SchDayTueRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayWednesdayReference | SchDayWedRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayWeekdaysReference | SchDayWDRef | reference | none | [7 empty] | Optional | SchDay
ScheduleDayWeekendsReference | SchDayWERef | reference | none | [7 empty] | Optional | SchDay
ScheduleWeekReference | SchWeekRef | reference | none |  | Yes | 53 | 53 |  |  |  | Compulsory | SchWeek
SecondarySideDaylightingControlledLightingPower | SecSideDayltgCtrlLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
SecondarySideDaylightingControls | SecSideDayltgCtrls | boolean | none | [7 empty] | Optional
SecondarySideDaylightingIlluminanceSetPoint | SecSideDayltgIllumSetpt | decimal | lux |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:DecimalNonnegative
SecondarySideDaylightingInstalledLightingPower | SecSideDayltgInstalledLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
SecondarySidelit100PercentControlled | SecSide100PctControlled | boolean | none | [7 empty] | Optional
SecondarySidelitDaylitArea | SecondarySidelitDaylitArea | decimal | ft2 | [10 empty] | The secondary daylighted area is an area farther from the daylighting source, but still receives useful daylight. | 2013 NR ACM 5.4.5
ShadingCredit | ShdgCred | boolean | none | [7 empty] | Required
SHGC | SHGC | decimal | none | [7 empty] | CondRequired |  |  | The ratio of the solar heat gain entering a space, through the subject fenestration product, to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation which is then re-radiated, conducted or convected into the space. often referred to as SHGC. | SOLAR HEAT GAIN COEFFICIENT (SHGC) is the ratio of the solar heat gain entering the space through the fenestration area to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation, which is then re-radiated, conducted, or convected into the space. 2013 NR ACM Fenestration Construction includes Solar Heat Gain Coefficient as an attribute.
SHGCCenterOfGlass | SHGCCOG | decimal | none | [7 empty] | CondRequired |  |  | The ratio of the solar heat gain entering a space, through the subject fenestration product, to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation which is then re-radiated, conducted or convected into the space. often referred to as SHGC.
SHWFluidSegmentReference | SHWFluidSegRef | reference | none | [7 empty] | Optional
SIPSFloor | SIPS Floor | enumerated list |  | SIPSCrawlSpaceR22Double2xSpline6_5In
SIPSCrawlSpaceR22IJoistSpline6_5In
SIPSCrawlSpaceR22Single2xSpline6_5In
SIPSCrawlSpaceR28Double2xSpline8_25In
SIPSCrawlSpaceR28IJoistSpline8_25In
SIPSCrawlSpaceR28Single2xSpline8_25In
SIPSCrawlSpaceR33Double2xSpline6_5In
SIPSCrawlSpaceR33IJoistSpline6_5In
SIPSCrawlSpaceR33Single2xSpline6_5In
SIPSCrawlSpaceR36IJoistSpline10_25In
SIPSCrawlSpaceR36Single2xSpline10_25In
SIPSNoCrawlSpaceR22Double2xSpline6_5In
SIPSNoCrawlSpaceR22IJoistSpline6_5In
SIPSNoCrawlSpaceR22Single2xSpline6_5In
SIPSNoCrawlSpaceR28Double2xSpline8_25In
SIPSNoCrawlSpaceR28IJoistSpline8_25In
SIPSNoCrawlSpaceR28Single2xSpline8_25In
SIPSNoCrawlSpaceR33Double2xSpline6_5In
SIPSNoCrawlSpaceR33IJoistSpline6_5In
SIPSNoCrawlSpaceR33Single2xSpline6_5In
SIPSNoCrawlSpaceR36IJoistSpline10_25In
SIPSNoCrawlSpaceR36Single2xSpline10_25In
SIPS_CrawlSpaceR36Double2xSpline10_25In
SIPS_NoCrawlSpaceR36Double2xSpline10_25In
SIPSRoof | SIPSRoof | enumerated list |  | SIPSR14MetalSpline48In
SIPSR22Double2xSpline6_5In
SIPSR22IJoistSpline6_5In
SIPSR22MetalSpline48In
SIPSR22OSBSpline6_5In
SIPSR22Single2xSpline6_5In
SIPSR28Double2xSpline8_5In
SIPSR28IJoistSpline8_5In
SIPSR28MetalSpline48In
SIPSR28OSBSpline8_5In
SIPSR28Single2xSpline8_5In
SIPSR33Double2xSpline6_5In
SIPSR33IJoistSpline6_5In
SIPSR33OSBSpline6_5In
SIPSR33Single2xSpline6_5In
SIPSR36Double2xSpline10_25In
SIPSR36IJoistSpline10_25In
SIPSR36MetalSpline48In
SIPSR36OSBSpline10_25In
SIPSR36Single2xSpline10_25In
SIPSR44Double2xSpline12_25In
SIPSR44IJoistSpline12_25In
SIPSR44OSBSpline12_25In
SIPSR44Single2xSpline12_25In
SIPSR55Double2xSpline10_25In
SIPSR55IJoistSpline10_25In
SIPSR55OSBSpline10_25In
SIPSR55Single2xSpline10_25In
SIPSWall | SIPSWall | enumerated list |  | SIPSR14Double2xSpline4_5In
SIPSR14IJoistSpline4_5In
SIPSR14OSBSpline4_5In
SIPSR14Single2xSpline4_5In
SIPSR18Double2xSpline4_5In
SIPSR18IJoistSpline4_5In
SIPSR18OSBSpline4_5In
SIPSR18Single2xSpline4_5In
SIPSR22Double2xSpline6_5In
SIPSR28Double2xSpline8_25In
SIPSR28IJoistSpline8_25In
SIPSR28OSBSpline8_25In
SIPSR28Single2xSpline8_25In
SIPSR33Double2xSpline6_5In
SIPS_R22IJoistSpline6_5In
SIPS_R22OSBSpline6_5In
SIPS_R22Single2xSpline6_5In
SIPS_R33IJoistSpline6_5In
SIPS_R33OSBSpline6_5In
SIPS_R33Single2xSpline6_5In
SIPS_R36Double2xSpline10_25In
SIPS_R36IJoistSpline10_25In
SIPS_R36OSBSpline10_25In
SIPS_R36Single2xSpline10_25In
SIPS_R44Double2xSpline12_25In
SIPS_R44IJoistSpline12_25In
SIPS_R44OSBSpline12_25In
SIPS_R44Single2xSpline12_25In
SIPS_R55Double2xSpline10_25In
SIPS_R55IJoistSpline10_25In
SIPS_R55OSBSpline10_25In
SIPS_R55Single2xSpline10_25In
SIPType | SIPSpcrType | enumerated list | none | [10 empty] | Defines the type of spacer in structurally insulated panels used in roof and wall construction. | In Joint Appendix 4 some tables include structurally insulated wall panels (SIPS) and defines whether the spacer is wood or oriented strand board. Values include OSB splines, wood spacers, (new types to be added) This is used in assigning thermal factors in the Joint Appendix 4 for performance compliance 2008 JA4 SIPS panel tables for Wall, Table 4.3.2 and Roof Table 4.2.3 evaluates these characteristics of the SIPS construction.
SkyClearness | SkyClear | decimal | none | [7 empty] | Required |  |  | This is a decmial value denoting the clearness used in the design day simulation
SkylightCurb | SkyltCurb | enumerated list | none | CurbMounted | [6 empty] | CondRequired |  |  | Curb or No Curb. For selection of NA-6 properties | Tables 143 A/B assign U Factor dependent on whether the skylight is mounted on a curb or directly on the roof. 2013 NR ACM Fenestration Type (Skylights) includes whether the skylight has a curb or not. 2013 Title 24 Part 6 Table NA6-5
DeckMounted
SkylightGlazing | SkyltGlz | enumerated list | none | Glass | [6 empty] | CondRequired |  |  | Used in selection of baseline properties
Plastic
SkylightRequirementException | SkyltReqExcpt | enumerated list | none | Auditorium | [6 empty] | CondRequired |  |  |  |  | Required when Spc:SkyltReqExcptFrac > 0, else NotInput
Church
ExistingWalls
FutureCeilings
FutureWalls
MovieTheater
Museum
RefrigeratedWarehouse
SkylightRequirementExceptionArea | SkyltReqExcptArea | decimal | ft2 |  |  |  |  | 0 | 1000000 |  | CondRequired
SkylightRequirementExceptionFraction | SkyltReqExcptFrac | decimal | none | [7 empty] | Defaulted
Skylit100PercentControlled | Skylit100PctControlled | binary | none | [7 empty] | Optional
SkylitDaylightingControlledLightingPower | SkylitDayltgCtrlLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
SkylitDaylightingIlluminanceSetPoint | SkylitDayltgIllumSetpt | decimal | lux |  |  |  |  | 0 | 10000 |  | Defaulted |  | dtyp:DecimalNonnegative
SkylitDaylightingInstalledLightingPower | SkylitDayltgInstalledLtgPwr | decimal | W |  |  |  |  | 0 | 1000000 |  | Defaulted |  | dtyp:DecimalNonnegative
SlabInsulationOrientation | SlabInsOrientation | enumerated list | none | 12inHorizontal | [6 empty] | Optional |  |  | The location and extent of slab-on-grade floor insulation | 2013 NACM-5.5.9
12inVertical
24inHorizontal
24inVertical
36inHorizontal
36inVertical
48inHorizontal
48inVertical
FullyInsulatedSlab
None
SlabInsulationThermalResistance | SlabInsThrmlR | enumerated list | none | R0 | [6 empty] | Optional |  |  | The rated R-value of slab-on-grade floor insulation. | 2013 NACM-5.5.9
R10
R15
R20
R25
R30
R35
R40
R45
R5
R50
R55
R7_5
SlabType | SlabType | enumerated list | none | [7 empty] | Optional |  |  | The classifications for floors in contact with the ground. | 2013 NACM-5.5.9
SolarReflectance | SolRefl | decimal | none | [7 empty] | Optional |  |  | From E+ Input/Output Ref:The diffuse solar reflectance of the unglazed part of the shading surface (default = 0.2). This reflectance is assumed to be the same for beam-to-diffuse and diffuse-to-diffuse reflection. Beam-to-diffuse reflection is assumed to be independent of angle of incidence of beam radiation. Diffuse-to-diffuse reflection is assumed to be independent of angular distribution of the incident of diffuse radiation. The outgoing diffuse radiation is assumed to be isotropic (hemispherically uniform). The sum of this reflectance and the shading surface transmittance should be less than or equal to 1.0. | 2013 NR ACM 5.5.7
SpaceFunction | SpcFunc | enumerated list | none | AuditoriumArea | [6 empty] | Compulsory |  |  | One of a list of occupancies assigned to the OccupancyArea | Title 24 Part 6 has definitions for occupancy types listed in the definitions in Section 101 under Nonresidential Function Area Or Type Of Use. Many of these types are used in lighting tables to assign values to rule targets such as lighting power adjustment factor. 2008 NR ACM has Tables N2-5 and N2-6 that use occupancy types for loads and schedules. 2013 NR ACM Appendix A has space-by-space occupancy types.
AutoRepairArea
BarCocktailLoungeCasinoArea
BeautySalonArea
CivicMeetingPlaceArea
ClassroomLectureTrainingVocationalArea
CommercialIndustrialStorageArea
CommercialIndustrialStorageAreaRefrigerated
ComputerRoom
ConventionConferenceMultipurposeMeetingCenterArea
CorridorRestroomStairsSupportArea
DiningArea
DryCleanCoinOperated
DryCleaningFullServiceCommercial
ElectricalMechancialTelephoneRoom
ExerciseRoom
ExhibitMuseumArea
FinancialTransactionsArea
GeneralCommercialIndustrialWorkAreaHighBay
GeneralCommercialIndustrialWorkAreaLowBay
GeneralCommercialIndustrialWorkAreaPrecision
GrocerySalesArea
GymnasiumSportsArena
HighRiseResidentialLivingSpace
HotelFunctionArea
HotelMotelGuestRoom
HousingPublicCommonAreaMultifamilyDormitory
HousingPublicCommonAreaSeniorHousing
KitchenCommercialFoodPreparation
KitchenetteResidentialKitchen
LaboratoryEquipmentRoom
LaboratoryScientific
Laundry
LibraryReadingArea
LibraryStacks
LobbyHotel
LobbyMainEntry
LockerDressingRoom
LoungeRecreational
MallAndAtria
MedicalAndClinicalCare
NurseriesForChildrenDayCare
Office250FtOrLess
OfficeGreaterThan250Ft
ParkingGarageAreaDaylightAdaptationZone
ParkingGarageAreaDedicatedRamp
ParkingGarageBuildingParkingArea
PoliceStationFireStation
ReligiousWorshipArea
RetailMerchandiseSalesWholesaleShowroom
TheaterMotionPicture
TheaterPerformance
TransportationFunction
TransportationFunctionConcourseBaggage
TransportationFunctionTicketing
UnleasedTenantArea
UnoccupiedExcludeInGrossFloorArea
UnoccupiedIncludeInGrossFloorArea
VideoConferencingStudio
WaitingArea
SpaceFunctionDefaultsReference | SpcFuncDefaultsRef | reference | none | [7 empty] | Optional |  |  | Reference to a unique SpaceFunctionDefaults object name
SpaceWaterHeaterReference | WtrHterRef | reference | none
SpandrelPanelsCurtainWalls | SpandrelPanelsCurtainWalls | enumerated list |  | AluminumNoThermalBreakDoubleNoLowENoIns
AluminumNoThermalBreakDoubleNoLowER10Ins
AluminumNoThermalBreakDoubleNoLowER15Ins
AluminumNoThermalBreakDoubleNoLowER20Ins
AluminumNoThermalBreakDoubleNoLowER25Ins
AluminumNoThermalBreakDoubleNoLowER30Ins
AluminumNoThermalBreakDoubleNoLowER4Ins
AluminumNoThermalBreakDoubleNoLowER7Ins
AluminumNoThermalBreakSingleGlassStoneMetalNoIns
AluminumNoThermalBreakSingleGlassStoneMetalR10Ins
AluminumNoThermalBreakSingleGlassStoneMetalR15Ins
AluminumNoThermalBreakSingleGlassStoneMetalR20Ins
AluminumNoThermalBreakSingleGlassStoneMetalR25Ins
AluminumNoThermalBreakSingleGlassStoneMetalR30Ins
AluminumNoThermalBreakSingleGlassStoneMetalR4Ins
AluminumNoThermalBreakSingleGlassStoneMetalR7Ins
AluminumNoThermalBreakTripleOrLowENoIns
AluminumNoThermalBreakTripleOrLowER10Ins
AluminumNoThermalBreakTripleOrLowER15Ins
AluminumNoThermalBreakTripleOrLowER20Ins
AluminumNoThermalBreakTripleOrLowER25Ins
AluminumNoThermalBreakTripleOrLowER30Ins
AluminumNoThermalBreakTripleOrLowER4Ins
AluminumNoThermalBreakTripleOrLowER7Ins
AluminumThermalBreakDoubleNoLowENoIns
AluminumThermalBreakDoubleNoLowER10Ins
AluminumThermalBreakDoubleNoLowER15Ins
AluminumThermalBreakDoubleNoLowER20Ins
AluminumThermalBreakDoubleNoLowER25Ins
AluminumThermalBreakDoubleNoLowER30Ins
AluminumThermalBreakDoubleNoLowER4Ins
AluminumThermalBreakDoubleNoLowER7Ins
AluminumThermalBreakSingleGlassStoneMetalNoIns
AluminumThermalBreakSingleGlassStoneMetalR10Ins
AluminumThermalBreakSingleGlassStoneMetalR15Ins
AluminumThermalBreakSingleGlassStoneMetalR20Ins
AluminumThermalBreakSingleGlassStoneMetalR25Ins
AluminumThermalBreakSingleGlassStoneMetalR30Ins
AluminumThermalBreakSingleGlassStoneMetalR4Ins
AluminumThermalBreakSingleGlassStoneMetalR7Ins
AluminumThermalBreakTripleOrLowENoIns
AluminumThermalBreakTripleOrLowER10Ins
AluminumThermalBreakTripleOrLowER15Ins
AluminumThermalBreakTripleOrLowER20Ins
AluminumThermalBreakTripleOrLowER25Ins
AluminumThermalBreakTripleOrLowER30Ins
AluminumThermalBreakTripleOrLowER4Ins
AluminumThermalBreakTripleOrLowER7Ins
ContinuousInsulationDoubleNoLowENoIns
ContinuousInsulationDoubleNoLowER10Ins
ContinuousInsulationDoubleNoLowER15Ins
ContinuousInsulationDoubleNoLowER20Ins
ContinuousInsulationDoubleNoLowER25Ins
ContinuousInsulationDoubleNoLowER30Ins
ContinuousInsulationDoubleNoLowER4Ins
ContinuousInsulationDoubleNoLowER7Ins
ContinuousInsulationSingleGlassStoneMetalNoIns
ContinuousInsulationSingleGlassStoneMetalR10Ins
ContinuousInsulationSingleGlassStoneMetalR15Ins
ContinuousInsulationSingleGlassStoneMetalR20Ins
ContinuousInsulationSingleGlassStoneMetalR25Ins
ContinuousInsulationSingleGlassStoneMetalR30Ins
ContinuousInsulationSingleGlassStoneMetalR4Ins
ContinuousInsulationSingleGlassStoneMetalR7Ins
ContinuousInsulationTripleOrLowENoIns
ContinuousInsulationTripleOrLowER10Ins
ContinuousInsulationTripleOrLowER15Ins
ContinuousInsulationTripleOrLowER20Ins
ContinuousInsulationTripleOrLowER25Ins
ContinuousInsulationTripleOrLowER30Ins
ContinuousInsulationTripleOrLowER4Ins
ContinuousInsulationTripleOrLowER7Ins
StructuralGlazingDoubleNoLowENoIns
StructuralGlazingDoubleNoLowER10Ins
StructuralGlazingDoubleNoLowER15Ins
StructuralGlazingDoubleNoLowER20Ins
StructuralGlazingDoubleNoLowER25Ins
StructuralGlazingDoubleNoLowER30Ins
StructuralGlazingDoubleNoLowER4Ins
StructuralGlazingDoubleNoLowER7Ins
StructuralGlazingSingleGlassStoneMetalNoIns
StructuralGlazingSingleGlassStoneMetalR10Ins
StructuralGlazingSingleGlassStoneMetalR15Ins
StructuralGlazingSingleGlassStoneMetalR20Ins
StructuralGlazingSingleGlassStoneMetalR25Ins
StructuralGlazingSingleGlassStoneMetalR30Ins
StructuralGlazingSingleGlassStoneMetalR4Ins
StructuralGlazingSingleGlassStoneMetalR7Ins
StructuralGlazingTripleOrLowENoIns
StructuralGlazingTripleOrLowER10Ins
StructuralGlazingTripleOrLowER15Ins
StructuralGlazingTripleOrLowER20Ins
StructuralGlazingTripleOrLowER25Ins
StructuralGlazingTripleOrLowER30Ins
StructuralGlazingTripleOrLowER4Ins
StructuralGlazingTripleOrLowER7Ins
SpecificationMethod | SpecMthd | enumerated list | none | Date | [6 empty] | Required
First
Fourth
Last
Second
Third
Status | Status | enumerated list | none | Altered | [6 empty] | Required |  |  | Defines if a construction or equipment is new, existing, modified, removed. Standards such as efficiency standards may not apply if a construction or equipment in a project is existing. equipment may be moved and reinstalled in the project.
Existing
Future
New
Status | Status | enumerated list | none | [7 empty] | Required |  |  | Status of a component in an existing alteration and addition (EAA)project
Status | Status | enumerated list | none | Existing | [6 empty] | Required |  |  | Defines if a construction or equipment is new, existing, modified, removed. Standards such as efficiency standards may not apply if a construction or equipment in a project is existing. equipment may be moved and reinstalled in the project.
New
StrawBaleWall | StrawBaleWall | enumerated list |  | StrawBaleIntExtStucco18In
SupplyPlenumSpaceReference | SupPlenumSpcRef | reference | none | [7 empty] | Optional | Spc
ThermalZoneReference | ThrmlZnRef | reference | none | [7 empty] | Required |  |  | This is a reference to the thermal zone that serves a given space.
Tilt | Tilt | decimal | deg arc | [7 empty] | CondRequired |  |  | The angle of inclination of a planar surface to the horizontal. Units: degrees Tilt is an attribute of Spatial Attitude that is part of the definition of the Surface Geometry for Exterior Wall and Roof | Usually the term slope is used to mean Tilt in the Standards | Required when Proj:GeometryInpType = 'Simplified', else NotInput
TimeDependentValuation | TDV | decimal | Btu
TimeZone | TimeZn | integer | none | [7 empty] | Optional |  |  | This is the international time zone value for the project, which for California Title 24 projects will be -8
TopLevelOccupancy |  | enumerated list | none | HotelMotelGuestRoom | [9 empty] | The highest-level definition of building occupancy with a value of Nonresidential or a type of residential facility: highrise, hotel/motel or lowrise ( just called residential) . The value for TopLevelOccupancy is assigned based on the occupancy type that covers teh majority of the space. Residential assignments are also dependent on whether the building is single or multi-family, and how many stories there are in the building. | T24 Section 100 Scope (a) Buildings Covered
TotalConditionedVolume | TotCondVol | decimal | ft3 |  |  |  |  | 1 |  |  | Defaulted |  | dtyp:DecimalNonnegative
TotalFloorArea | TotFlrArea | decimal | ft2 |  |  |  |  | 1 |  |  | Defaulted |  |  | BuildlingGrossTotalFloorArea is the gross floor area of the building measured from exterior surface to exterior surface and including all reas inside the building envelope. | 2013 Title 24 Section 140 (c) Calculation of Allowed Indoor Lighting Power Density 1. Complete Building Method involves the entire building which is defined as including all conditioned and unconditioned space which a building permit is sought plus any conditioned and unconditioned space of the existing structure when applying lighting compliance to the complete building. 2013 NR ACM 5.2.2 Baseline Standard Building Classification discusses use of the Complete Building Method
TotalStoryCount | TotStoryCnt | integer | none |  |  |  |  | 1 |  |  | Required |  | dtyp:IntegerNonnegative | The total number of stories in a building and includes both above grade stories and any below grade stories. | 2013 NR ACM
TotalStoryCountAltered | TotStoryCntAltered | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of altered stories in an alterations/additions building and includes both above grade stories and any below grade stories. | 2013 NR ACM
TotalStoryCountExisting | TotStoryCntExisting | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of existing stories in an alterations/additions building and includes both above grade stories and any below grade stories. | 2013 NR ACM
TotalStoryCountNew | TotStoryCntNew | integer | none |  |  |  |  | 0 |  |  | Optional |  | dtyp:IntegerNonnegative | The total number of new stories in an alterations/additions building and includes both above grade stories and any below grade stories. | 2013 NR ACM
TotalUnconditionedFloorArea | TotUncondFlrArea | decimal | ft2 | [7 empty] | NotInput |  |  | All unconditioned floor area in the Building project. It can be derived by summing Zone Floor Area of all Zones with Space Conditioning Type set to Unconditioned | 2008 NR ACM 5.7.1.1: The total floor area of enclosed unconditioned space in the building. Used to describe compliance documentation necessary for additions when meeting the indoor lighting requirements of the Nonresidential Standards.
Transmittance | Trans | decimal | none | [7 empty] | Optional
TransmittanceOption | TransOption | enumerated list | none | Constant | [6 empty] | Defaulted
Scheduled
TransmittanceScheduleReference | TransSchRef | reference | none | [7 empty] | Optional | Sch |  | A schedule of type Fraction which defines the hourly transmittance of the shading object. | 2013 NR ACM 5.5.7
Type | Type | enumerated list | none | Fraction | [6 empty] | Compulsory |  |  | A list of schedule control mechanisms
OnOff
Temperature
ThrmlEngyStorMode
Type | Type | enumerated list | none | Cooling | [6 empty] | Required |  |  |  | 2013 NR ACM section 5.2.3 Geographic and Climate Data Design Day Data
Heating
Type | Type | enumerated list | none | InsulatedSingleLayerSectionalMetal | [6 empty] | Required |  |  |  | 2013 Joint Appendix JA4 Table 4.5.1 Opaque Doors
InsulatedSwingingMetal
UninsulatedDoubleLayerMetal
UninsulatedSingleLayerMetal
UninsulatedSingleLayerRollupMetal
WoodOther
WoodThick
Type | Type | enumerated list | none | ThrmlEngyStorMode | No | [5 empty] | Compulsory
UFactor | UFactor | decimal | Btu per h ft2 F | [7 empty] | Optional |  | dtyp:Decimal3Places | The overall coefficient of thermal transmittance through a layer or construction assembly. It includes air film resistance at both surfaces. | T24 Part 6 definition: U-FACTOR is the overall coefficient of thermal transmittance of a construction assembly, in Btu/(hr x ft² x ºF). Used in table 143 and JA 4 tables of construction assemblies
UFactor | UFactor | decimal | Btu per h ft2 F |  |  |  |  | 0 | 2.5 |  | CondRequired |  |  | The overall coefficient of thermal transmittance through a layer or construction assembly. It includes air film resistance at both surfaces. | T24 Part 6 definition: U-FACTOR is the overall coefficient of thermal transmittance of a construction assembly, in Btu/(hr x ft² x ºF). Used in table 143 and JA 4 tables of construction assemblies
UFactorCenterOfGlass | UFactorCOG | decimal | Btu per h ft2 F | [7 empty] | CondRequired |  |  | The overall coefficient of thermal transmittance through glass of a fenestration product.
VentilationAirChangesPerHour | VentACH | decimal | ft3 per min | [7 empty] | Optional |  |  |  |  | Compliance Use shown here is for Space. When this property is used in SpaceFunctionDefaults, Compliance Use is Defaulted.
VentilationPerArea | VentPerArea | decimal | ft3 per min ft2 | [7 empty] | Defaulted
VentilationPerPerson | VentPerPerson | decimal | ft3 per min person | [7 empty] | Defaulted
VentilationPerSpace | VentPerSpc | decimal | ft3 per min | [7 empty] | Optional
VeryValuableDisplayDescription | VeryValDispDesc | string | none | [7 empty] | Optional |  |  |  | NRCCLTI01E
VisibleReflectance | VisRefl | decimal | none | [7 empty] | Optional |  |  | From E+ Input/Output Ref:The diffuse visible reflectance of the unglazed part of the shading surface (default = 0.2). This reflectance is assumed to be the same for beam-to-diffuse and diffuse-to-diffuse reflection. Beam-to-diffuse reflection is assumed to be independent of angle of incidence of beam radiation. Diffuse-to-diffuse reflection is assumed to be independent of angular distribution of the incident of diffuse radiation. The outgoing diffuse radiation is assumed to be isotropic (hemispherically uniform). This value if used only for the daylighting calculation (ref: Daylighting:Controls). The sum of this reflectance and the shading surface transmittance should be less than or equal to 1.0. | 2013 NR ACM 5.5.7
VisibleTransmittance | VT | decimal | none | [7 empty] | CondRequired |  |  | The fraction of incident visible radiation that is transmitted by the material. Visible radiation includes only a sub-range of solar radiation and excludes infrared and ultraviolet wavelengths. | 2088 NR ACM only refers to VT in the section5, Reference Method Comparison Tests. Title 24 part 6 has only a definition for the term but never explicitly applies it. 2013 NR ACM Table 50 – Baseline Building Criteria for Vertical Glazing for 90.1 2001 referred to as VT.
VisibleTransmittanceCenterOfGlass | VTCOG | decimal | none | [7 empty] | CondRequired |  |  | The fraction of incident visible radiation that is transmitted by the material. Visible radiation includes only a sub-range of solar radiation and excludes infrared and ultraviolet wavelengths. | 2088 NR ACM only refers to VT in the section5, Reference Method Comparison Tests. Title 24 part 6 has only a definition for the term but never explicitly applies it. 2013 NR ACM Table 50 – Baseline Building Criteria for Vertical Glazing for 90.1 2001 referred to as VT.
Volume | Vol | decimal | ft3 | [7 empty] | Required |  |  | The measurement of space or object calculated by multiplying the three dimensions of the space: length, width, and height. | Title 24 and JA II have a definition for conditioned volume as follows: CONDITIONED VOLUME is the total volume (in cubic feet) of the conditioned space within a building
WeatherStation | WeatherStation | enumerated list | none | ALTURAS725958 | [6 empty] | Required |  |  | 86 different weather stations that provide weather data for different climate zones.
ARCATA725945
BAKERSFIELD723840
BISHOP724800
BISHOP724800
BLUE_CANYON725845
BLYTHE_RIVERSIDE_CO747188
BURBANK_GLENDALE722880
CAMP_PENDLETON722926
CARLSBAD722927
CHINA_LAKE746120
CHINO722899
CONCORD724936
CRESCENT_CITY725946
DAGGETT_BARSTOW723815
DAGGETT_BARSTOW723815
EL_CENTRO722810
EUREKA725940
FAIRFLD_TRAVIS_AFB745160
FRESNO723890
FULLERTON722976
HAWTHORNE_NORTHROP_FLD722956
HAYWARD724935
IMPERIAL747185
IMPERIAL_BEACH722909
INYOKERN723826
LANCASTER723816
LEMOORE747020
LIVERMORE724927
LOMPOC722895
LONG_BEACH722970
LOS_ALAMITOS722975
LOS_ANGELES_DOWNTOWN722874
LOS_ANGELES_INTL722950
MARYSVILLE_BEALE_AFB724837
MERCED724815
MODESTO724926
MOJAVE722953
MONTAGUE_SISKIYOU_CO725955
MONTEREY724915
MONTEREY724915
NAPA_CO724955
NEEDLES723805
OAKLAND724930
OXNARD723927
PALMDALE723820
PALM_SPRINGS_INTL722868
PALM_SPRINGS_INTL722868
PALO_ALTO724937
PASO_ROBLES723965
POINT_MUGU723910
PORTERVILLE723895
REDDING725920
RED_BLUFF725910
RIVERSIDE722869
RIVERSIDE_MARCH_AFB722860
SACRAMENTO_EXECUTIVE724830
SACRAMENTO_METRO724839
SALINAS724917
SANDBERG723830
SANTA_ANA722977
SANTA_BARBARA723925
SANTA_MARIA723940
SANTA_MONICA722885
SANTA_ROSA724957
SAN_CARLOS724938
SAN_CLEMENTE_IS722925
SAN_DIEGO_GILLESPIE722907
SAN_DIEGO_LINDBERGH722900
SAN_DIEGO_MONTGOMER722903
SAN_DIEGO_NORTH_IS722906
SOUTH_LAKE_TAHOE725847
STOCKTON724920
TORRANCE722955
TRUCKEE_TAHOE725846
TWENTYNINE_PALMS690150
UKIAH725905
VANDENBERG_AFB723930
VAN_NUYS722886
VISALIA723896
YUBA_CO724838
WeatherStationNumber | WeatherStationNum | integer | none | [7 empty] | Optional |  |  | A numeric value for each of the 86 weather stations used for table lookup
WholeBuildingModeled | WholeBldgModeled | boolean | none | [7 empty] | Defaulted |  |  |  | 2013 NR ACM
WholePlantModeled | WholePlantModeled | boolean | none |  | No | [5 empty] | Defaulted
Width | Wd | decimal | ft | [7 empty] | CondRequired |  |  | The shorter of the two dimensions of a horizontal rectangular surface or the horizontal extent of a vertical rectangular surface Units: feet | The Standards use length and width interchangeably. For example the Display Perimeter which is the horizontal dimension of a vertical surface is defined as the length of an exterior wall, but the horizontal dimension for window which is also a vertical surface is referred to as width. | Required when GeometryInpType = Simplified and window shades specified, else NotInput
WindDirection | WindDirection | decimal | deg arc | [7 empty] | Required |  |  |  | 2013 NR ACM section 5.2.3 Geographic and Climate Data Weather Data for Simulation
WindowDivider | WinDivider | enumerated list | none | DividerBetwnPanesGreaterThanOrEqualTo7_16in | [6 empty] | CondRequired |  |  | Used in selection of default properties
DividerBetwnPanesLessThan7_16in
NoDivider
NotApplicable
TrueDividedLite
WindowReference | WinRef | reference | none |  | No | [5 empty] | Optional | Win
WindSpeed | WindSpd | decimal | mph | [7 empty] | Required |  |  |  | 2013 NR ACM section 5.2.3 Geographic and Climate Data Weather Data for Simulation
Woods | Woods | enumerated list |  | Ash1In
Birch1In
CaliforniaRedwood1In
DouglasFirLarch1In
Hardwood0_5In
Hardwood0_75In
Hardwood1In
Maple1In
Oak1In
PineOvenDried1In
Wood0_5In
Wood1In
Wood2In
Wood4In
WoodSiding0_5In
WorkPlaneHeight | WorkPlaneHgt | decimal | ft | [7 empty] | Defaulted |  |  | Distance from the finished floor to the work plane. Used to calculate vertical distance from the work plane to the centerline of the lighting fixture | 2013 Title 24 part 6 Table 140.6-F
X | X | decimal | ft | [7 empty] | CondRequired |  |  | A member of a CartesianPoint representing the length along the X axis from the origin. |  | For CBECC-Com nonresidential simulations, this is required when GeometryInpType = Simplified and window shades specified and multiple windows or doors, else NotInput
Y | Y | decimal | ft | [7 empty] | CondRequired |  |  | A member of a CartesianPoint representing the length along the Y axis from the origin. |  | For CBECC-Com nonresidential simulations, this is required when GeometryInpType = Simplified and window shades specified and multiple windows or doors, else NotInput
Z | Z | decimal | ft | [7 empty] | CondRequired |  |  | Height above site ground level (negative for below grade stories) | 2013 NR ACM | Required when Project:GeometryInputType = 'Simplified', else NotInput
Zipcode | Zipcode | string | none | [9 empty] | dtyp:Zipcode

## Enumerations
|  | CBECC NR Term | CBECC NR Term Short Form | CBECC NR XML Term | Property | Term Order | Definition | Schedule Occupancy Type | CBCOccupancyGroup | Group | Top Level Occupancy Type | Standards Reference
General Enumerations
AllowanceType
|  | AccentDisplayFeature | AccentDisplayFeature |  | AllowanceType
|  | Decorative | Decorative |  | AllowanceType
|  | Ornamental | Ornamental |  | AllowanceType
|  | ParkingGarageATMLighting |  |  | AllowanceType
|  | PrecisionCommercialIndustrial | PrecisionCommercialIndustrial |  | AllowanceType
|  | SpecializedLabTaskWork | SpecializedLabTaskWork |  | AllowanceType
|  | SpecializedTaskWork | SpecializedTaskWork |  | AllowanceType
|  | TailoredFloorDisplayAllowance | TailoredFloorDisplayAllowance |  | AllowanceType |  | Tailored Method lighting allowance for floor displays.
|  | TailoredOrnamentalAndSpecialEffectAllowance | TailoredOrnamentalAndSpecialEffectAllowance |  | AllowanceType
|  | TailoredTaskAllowance | TailoredTaskAllowance |  | AllowanceType
|  | TailoredVeryValuableDisplayCaseAllowance | TailoredVeryValuableDisplayCaseAllowance |  | AllowanceType
|  | TailoredWallDisplayAllowance | TailoredWallDisplayAllowance |  | AllowanceType |  | Tailored Method lighting allowance for wall displays.
|  | VideoConferencingStudioLighting | VideoConferencingStudioLighting |  | AllowanceType
|  | WhiteOrChalkBoard | WhiteOrChalkBoard |  | AllowanceType
AssemblyContext
|  | FieldFabricated | FieldFabricated |  | AssemblyContext
|  | Manufactured | Manufactured |  | AssemblyContext
|  | SiteBuilt | SiteBuilt |  | AssemblyContext
BuildingTerrain
|  | City | City |  | BuildingTerrain
|  | Country | Country |  | BuildingTerrain
|  | Ocean | Ocean |  | BuildingTerrain
|  | Suburbs | Suburbs |  | BuildingTerrain
|  | Urban | Urban |  | BuildingTerrain
CavityInsulationOption
|  | R0 | R0 | R-0 | CavityInsulationOption
|  | R10 | R10 | R-10 | CavityInsulationOption
|  | R10_R13 | R10_R13 | R-10 + R-13 | CavityInsulationOption
|  | R11 | R11 | R-11 | CavityInsulationOption
|  | R13 | R13 | R-13 | CavityInsulationOption
|  | R13_R13 | R13_R13 | R-13 + R-13 | CavityInsulationOption
|  | R15 | R15 | R-15 | CavityInsulationOption
|  | R16 | R16 | R-16 | CavityInsulationOption
|  | R19 | R19 | R-19 | CavityInsulationOption
|  | R19_R13 | R19_R13 | R-19 + R-13 | CavityInsulationOption
|  | R20 | R20 | R-20 | CavityInsulationOption
|  | R21 | R21 | R-21 | CavityInsulationOption
|  | R22 | R22 | R-22 | CavityInsulationOption
|  | R23 | R23 | R-23 | CavityInsulationOption
|  | R24_CavNR |  |  | CavityInsulationOption
|  | R25 | R25 | R-25 | CavityInsulationOption
|  | R26 | R26 | R-26 | CavityInsulationOption
|  | R29 | R29 | R-29 | CavityInsulationOption
|  | R30 | R30 | R-30 | CavityInsulationOption
|  | R32 | R32 | R-32 | CavityInsulationOption
|  | R35 | R35 | R-35 | CavityInsulationOption
|  | R36 | R36 | R-36 | CavityInsulationOption
|  | R38 | R38 | R-38 | CavityInsulationOption
|  | R5 | R5 | R-5 | CavityInsulationOption
|  | R6 | R6 | R-6 | CavityInsulationOption
|  | R6_R13 | R6_R13 | R-6 + R-13 | CavityInsulationOption
CertificationMethod
|  | CECDefaultPerformance | DefaultPerformance | DefaultPerformance | CertificationMethod
|  | CECDefaultPerformance_Door |  |  | CertificationMethod
|  | COGEquations | COGEquations |  | CertificationMethod
|  | NFRCRated | NFRCRated |  | CertificationMethod
|  | NFRCRated_Door |  |  | CertificationMethod
ClimateZone
|  | ClimateZone1 | ClimateZone1 |  | ClimateZone | 1 | CA Title 24 Climate Zone1
|  | ClimateZone2 | ClimateZone2 |  | ClimateZone | 2 | CA Title 24 Climate Zone 2
|  | ClimateZone3 | ClimateZone3 |  | ClimateZone | 3 | CA Title 24 Climate Zone 3
|  | ClimateZone4 | ClimateZone4 |  | ClimateZone | 4 | CA Title 24 Climate Zone 4
|  | ClimateZone5 | ClimateZone5 |  | ClimateZone | 5 | CA Title 24 Climate Zone 5
|  | ClimateZone6 | ClimateZone6 |  | ClimateZone | 6 | CA Title 24 Climate Zone 6
|  | ClimateZone7 | ClimateZone7 |  | ClimateZone | 7 | CA Title 24 Climate Zone 7
|  | ClimateZone8 | ClimateZone8 |  | ClimateZone | 8 | CA Title 24 Climate Zone 8
|  | ClimateZone9 | ClimateZone9 |  | ClimateZone | 9 | CA Title 24 Climate Zone 9
|  | ClimateZone10 | ClimateZone10 |  | ClimateZone | 10 | CA Title 24 Climate Zone 10
|  | ClimateZone11 | ClimateZone11 |  | ClimateZone | 11 | CA Title 24 Climate Zone 11
|  | ClimateZone12 | ClimateZone12 |  | ClimateZone | 12 | CA Title 24 Climate Zone 12
|  | ClimateZone13 | ClimateZone13 |  | ClimateZone | 13 | CA Title 24 Climate Zone 13
|  | ClimateZone14 | ClimateZone14 |  | ClimateZone | 14 | CA Title 24 Climate Zone14
|  | ClimateZone15 | ClimateZone15 |  | ClimateZone | 15 | CA Title 24 Climate Zone15
|  | ClimateZone16 | ClimateZone16 |  | ClimateZone | 16 | CA Title 24 Climate Zone 16
ClimateZoneCounty
|  | Alameda | Alameda | Alameda | ClimateZoneCounty
|  | Alpine | Alpine | Alpine | ClimateZoneCounty
|  | Amador | Amador | Amador | ClimateZoneCounty
|  | Butte | Butte | Butte | ClimateZoneCounty
|  | Calaveras | Calaveras | Calaveras | ClimateZoneCounty
|  | Colusa | Colusa | Colusa | ClimateZoneCounty
|  | ContraCosta | ContraCosta | Contra Costa | ClimateZoneCounty
|  | DelNorte | DelNorte | Del Norte | ClimateZoneCounty
|  | ElDorado | ElDorado | El Dorado | ClimateZoneCounty
|  | Fresno | Fresno | Fresno | ClimateZoneCounty
|  | Glenn | Glenn | Glenn | ClimateZoneCounty
|  | Humboldt | Humboldt | Humboldt | ClimateZoneCounty
|  | Imperial | Imperial | Imperial | ClimateZoneCounty
|  | Inyo | Inyo | Inyo | ClimateZoneCounty
|  | Kern | Kern | Kern | ClimateZoneCounty
|  | Kings | Kings | Kings | ClimateZoneCounty
|  | Lake | Lake | Lake | ClimateZoneCounty
|  | Lassen | Lassen | Lassen | ClimateZoneCounty
|  | LosAngeles | LosAngeles | Los Angeles | ClimateZoneCounty
|  | Madera | Madera | Madera | ClimateZoneCounty
|  | Marin | Marin | Marin | ClimateZoneCounty
|  | Mariposa | Mariposa | Mariposa | ClimateZoneCounty
|  | Mendocino | Mendocino | Mendocino | ClimateZoneCounty
|  | Merced | Merced | Merced | ClimateZoneCounty
|  | Modoc | Modoc | Modoc | ClimateZoneCounty
|  | Mono | Mono | Mono | ClimateZoneCounty
|  | Monterey | Monterey | Monterey | ClimateZoneCounty
|  | Napa | Napa | Napa | ClimateZoneCounty
|  | Nevada | Nevada | Nevada | ClimateZoneCounty
|  | Orange | Orange | Orange | ClimateZoneCounty
|  | Placer | Placer | Placer | ClimateZoneCounty
|  | Plumas | Plumas | Plumas | ClimateZoneCounty
|  | Riverside | Riverside | Riverside | ClimateZoneCounty
|  | Sacramento | Sacramento | Sacramento | ClimateZoneCounty
|  | SanBenito | SanBenito | San Benito | ClimateZoneCounty
|  | SanBernardino | SanBernardino | San Bernardino | ClimateZoneCounty
|  | SanDiego | SanDiego | San Diego | ClimateZoneCounty
|  | SanFrancisco | SanFrancisco | San Francisco | ClimateZoneCounty
|  | SanJoaquin | SanJoaquin | San Joaquin | ClimateZoneCounty
|  | SanLuisObispo | SanLuisObispo | San Luis Obispo | ClimateZoneCounty
|  | SanMateo | SanMateo | San Mateo | ClimateZoneCounty
|  | SantaBarbara | SantaBarbara | Santa Barbara | ClimateZoneCounty
|  | SantaClara | SantaClara | Santa Clara | ClimateZoneCounty
|  | SantaCruz | SantaCruz | Santa Cruz | ClimateZoneCounty
|  | Shasta | Shasta | Shasta | ClimateZoneCounty
|  | Sierra | Sierra | Sierra | ClimateZoneCounty
|  | Siskiyou | Siskiyou | Siskiyou | ClimateZoneCounty
|  | Solano | Solano | Solano | ClimateZoneCounty
|  | Sonoma | Sonoma | Sonoma | ClimateZoneCounty
|  | Stanislaus | Stanislaus | Stanislaus | ClimateZoneCounty
|  | Sutter | Sutter | Sutter | ClimateZoneCounty
|  | Tehama | Tehama | Tehama | ClimateZoneCounty
|  | Trinity | Trinity | Trinity | ClimateZoneCounty
|  | Tulare | Tulare | Tulare | ClimateZoneCounty
|  | Tuolumne | Tuolumne | Tuolumne | ClimateZoneCounty
|  | Ventura | Ventura | Ventura | ClimateZoneCounty
|  | Yolo | Yolo | Yolo | ClimateZoneCounty
|  | Yuba | Yuba | Yuba | ClimateZoneCounty
ClimateZoneNumber
|  | 1 | 1 |  | ClimateZoneNumber
|  | 10 | 10 |  | ClimateZoneNumber
|  | 11 | 11 |  | ClimateZoneNumber
|  | 12 | 12 |  | ClimateZoneNumber
|  | 13 | 13 |  | ClimateZoneNumber
|  | 14 | 14 |  | ClimateZoneNumber
|  | 15 | 15 |  | ClimateZoneNumber
|  | 16 | 16 |  | ClimateZoneNumber
|  | 2 | 2 |  | ClimateZoneNumber
|  | 3 | 3 |  | ClimateZoneNumber
|  | 4 | 4 |  | ClimateZoneNumber
|  | 5 | 5 |  | ClimateZoneNumber
|  | 6 | 6 |  | ClimateZoneNumber
|  | 7 | 7 |  | ClimateZoneNumber
|  | 8 | 8 |  | ClimateZoneNumber
|  | 9 | 9 |  | ClimateZoneNumber
CodeCategory
|  | Air | Air | Air | CodeCategory
|  | Composite | Composite | Composite | CodeCategory
|  | Concrete | Concrete | Concrete | CodeCategory
|  | ICFWall | ICFWall | ICF Wall | CodeCategory |  | A type of wall construction which uses concrete forming systems that use stay-in-place panels made from avariety of insulating materials for constructing cast-in-place solid concrete walls. Rules for this type are found in JA 4 Table 4.3.13 Thermal Properties of Insulating Concrete Forms |  |  |  |  | 2013 JA4
|  | SIPSFloor | SIPS Floor | SIPS Floor | CodeCategory
|  | SIPSRoof | SIPSRoof | SIPS Roof | CodeCategory
|  | SIPSWall | SIPSWall | SIPS Wall | CodeCategory
|  | StrawBaleWall | StrawBaleWall | Straw Bale Wall | CodeCategory
|  | Wood | Wood | Woods | CodeCategory
CompatibleSurfaceType
|  | Ceiling | Ceiling |  | CompatibleSurfaceType
|  | ExteriorFloor | ExteriorFloor |  | CompatibleSurfaceType
|  | ExteriorWall | ExteriorWall |  | CompatibleSurfaceType
|  | InteriorFloor | InteriorFloor |  | CompatibleSurfaceType
|  | InteriorWall | InteriorWall |  | CompatibleSurfaceType
|  | Roof | Roof |  | CompatibleSurfaceType
|  | UndergroundFloor | UndergroundFloor |  | CompatibleSurfaceType
|  | UndergroundWall | UndergroundWall |  | CompatibleSurfaceType
ConditioningType
|  | DirectlyConditioned | DirectlyConditioned |  | ConditioningType |  | An enclosed space that is served by a heating and/or cooling systems to provide thermal comfort conditioning to the occupants.
|  | IndirectlyConditioned | IndirectlyConditioned |  | ConditioningType |  | Describes an enclosed space, including, but not limited to, unconditioned volume in atria, that (1) is not directly conditioned space; and (2) either (a) has a thermal transmittance area product (UA) to directly conditioned space exceeding that to the outdoors or to unconditioned space ... or (b) is a space through which air from directly conditioned spaces is transferred at a rate exceeding three air changes per hour. |  |  |  |  | Reference: 2008 NR ACM 2.3.1.2
|  | Unconditioned | Unconditioned |  | ConditioningType |  | Defines an enclosed space within a building that is not directly conditioned, or indirectly conditioned. |  |  |  |  | Reference: NR ACM 2.3.1.3 Enclosed Unconditioned: Compliance software shall require the user to explicitly model any enclosed unconditioned spaces such as stairways, warehouses, unoccupied adjacent tenant spaces, attached sunspaces, attics and crawl spaces if and only if they are part of the permitted space.
ControlSystemType
|  | DDCToZoneLevel | DirectDigitalControlsToZoneLevel |  | ControlSystemType
|  | NoControlSystem | NoControlSystem |  | ControlSystemType
|  | OtherControlSystem | OtherControlSystem |  | ControlSystemType
DaylightingControlType
|  | Continuous | Continuous |  | DaylightingControlType |  | Continuous Dimming controls have a linear relationship between fraction of rated power to fraction of rated light output. This relationship is a linear interpolation between the maximum power fraction (1.0) at full light output (1.0) and the minimum power fraction at the minimum dimmed light output.
|  | ContinuousPlusOff | ContinuousPlusOff |  | DaylightingControlType |  | Continuous Dimming + Off controls are the same as continuous dimming controls except that these controls can turn all the way off when none of the controlled light output is needed.
|  | None | None |  | DaylightingControlType
|  | SteppedSwitching | SteppedSwitching |  | DaylightingControlType |  | Step Switching controls have discrete steps of light output, where the fraction of rated power matches the fraction of light output.
DaylitAreaType
|  | PrimarySidelit | PrimarySidelit |  | DaylitAreaType |  | The area on plan directly adjacent to each vertical glazing, one window head height deep into the area, and window width plus 0.5 times window head height wide on each side of the rough opening of the window, minus any area on plan beyond a permanent obstruction that is 6 feet or taller as measured from the floor.
|  | SecondarySidelit | SecondarySidelit |  | DaylitAreaType
|  | SkylitDaylit | SkylitDaylit |  | DaylitAreaType |  | The area on plan under each skylight, 0.7 times ceiling height in each direction from the edge of the rough opening of the skylight, minus any area on plan beyond a permanent obstruction that is taller than the following: A permanent obstruction that is taller than one-half the distance from the floor to the bottom of the skylight.
DayOfWeek
|  | Friday | Friday |  | DayOfWeek
|  | Monday | Monday |  | DayOfWeek
|  | Saturday | Saturday |  | DayOfWeek
|  | Sunday | Sunday |  | DayOfWeek
|  | Thursday | Thursday |  | DayOfWeek
|  | Tuesday | Tuesday |  | DayOfWeek
|  | Wednesday | Wednesday |  | DayOfWeek
EnvelopeStatus
|  | Altered | Altered |  | EnvelopeStatus
|  | Existing | Existing |  | EnvelopeStatus
|  | New | New |  | EnvelopeStatus
FenestrationPanes
|  | DoublePane | DoublePane |  | FenestrationPanes
|  | GlassBlock | GlassBlock |  | FenestrationPanes
|  | SinglePane | SinglePane |  | FenestrationPanes
|  | TranslucentOrTransparentPanel | TranslucentOrTransparentPanel |  | FenestrationPanes
FenestrationProductType
|  | CurtainWall | CurtainWall |  | FenestrationProductType
|  | FixedWindow | FixedWindow |  | FenestrationProductType
|  | GlazedDoor | GlazedDoor |  | FenestrationProductType
|  | NotApplicable | NotApplicable | - n/a - | FenestrationProductType
|  | OperableWindow | OperableWindow |  | FenestrationProductType
|  | Skylight | Skylight |  | FenestrationProductType
FenestrationType
|  | VerticalFenestration | VerticalFenestration |  | FenestrationType
FixtureType
|  | NotInCeiling | NotInCeiling |  | FixtureType
|  | RecessedOrDownlight | RecessedOrDownlight |  | FixtureType
|  | RecessedWithLens | RecessedWithLens |  | FixtureType
FramingConfiguration
|  | Floor16inOC | Floor16inOC |  | FramingConfiguration
|  | Floor24inOC | Floor24inOC |  | FramingConfiguration
|  | Roof16inOC | Roof16inOC |  | FramingConfiguration
|  | Roof24inOC | Roof24inOC |  | FramingConfiguration
|  | Roof48inOC | Roof48inOC |  | FramingConfiguration
|  | RoofMetalScrewDown | RoofMetalScrewDown |  | FramingConfiguration
|  | RoofMetalStandingSeam | RoofMetalStandingSeam |  | FramingConfiguration
|  | RoofMetalStandingSeamFilledCavity | RoofMetalStandingSeamFilledCavity |  | FramingConfiguration
|  | Wall16inOC | Wall16inOC |  | FramingConfiguration
|  | Wall24inOC | Wall24inOC |  | FramingConfiguration
|  | WallAWS24inOC | WallAWS24inOC |  | FramingConfiguration
|  | WallAWS48inOC | WallAWS48inOC |  | FramingConfiguration
|  | WallMetalDoubleLayerBatt | WallMetalDoubleLayerBatt |  | FramingConfiguration
|  | WallMetalSingleLayerBatt | WallMetalSingleLayerBatt |  | FramingConfiguration
FramingDepth
|  | 0_5In | 0_5In |  | FramingDepth
|  | 0_75In | 0_75In |  | FramingDepth
|  | 1_5In | 1_5In |  | FramingDepth
|  | 11_25In | 11_25In |  | FramingDepth
|  | 1In | 1In |  | FramingDepth
|  | 2_5In | 2_5In |  | FramingDepth
|  | 2In | 2In |  | FramingDepth
|  | 3_5In | 3_5In |  | FramingDepth
|  | 3In | 3In |  | FramingDepth
|  | 4_5In | 4_5In |  | FramingDepth
|  | 4In | 4In |  | FramingDepth
|  | 5_5In | 5_5In |  | FramingDepth
|  | 5In | 5In |  | FramingDepth
|  | 7_25In | 7_25In |  | FramingDepth
|  | 9_25In | 9_25In |  | FramingDepth
FramingMaterial
|  | Metal | Metal |  | FramingMaterial
|  | Wood | Wood |  | FramingMaterial
FunctionClassificationMethod
|  | AreaCategoryMethod | AreaCategoryMethod |  | FunctionClassificationMethod |  | Space classification method whereby each Space has an associated Function from enumerated list. |  |  |  |  | 2013 NR ACM: Sec 2.1.3 & 5.4 2013 Title 24 Part 6: 140.6(c)2
FunctionScheduleGroup
|  | Assembly | Assembly |  | FunctionScheduleGroup
|  | Data | Data |  | FunctionScheduleGroup
|  | Health | Health |  | FunctionScheduleGroup
|  | Laboratory | Laboratory |  | FunctionScheduleGroup
|  | Manufacturing | Manufacturing |  | FunctionScheduleGroup
|  | Office | Office |  | FunctionScheduleGroup
|  | Parking | Parking |  | FunctionScheduleGroup
|  | ResidentialCommon | ResidentialCommon |  | FunctionScheduleGroup
|  | ResidentialLiving | ResidentialLiving |  | FunctionScheduleGroup
|  | Restaurant | Restaurant |  | FunctionScheduleGroup
|  | Retail | Retail |  | FunctionScheduleGroup
|  | School | School |  | FunctionScheduleGroup
|  | Warehouse | Warehouse |  | FunctionScheduleGroup
GasType
|  | NaturalGas | NaturalGas |  | GasType
|  | Propane | Propane |  | GasType
GlazingTint
|  | ClearGlazing | ClearGlazing |  | GlazingTint
|  | TintedGlazing | TintedGlazing |  | GlazingTint
Hour
|  | Charge | Charge |  | Hour
|  | Discharge | Discharge |  | Hour
|  | Off | Off |  | Hour
InfiltrationMethod
|  | AirChangesPerHour | AirChangesPerHour |  | InfiltrationMethod |  | number of air changes per hour |  |  |  |  | 2013 NR ACM Sec 5.4
|  | FlowArea | FlowArea |  | InfiltrationMethod |  | factor per floor area of the zone or space |  |  |  |  | 2013 NR ACM Sec 5.4
|  | FlowExteriorArea | FlowExteriorArea |  | InfiltrationMethod |  | factor per exterior surface area of the zone or space |  |  |  |  | 2013 NR ACM Sec 5.4
|  | FlowExteriorWallArea | FlowExteriorWallArea |  | InfiltrationMethod |  | factor per exterior wall surface area of the zone or space |  |  |  |  | 2013 NR ACM Sec 5.4
|  | FlowSpace | FlowSpace |  | InfiltrationMethod | [6 empty] | 2013 NR ACM Sec 5.4
InsulationForm
|  | Batt | Batt |  | InsulationForm
|  | Block | Block |  | InsulationForm
|  | Foam | Foam |  | InsulationForm
|  | RigidBoard | RigidBoard |  | InsulationForm
InsulationPlacement
|  | CavityAttic | CavityAttic |  | InsulationPlacement
|  | CavityFraming | CavityFraming |  | InsulationPlacement
|  | CavityFurring | CavityFurring |  | InsulationPlacement
|  | ContinuousAboveDeckNoSleepers | ContinuousAboveDeckNoSleepers |  | InsulationPlacement
|  | ContinuousAboveDeckSleepers | ContinuousAboveDeckSleepers |  | InsulationPlacement
|  | ContinuousAboveWaterproofMembrane | ContinuousAboveWaterproofMembrane |  | InsulationPlacement |  | If Roof.Insulation is placed AboveWaterproofMembrane in ClimateZone 1 or 16, the Insulation.RValue is multiplied by 0.8 before applying the rule that assigns the UFactor.
|  | ContinuousBelowDeck | ContinuousBelowDeck |  | InsulationPlacement
|  | OverSuspendedCeiling | OverSuspendedCeiling |  | InsulationPlacement
|  | SlabFullyInsulated | SlabFullyInsulated |  | InsulationPlacement
|  | SlabHorizontal | SlabHorizontal |  | InsulationPlacement
|  | SlabVertical | SlabVertical |  | InsulationPlacement
InsulationType
|  | Cellulose | Cellulose |  | InsulationType |  | Cellulose is one of the materials used in cavity insulation.
|  | Fiberglass | Fiberglass |  | InsulationType |  | Fiberglass material used in insulation.
|  | MineralWool | MineralWool |  | InsulationType |  | Mineral Wool Insulation is one of the materials used in cavity insulation.
|  | PlasticPolyisocyanurate | PlasticPolyisocyanurate |  | InsulationType |  | Plastic Polyisocyanurate is a type of plastic used in cavity insulation and its RValue is evaluated to assign UFactor in some Joint Appendix 4 tables.
|  | PlasticPolystyrene | PlasticPolystyrene |  | InsulationType |  | PlasticPolystyrene is is a type of plastic used in cavity insulation and its RValue is evaluated to assign UFactor in some Joint Appendix 4 tables.
|  | UreaFormaldehyde | UreaFormaldehyde |  | InsulationType |  | Urea Formaldehyde is a type of plastic or resin used as an insulating material in some construction assemblies, and its RValue is evaluated in order to assign UFactor in some tables in Joint Appendix 4.
InteriorLightingSpecificationMethod
|  | AreaCategoryMethod | AreaCategoryMethod |  | InteriorLightingSpecificationMethod
|  | TailoredMethod | TailoredMethod |  | InteriorLightingSpecificationMethod
KitchenExhaustHoodDuty
|  | ExtraHeavy | ExtraHeavy |  | KitchenExhaustHoodDuty
|  | Heavy | Heavy |  | KitchenExhaustHoodDuty
|  | Light | Light |  | KitchenExhaustHoodDuty
|  | Medium | Medium |  | KitchenExhaustHoodDuty
|  | None | None |  | KitchenExhaustHoodDuty
KitchenExhaustHoodStyle
|  | BackshelfOrPassover | BackshelfOrPassover |  | KitchenExhaustHoodStyle
|  | DoubleIsland | DoubleIsland |  | KitchenExhaustHoodStyle
|  | Eyebrow | Eyebrow |  | KitchenExhaustHoodStyle
|  | SingleIsland | SingleIsland |  | KitchenExhaustHoodStyle
|  | WallMountedCanopy | WallMountedCanopy |  | KitchenExhaustHoodStyle
LaboratoryExhaustRateType
|  | HoodDominated | HoodDominated |  | LaboratoryExhaustRateType
|  | LoadDominated | LoadDominated |  | LaboratoryExhaustRateType
LampType
|  | CFL | CFL |  | LampType
|  | HighPressureSodium | HighPressureSodium |  | LampType
|  | Incandescent | Incandescent |  | LampType
|  | LED | LED |  | LampType
|  | LinearFluorescent | LinearFluorescent |  | LampType
|  | MercuryVapor | MercuryVapor |  | LampType
|  | MetalHalide | MetalHalide |  | LampType
LightingStatus
|  | Altered | Altered |  | LightingStatus
|  | Existing | Existing |  | LightingStatus
|  | New | New |  | LightingStatus
LuminaireStatus
|  | ExistingAlteration_Luminaire |  |  | LuminaireStatus
|  | ExistingUnchanged_Luminaire |  |  | LuminaireStatus
|  | Future_Luminaire |  |  | LuminaireStatus
|  | New_Luminaire |  |  | LuminaireStatus
MasonryGrout
|  | PartialGrout | PartialGrout |  | MasonryGrout |  | PartialGrout is one type of MasonryGrout which indicates that only some cells in a hollow masonry wall are grouted.
|  | PartialInsulatedGrout | PartialInsulatedGrout |  | MasonryGrout |  | PartialinsulatedGrout is one type of MasonryGrout which indicates that only some cells in a hollow masonry wall are grouted and cells not grouted are filled with insulation.
|  | SolidGrout | SolidGrout |  | MasonryGrout |  | SolidGrout is one type of MasonryGrout which indicates that every cell in a hollow masonry wall is grouted.
MasonryType
|  | ClayBrick | ClayBrick |  | MasonryType
|  | ClayHollowUnit | ClayHollowUnit |  | MasonryType |  | Used in masonry walls and its thickness and grout characteristics are evaluated in order to assign UFactor.
|  | Concrete | Concrete |  | MasonryType
|  | ConcreteMasonryUnitLightWeight | ConcreteMasonryUnitLightWeight |  | MasonryType |  | A type of masonry unit used for mass walls with a density of 105 lb/ft^3.
|  | ConcreteMasonryUnitMediumWeight | ConcreteMasonryUnitMediumWeight |  | MasonryType |  | A type of masonry unit used for mass walls with a density of 115 lb/ft^3.
|  | ConcreteMasonryUnitNormalWeight | ConcreteMasonryUnitNormalWeight |  | MasonryType |  | A type of masonry unit used for mass walls with a density of 125 lb/ft^3.
|  | InsulatingConcreteForms | InsulatingConcreteForms |  | MasonryType
Month
|  | April | April |  | Month
|  | August | August |  | Month
|  | December | December |  | Month
|  | February | February |  | Month
|  | January | January |  | Month
|  | July | July |  | Month
|  | June | June |  | Month
|  | March | March |  | Month
|  | May | May |  | Month
|  | November | November |  | Month
|  | October | October |  | Month
|  | September | September |  | Month
NonRegulatedExclusion
|  | ATMLighting | ATMLighting |  | NonRegulatedExclusion
|  | CBCRequiredExitSign | CBCRequiredExitSign |  | NonRegulatedExclusion
|  | CBCRequiredExitwayOrEgressNormallyOff | CBCRequiredExitwayOrEgressNormallyOff |  | NonRegulatedExclusion
|  | DanceFloorOrTheatrical | DanceFloorOrTheatrical |  | NonRegulatedExclusion | [6 empty] | 90.1 2007 Sec 9.2.2.3
|  | ElevatorLighting | ElevatorLighting |  | NonRegulatedExclusion
|  | ExamSurgicalNightOrEquipmentIntegratedInMedicalOrClinical | ExamSurgicalNightOrEquipmentIntegratedInMedicalOrClinical |  | NonRegulatedExclusion | [6 empty] | 90.1 2007 Sec 9.2.2.3
|  | FilmOrPhotoStudioLightingSeparatelySwitched | FilmOrPhotoStudioLightingSeparatelySwitched |  | NonRegulatedExclusion
|  | HighRiseResidentialDwellingUnit | HighRiseResidentialDwellingUnit |  | NonRegulatedExclusion
|  | HistoricBuilding | HistoricBuilding |  | NonRegulatedExclusion
|  | HotelMotelGuestRoom | HotelMotelGuestRoom |  | NonRegulatedExclusion
|  | LightingDemonstrationEquipInLightingEducationFacilities | LightingDemonstrationEquipInLightingEducationFacilities |  | NonRegulatedExclusion | [6 empty] | 90.1 2007 Sec 9.2.2.3
|  | LightingEquipmentForSale | LightingEquipmentForSale |  | NonRegulatedExclusion | [6 empty] | 90.1 2007 Sec 9.2.2.3
|  | ManufacturerInstalledInFreezerVendingFoodPrepScientificOrIndEquip | ManufacturerInstalledInFreezerVendingFoodPrepScientificOrIndEquip |  | NonRegulatedExclusion | [6 empty] | 90.1 2007 Sec 9.2.2.3
|  | PlantGrowthOrMaintWithMultiLevelAstroTimer | PlantGrowthOrMaintWithMultiLevelAstroTimer |  | NonRegulatedExclusion
|  | SignageLighting | SignageLighting |  | NonRegulatedExclusion
|  | SmallAgriculturalBuilding | SmallAgriculturalBuilding |  | NonRegulatedExclusion
|  | SmallNonresidentialParkingGarage | SmallNonresidentialParkingGarage |  | NonRegulatedExclusion
|  | SmallRefrigeratedCases | SmallRefrigeratedCases |  | NonRegulatedExclusion
|  | SmallUnconditionedAgriculturalBuilding | SmallUnconditionedAgriculturalBuilding |  | NonRegulatedExclusion
|  | TemporaryExhibitSeparatelySwitchedInCivicTransConvOrHotel | TemporaryExhibitSeparatelySwitchedInCivicTransConvOrHotel |  | NonRegulatedExclusion
|  | TemporaryLightingSystems | TemporaryLightingSystems |  | NonRegulatedExclusion
|  | ThemeParksThemeAndSpecialEffects | ThemeParksThemeAndSpecialEffects |  | NonRegulatedExclusion
Open
|  | NonSwinging | NonSwinging |  | Open
|  | Swinging | Swinging |  | Open |  | An attribute of a door and defines how the door opens. Includes all operable opaque panels with hinges on one side and opaque revolving doors
OperableWindowConfiguration
|  | CasementAwning | CasementAwning |  | OperableWindowConfiguration
|  | Sliding | Sliding |  | OperableWindowConfiguration
OverhangTransmittanceOption
|  | Constant | Constant | Constant | OverhangTransmittanceOption
|  | Scheduled | Scheduled | Scheduled | OverhangTransmittanceOption
PermitScope
|  | PermitNonresidentialAll | PermitNonresidentialAll |  | PermitScope |  | Permit scope for nonresidential envelope, lighting and mechanical
|  | PermitNonresidentialEnvelope | PermitNonresidentialEnvelope |  | PermitScope |  | Permit scope for nonresidential envelope only
|  | PermitNonresidentialEnvelopeLighting | PermitNonresidentialEnvelopeLighting |  | PermitScope |  | Permit scope for nonresidential envelope and lighting
|  | PermitNonresidentialEnvelopeMechanical | PermitNonresidentialEnvelopeMechanical |  | PermitScope |  | Permit scope for nonresidential envelope and mechanical
|  | PermitNonresidentialLighting | PermitNonresidentialLighting |  | PermitScope |  | Permit scope for nonresidential lighting only
|  | PermitNonresidentialLightingMechanical | PermitNonresidentialLightingMechanical |  | PermitScope |  | Permit scope for nonresidential lighting and mechanical
|  | PermitNonresidentialMechanical | PermitNonresidentialMechanical |  | PermitScope |  | Permit scope for nonresidential mechanical only
SkylightCurb
|  | CurbMounted | CurbMounted |  | SkylightCurb
|  | DeckMounted | DeckMounted |  | SkylightCurb
SkylightGlazing
|  | Glass | Glass |  | SkylightGlazing
|  | Plastic | Plastic |  | SkylightGlazing
SkylightRequirementException
|  | Auditorium | Auditorium |  | SkylightRequirementException
|  | Church | Church |  | SkylightRequirementException
|  | ExistingWalls | ExistingWalls |  | SkylightRequirementException
|  | FutureCeilings | FutureCeilings |  | SkylightRequirementException
|  | FutureWalls | FutureWalls |  | SkylightRequirementException
|  | MovieTheater | MovieTheater |  | SkylightRequirementException
|  | Museum | Museum |  | SkylightRequirementException
|  | RefrigeratedWarehouse | RefrigeratedWarehouse |  | SkylightRequirementException
SlabInsulationOrientation
|  | 12inHorizontal | 12inHorizontal |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | 12inVertical | 12inVertical |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | 24inHorizontal | 24inHorizontal |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | 24inVertical | 24inVertical |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | 36inHorizontal | 36inHorizontal |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | 36inVertical | 36inVertical |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | 48inHorizontal | 48inHorizontal |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | 48inVertical | 48inVertical |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | FullyInsulatedSlab | FullyInsulatedSlab |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
|  | None | None |  | SlabInsulationOrientation | [6 empty] | 2013 NACM-5.5.9
SlabInsulationThermalResistance
|  | R0 | R0 |  | SlabInsulationThermalResistance
|  | R10 | R10 |  | SlabInsulationThermalResistance
|  | R15 | R15 |  | SlabInsulationThermalResistance
|  | R20 | R20 |  | SlabInsulationThermalResistance
|  | R25 | R25 |  | SlabInsulationThermalResistance
|  | R30 | R30 |  | SlabInsulationThermalResistance
|  | R35 | R35 |  | SlabInsulationThermalResistance
|  | R40 | R40 |  | SlabInsulationThermalResistance
|  | R45 | R45 |  | SlabInsulationThermalResistance
|  | R5 | R5 |  | SlabInsulationThermalResistance
|  | R50 | R50 |  | SlabInsulationThermalResistance
|  | R55 | R55 |  | SlabInsulationThermalResistance
|  | R7_5 | R7_5 |  | SlabInsulationThermalResistance
SpecificationMethod
|  | Date | Date |  | SpecificationMethod
|  | First | First |  | SpecificationMethod
|  | Fourth | Fourth |  | SpecificationMethod
|  | Last | Last |  | SpecificationMethod
|  | Second | Second |  | SpecificationMethod
|  | Third | Third |  | SpecificationMethod
Status
|  | Altered | Altered |  | Status | [6 empty] | CF1R-PRF EAA
|  | Existing | Existing |  | Status | [6 empty] | CF1R-PRF EAA
|  | Future | Future |  | Status
|  | New | New |  | Status | [6 empty] | CF1R-PRF EAA
Type
|  | Cooling | Cooling |  | Type
|  | Fraction | Fraction |  | Type
|  | Heating | Heating |  | Type
|  | InsulatedSingleLayerSectionalMetal | InsulatedSingleLayerSectionalMetal |  | Type
|  | InsulatedSwingingMetal | InsulatedSwingingMetal |  | Type
|  | OnOff | OnOff |  | Type
|  | Temperature | Temperature |  | Type
|  | ThrmlEngyStorMode | ThrmlEngyStorMode |  | Type
|  | UninsulatedDoubleLayerMetal | UninsulatedDoubleLayerMetal |  | Type
|  | UninsulatedSingleLayerMetal | UninsulatedSingleLayerMetal |  | Type
|  | UninsulatedSingleLayerRollupMetal | UninsulatedSingleLayerRollupMetal |  | Type
|  | WoodOther | WoodOther |  | Type
|  | WoodThick | WoodThick |  | Type
WeatherStation
|  | ALTURAS725958 | ALTURAS725958 | ALTURAS_725958 | WeatherStation
|  | ARCATA725945 | ARCATA725945 | ARCATA_725945 | WeatherStation
|  | BAKERSFIELD723840 | BAKERSFIELD723840 | BAKERSFIELD_723840 | WeatherStation
|  | BISHOP724800 | BISHOP724800 | BISHOP_724800 | WeatherStation
|  | BLUE_CANYON725845 | BLUE_CANYON725845 | BLUE-CANYON_725845 | WeatherStation
|  | BLYTHE_RIVERSIDE_CO747188 | BLYTHE_RIVERSIDE_CO747188 | BLYTHE-RIVERSIDE-CO_747188 | WeatherStation
|  | BURBANK_GLENDALE722880 | BURBANK_GLENDALE722880 | BURBANK-GLENDALE_722880 | WeatherStation
|  | CAMARILLO723926 | BISHOP724800 | CAMARILLO_723926 | WeatherStation
|  | CAMP_PENDLETON722926 | CAMP_PENDLETON722926 | CAMP-PENDLETON_722926 | WeatherStation
|  | CARLSBAD722927 | CARLSBAD722927 | CARLSBAD_722927 | WeatherStation
|  | CHINA_LAKE746120 | CHINA_LAKE746120 | CHINA-LAKE_746120 | WeatherStation
|  | CHINO722899 | CHINO722899 | CHINO_722899 | WeatherStation
|  | CONCORD724936 | CONCORD724936 | CONCORD_724936 | WeatherStation
|  | CRESCENT_CITY725946 | CRESCENT_CITY725946 | CRESCENT-CITY_725946 | WeatherStation
|  | DAGGETT_BARSTOW723815 | DAGGETT_BARSTOW723815 | DAGGETT-BARSTOW_723815 | WeatherStation
|  | EDWARDS_AFB723810 | DAGGETT_BARSTOW723815 | EDWARDS-AFB_723810 | WeatherStation
|  | EL_CENTRO722810 | EL_CENTRO722810 | EL-CENTRO_722810 | WeatherStation
|  | EUREKA725940 | EUREKA725940 | EUREKA_725940 | WeatherStation
|  | FAIRFLD_TRAVIS_AFB745160 | FAIRFLD_TRAVIS_AFB745160 | FAIRFLD-TRAVIS-AFB_745160 | WeatherStation
|  | FRESNO723890 | FRESNO723890 | FRESNO_723890 | WeatherStation
|  | FULLERTON722976 | FULLERTON722976 | FULLERTON_722976 | WeatherStation
|  | HAWTHORNE_NORTHROP_FLD722956 | HAWTHORNE_NORTHROP_FLD722956 | HAWTHORNE-NORTHROP-FLD_722956 | WeatherStation
|  | HAYWARD724935 | HAYWARD724935 | HAYWARD_724935 | WeatherStation
|  | IMPERIAL_BEACH722909 | IMPERIAL_BEACH722909 | IMPERIAL-BEACH_722909 | WeatherStation
|  | IMPERIAL747185 | IMPERIAL747185 | IMPERIAL_747185 | WeatherStation
|  | INYOKERN723826 | INYOKERN723826 | INYOKERN_723826 | WeatherStation
|  | LANCASTER723816 | LANCASTER723816 | LANCASTER_723816 | WeatherStation
|  | LEMOORE747020 | LEMOORE747020 | LEMOORE_747020 | WeatherStation
|  | LIVERMORE724927 | LIVERMORE724927 | LIVERMORE_724927 | WeatherStation
|  | LOMPOC722895 | LOMPOC722895 | LOMPOC_722895 | WeatherStation
|  | LONG_BEACH722970 | LONG_BEACH722970 | LONG-BEACH_722970 | WeatherStation
|  | LOS_ALAMITOS722975 | LOS_ALAMITOS722975 | LOS-ALAMITOS_722975 | WeatherStation
|  | LOS_ANGELES_DOWNTOWN722874 | LOS_ANGELES_DOWNTOWN722874 | LOS-ANGELES-DOWNTOWN_722874 | WeatherStation
|  | LOS_ANGELES_INTL722950 | LOS_ANGELES_INTL722950 | LOS-ANGELES-INTL_722950 | WeatherStation
|  | MARYSVILLE_BEALE_AFB724837 | MARYSVILLE_BEALE_AFB724837 | MARYSVILLE_BEALE_AFB724837 | WeatherStation
|  | MERCED724815 | MERCED724815 | MERCED_724815 | WeatherStation
|  | MODESTO724926 | MODESTO724926 | MODESTO_724926 | WeatherStation
|  | MOJAVE722953 | MOJAVE722953 | MOJAVE_722953 | WeatherStation
|  | MONTAGUE_SISKIYOU_CO725955 | MONTAGUE_SISKIYOU_CO725955 | MONTAGUE-SISKIYOU-CO_725955 | WeatherStation
|  | MONTEREY724915 | MONTEREY724915 | MONTEREY_724915 | WeatherStation
|  | MOUNT_SHASTA725957 | MONTEREY724915 | MOUNT-SHASTA_725957 | WeatherStation
|  | NAPA_CO724955 | NAPA_CO724955 | NAPA-CO_724955 | WeatherStation
|  | NEEDLES723805 | NEEDLES723805 | NEEDLES_723805 | WeatherStation
|  | OAKLAND724930 | OAKLAND724930 | OAKLAND_724930 | WeatherStation
|  | OXNARD723927 | OXNARD723927 | OXNARD_723927 | WeatherStation
|  | PALM_SPRINGS_INTL722868 | PALM_SPRINGS_INTL722868 | PALM-SPRINGS-INTL_722868 | WeatherStation
|  | PALM_SPRINGS_THERMAL747187 | PALM_SPRINGS_INTL722868 | PALM-SPRINGS-THERMAL_747187 | WeatherStation
|  | PALMDALE723820 | PALMDALE723820 | PALMDALE_723820 | WeatherStation
|  | PALO_ALTO724937 | PALO_ALTO724937 | PALO-ALTO_724937 | WeatherStation
|  | PASO_ROBLES723965 | PASO_ROBLES723965 | PASO-ROBLES_723965 | WeatherStation
|  | POINT_MUGU723910 | POINT_MUGU723910 | POINT-MUGU_723910 | WeatherStation
|  | PORTERVILLE723895 | PORTERVILLE723895 | PORTERVILLE_723895 | WeatherStation
|  | RED_BLUFF725910 | RED_BLUFF725910 | RED-BLUFF_725910 | WeatherStation
|  | REDDING725920 | REDDING725920 | REDDING_725920 | WeatherStation
|  | RIVERSIDE_MARCH_AFB722860 | RIVERSIDE_MARCH_AFB722860 | RIVERSIDE-MARCH-AFB_722860 | WeatherStation
|  | RIVERSIDE722869 | RIVERSIDE722869 | RIVERSIDE_722869 | WeatherStation
|  | SACRAMENTO_EXECUTIVE724830 | SACRAMENTO_EXECUTIVE724830 | SACRAMENTO-EXECUTIVE_724830 | WeatherStation
|  | SACRAMENTO_METRO724839 | SACRAMENTO_METRO724839 | SACRAMENTO-METRO_724839 | WeatherStation
|  | SALINAS724917 | SALINAS724917 | SALINAS_724917 | WeatherStation
|  | SAN_CARLOS724938 | SAN_CARLOS724938 | SAN-CARLOS_724938 | WeatherStation
|  | SAN_CLEMENTE_IS722925 | SAN_CLEMENTE_IS722925 | SAN-CLEMENTE-IS_722925 | WeatherStation
|  | SAN_DIEGO_GILLESPIE722907 | SAN_DIEGO_GILLESPIE722907 | SAN-DIEGO-GILLESPIE_722907 | WeatherStation
|  | SAN_DIEGO_LINDBERGH722900 | SAN_DIEGO_LINDBERGH722900 | SAN-DIEGO-LINDBERGH_722900 | WeatherStation
|  | SAN_DIEGO_MONTGOMER722903 | SAN_DIEGO_MONTGOMER722903 | SAN-DIEGO-MONTGOMER_722903 | WeatherStation
|  | SAN_DIEGO_NORTH_IS722906 | SAN_DIEGO_NORTH_IS722906 | SAN-DIEGO-NORTH-IS_722906 | WeatherStation
|  | SAN_FRANCISCO_INTL724940 | SAN_FRANCISCO_INTL724940 | SAN-FRANCISCO-INTL_724940 | WeatherStation
|  | SAN_JOSE_INTL724945 | SAN_JOSE_INTL724945 | SAN-JOSE-INTL_724945 | WeatherStation
|  | SAN_JOSE_REID724946 | SAN_JOSE_REID724946 | SAN-JOSE-REID_724946 | WeatherStation
|  | SAN_LUIS_CO722897 | SAN_LUIS_CO722897 | SAN-LUIS-CO_722897 | WeatherStation
|  | SAN_NICHOLAS_IS722910 | SAN_NICHOLAS_IS722910 | SAN-NICHOLAS-IS_722910 | WeatherStation
|  | SANDBERG723830 | SANDBERG723830 | SANDBERG_723830 | WeatherStation
|  | SANTA_ANA722977 | SANTA_ANA722977 | SANTA-ANA_722977 | WeatherStation
|  | SANTA_BARBARA723925 | SANTA_BARBARA723925 | SANTA-BARBARA_723925 | WeatherStation
|  | SANTA_MARIA723940 | SANTA_MARIA723940 | SANTA-MARIA_723940 | WeatherStation
|  | SANTA_MONICA722885 | SANTA_MONICA722885 | SANTA-MONICA_722885 | WeatherStation
|  | SANTA_ROSA724957 | SANTA_ROSA724957 | SANTA-ROSA_724957 | WeatherStation
|  | SOUTH_LAKE_TAHOE725847 | SOUTH_LAKE_TAHOE725847 | SOUTH-LAKE-TAHOE_725847 | WeatherStation
|  | STOCKTON724920 | STOCKTON724920 | STOCKTON_724920 | WeatherStation
|  | TORRANCE722955 | TORRANCE722955 | TORRANCE_722955 | WeatherStation
|  | TRUCKEE_TAHOE725846 | TRUCKEE_TAHOE725846 | TRUCKEE-TAHOE_725846 | WeatherStation
|  | TWENTYNINE_PALMS690150 | TWENTYNINE_PALMS690150 | TWENTYNINE-PALMS_690150 | WeatherStation
|  | UKIAH725905 | UKIAH725905 | UKIAH_725905 | WeatherStation
|  | VAN_NUYS722886 | VAN_NUYS722886 | VAN-NUYS_722886 | WeatherStation
|  | VANDENBERG_AFB723930 | VANDENBERG_AFB723930 | VANDENBERG-AFB_723930 | WeatherStation
|  | VISALIA723896 | VISALIA723896 | VISALIA_723896 | WeatherStation
|  | YUBA_CO724838 | YUBA_CO724838 | YUBA-CO_724838 | WeatherStation
WindowDivider
|  | DividerBetwnPanesGreaterThanOrEqualTo7_16in | DividerBetwnPanesGreaterThanOrEqualTo7_16in |  | WindowDivider
|  | DividerBetwnPanesLessThan7_16in | DividerBetwnPanesLessThan7_16in |  | WindowDivider
|  | NoDivider | NoDivider |  | WindowDivider
|  | NotApplicable | NotApplicable | - n/a - | WindowDivider
|  | TrueDividedLite | TrueDividedLite |  | WindowDivider
(no property)
R6_DeckInsul
|  | Skylight | Skylight
AirLayers
CodeItem
|  | AirCavityWallRoofCeiling4InPlus |  | Air - Cavity - Wall Roof Ceiling - 4 in. or more | CodeItem |  |  |  |  | AirLayers
|  | AirCeiling0_5In |  | Air - Ceiling - 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirCeiling0_75In |  | Air - Ceiling - 3/4 in. | CodeItem |  |  |  |  | AirLayers
|  | AirCeiling1_5In |  | Air - Ceiling - 1 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirCeiling3_5In |  | Air - Ceiling - 3 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirFloor0_5In |  | Air - Floor - 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirFloor0_75In |  | Air - Floor - 3/4 in. | CodeItem |  |  |  |  | AirLayers
|  | AirFloor1_5In |  | Air - Floor - 1 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirFloor3_5In |  | Air - Floor - 3 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirMetalWallFraming16Or24InOC |  | Air - Metal Wall Framing - 16 or 24 in. OC | CodeItem |  |  |  |  | AirLayers
|  | AirRoof0_5In |  | Air - Roof - 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirRoof0_75In |  | Air - Roof - 3/4 in. | CodeItem |  |  |  |  | AirLayers
|  | AirRoof1_5In |  | Air - Roof - 1 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirRoof3_5In |  | Air - Roof - 3 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirWall0_5In |  | Air - Wall - 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirWall0_75In |  | Air - Wall - 3/4 in. | CodeItem |  |  |  |  | AirLayers
|  | AirWall1_5In |  | Air - Wall - 1 1/2 in. | CodeItem |  |  |  |  | AirLayers
|  | AirWall3_5In |  | Air - Wall - 3 1/2 in. | CodeItem |  |  |  |  | AirLayers
CodeCategory
BuildingBoardAndSiding |  |  | BoardAndSiding | Bldg Board and Siding | CodeCategory
CodeItem
|  | FiberboardSheathing0_5In |  | Fiberboard sheathing - 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | FiberCementBoard63LbPerFt3Thickness0_33In |  | Fiber cement board - 63 lb/ft3 - 1/3 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | FiberCementBoard88LbPerFt3Thickness0_33In |  | Fiber cement board - 88 lb/ft3 - 1/3 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | FiberCementBoard88LbPerFt3Thickness0_5In |  | Fiber cement board - 88 lb/ft3 - 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | GypsumBoard0_375In |  | Gypsum Board - 3/8 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | GypsumBoard0_5In |  | Gypsum Board - 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | GypsumBoard0_625In |  | Gypsum Board - 5/8 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | GypsumBoard0_75In |  | Gypsum Board - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | HardBoard0_75In |  | Hard Board - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | HardBoardHDF50LbPerFt3Thickness0_375In |  | Hardboard - HDF - 50 lb/ft3 - 3/8in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | HardBoardHDF50LbPerFt3Thickness0_5In |  | Hardboard - HDF - 50 lb/ft3 - 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | HardBoardHDF50LbPerFt3Thickness0_625In |  | Hardboard - HDF - 50 lb/ft3 - 5/8in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | HardBoardHDF50LbPerFt3Thickness0_75In |  | Hardboard - HDF - 50 lb/ft3 - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | HBPartBoard0_75In |  | HB Part. Brd - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | MetalDeck0_0625In |  | Metal Deck - 1/16 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | MetalSiding0_0625In |  | Metal Siding - 1/16 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | OrientedStrandBoard0_5In |  | OSB - Oriented Strand Board - 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | OrientedStrandBoard0_625In |  | OSB - Oriented Strand Board - 5/8 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | OrientedStrandBoard0_75In |  | OSB - Oriented Strand Board - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | Plywood0_25In |  | Plywood - 1/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | Plywood0_375In |  | Plywood - 3/8 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | Plywood0_5In |  | Plywood - 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | Plywood0_625In |  | Plywood - 5/8 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | Plywood0_75In |  | Plywood - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | Plywood1_25In |  | Plywood - 1 1/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | Plywood1_5In |  | Plywood - 1 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | Plywood1In |  | Plywood - 1 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | ShinglesAsbestosCementLapped0_25In |  | Shingles - Asbestos cement - lapped - 1/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | ShinglesAsphaltRollSiding0_25In |  | Shingles - Asphalt roll siding - 1/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | ShinglesWood16In7_5InExposure0_5In |  | Shingles - Wood - 16 in. - 7 1/2 in. exposure - 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | ShinglesWoodInsulatedBackerBoardSiding0_3125In |  | Shingles - Wood - plus insulated backer board Siding - 5/16 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | SidingAsphaltInsulating0_5InBed0_5In |  | Siding - Asphalt insulating siding - 1/2 in. bed - 1/2 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | SidingWoodBevel10_0InLapped0_75In |  | Siding - Wood - bevel - 10 in. - lapped - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | StuccoSyntheticEIFS_Finish1In |  | Synthetic Stucco - EIFS finish - 1 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | WoodShingles0_75In |  | Wood shingles - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
|  | WoodShinglesPlainAndPlasticFilmFaced0_75In |  | Wood shingles - plain and plastic film faced - 3/4 in. | CodeItem |  |  |  |  | BuildingBoardAndSiding
CodeCategory
BuildingMembrane |  |  | Membrane | Building Membrane | CodeCategory
CodeItem
|  | BuildingPaper0_0625In |  | Building Paper - 1/16 in. | CodeItem |  |  |  |  | BuildingMembrane
|  | RoofingFelt0_125In |  | Roofing felt - 1/8 in. | CodeItem |  |  |  |  | BuildingMembrane
|  | VaporPermeableFelt0_125In |  | Vapor permeable felt - 1/8 in. | CodeItem |  |  |  |  | BuildingMembrane
|  | VaporSeal2LayerMopped15LbFelt0_25In |  | Vapor seal - 2 layers of mopped 15 lb felt - 1/4 in. | CodeItem |  |  |  |  | BuildingMembrane
|  | VaporSealPlasticFilm0_0625In |  | Vapor seal - plastic film - 1/16 in. | CodeItem |  |  |  |  | BuildingMembrane
(no property)
ConcreteMaterial
CodeItem
|  | Concrete100LbPerFt3Thickness10In |  | Concrete - 100 lb/ft3 - 10 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete100LbPerFt3Thickness12In |  | Concrete - 100 lb/ft3 - 12 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete100LbPerFt3Thickness2In |  | Concrete - 100 lb/ft3 - 2 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete100LbPerFt3Thickness4In |  | Concrete - 100 lb/ft3 - 4 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete100LbPerFt3Thickness6In |  | Concrete - 100 lb/ft3 - 6 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete100LbPerFt3Thickness8In |  | Concrete - 100 lb/ft3 - 8 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete140LbPerFt3Thickness10In |  | Concrete - 140 lb/ft3 - 10 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete140LbPerFt3Thickness12In |  | Concrete - 140 lb/ft3 - 12 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete140LbPerFt3Thickness2In |  | Concrete - 140 lb/ft3 - 2 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete140LbPerFt3Thickness4In |  | Concrete - 140 lb/ft3 - 4 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete140LbPerFt3Thickness6In |  | Concrete - 140 lb/ft3 - 6 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete140LbPerFt3Thickness8In |  | Concrete - 140 lb/ft3 - 8 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete80LbPerFt3Thickness10In |  | Concrete - 80 lb/ft3 - 10 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete80LbPerFt3Thickness12In |  | Concrete - 80 lb/ft3 - 12 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete80LbPerFt3Thickness2In |  | Concrete - 80 lb/ft3 - 2 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete80LbPerFt3Thickness4In |  | Concrete - 80 lb/ft3 - 4 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete80LbPerFt3Thickness6In |  | Concrete - 80 lb/ft3 - 6 in. | CodeItem |  |  |  |  | ConcreteMaterial
|  | Concrete80LbPerFt3Thickness8In |  | Concrete - 80 lb/ft3 - 8 in. | CodeItem |  |  |  |  | ConcreteMaterial
CodeCategory
ConcreteSandwichPanel |  |  | ConcreteSandwichPanel | Concrete Sandwich Panel | CodeCategory
CodeItem
|  | ConcreteSandwichPanel100PercentInsulationNoSteelInsulation1_5In |  | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationNoSteelInsulation2In |  | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationNoSteelInsulation3In |  | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 3 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationNoSteelInsulation4In |  | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 4 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationNoSteelInsulation6In |  | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 6 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationSteelInsulation1_5In |  | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationSteelInsulation2In |  | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationSteelInsulation3In |  | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 3 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationSteelInsulation4In |  | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 4 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel100PercentInsulationSteelInsulation6In |  | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 6 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationNoSteelInsulation1_5In |  | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationNoSteelInsulation2In |  | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationNoSteelInsulation3In |  | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 3 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationNoSteelInsulation4In |  | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 4 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationNoSteelInsulation6In |  | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 6 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationSteelInsulation1_5In |  | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationSteelInsulation2In |  | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationSteelInsulation3In |  | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 3 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationSteelInsulation4In |  | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 4 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel80PercentInsulationSteelInsulation6In |  | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 6 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationNoSteelInsulation1_5In |  | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationNoSteelInsulation2In |  | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationNoSteelInsulation3In |  | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 3 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationNoSteelInsulation4In |  | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 4 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationNoSteelInsulation6In |  | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 6 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationSteelInsulation1_5In |  | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationSteelInsulation2In |  | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 2 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationSteelInsulation3In |  | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 3 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationSteelInsulation4In |  | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 4 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
|  | ConcreteSandwichPanel90PercentInsulationSteelInsulation6In |  | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 6 in. | CodeItem |  |  |  |  | ConcreteSandwichPanel
CodeCategory
FinishMaterials |  |  | FinishMaterials | Finish Materials | CodeCategory
CodeItem
|  | AcousticTile0_375In |  | Acoustic Tile - 3/8 in. | CodeItem |  |  |  |  | FinishMaterials
|  | AcousticTile0_5In |  | Acoustic Tile - 1/2 in. | CodeItem |  |  |  |  | FinishMaterials
|  | AcousticTile0_75In |  | Acoustic Tile - 3/4 in. | CodeItem |  |  |  |  | FinishMaterials
|  | Carpet0_75In |  | Carpet - 3/4 in. | CodeItem |  |  |  |  | FinishMaterials
|  | LinoleumCorkTile0_25In |  | Linoleum/cork tile - 1/4 in. | CodeItem |  |  |  |  | FinishMaterials
|  | RubberTile1In |  | Rubber Tile - 1 in. | CodeItem |  |  |  |  | FinishMaterials
|  | SlateOrTile0_5In |  | Slate or tile - 1/2 in. | CodeItem |  |  |  |  | FinishMaterials
|  | Terrazzo1In |  | Terrazzo - 1 in. | CodeItem |  |  |  |  | FinishMaterials
(no property)
ICF_Wall
CodeItem
|  | ICF1_5InPolyurethaneEachSideConcrete6In |  | Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF1_5InPolyurethaneEachSideConcrete8In |  | Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF2_5InEPSEachSideConcrete6In |  | Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF2_5InEPSEachSideConcrete8In |  | Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF2InEPSEachSideConcrete6In |  | Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF2InEPSEachSideConcrete8In |  | Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF2InPolyurethaneEachSideConcrete6In |  | Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF2InPolyurethaneEachSideConcrete8In |  | Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF2InXPSEachSideConcrete6In |  | Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF2InXPSEachSideConcrete8In |  | Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF3InEPSEachSideConcrete6In |  | Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF3InEPSEachSideConcrete8In |  | Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF3InXPSEachSideConcrete6In |  | Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF3InXPSEachSideConcrete8In |  | Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF4_5InPolyurethaneEachSideConcrete6In |  | Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF4_5InPolyurethaneEachSideConcrete8In |  | Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF4InEPSEachSideConcrete6In |  | Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF4InEPSEachSideConcrete8In |  | Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF4InXPSEachSideConcrete6In |  | Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 6 in. | CodeItem |  |  |  |  | ICF_Wall
|  | ICF4InXPSEachSideConcrete8In |  | Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 8 in. | CodeItem |  |  |  |  | ICF_Wall
CodeCategory
InsulationBatt |  |  | InsulationBatt | Insulation Batt | CodeCategory
CodeItem
|  | GlassFiberBatt10In_ R30_CEC_Default |  | Glass fiber batt - 10 in. R30 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt12In_ R38_CEC_Default |  | Glass fiber batt - 12 in. R38 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt3_5In_ R11_CEC_Default |  | Glass fiber batt - 3 1/2 in. R11 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt3_5In_ R13_CEC_Default |  | Glass fiber batt - 3 1/2 in. R13 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt3_5In_ R15_CEC_Default |  | Glass fiber batt - 3 1/2 in. R15 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt4_5In |  | Glass fiber batt - 4 1/2 in. | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt4In |  | Glass fiber batt - 4 in. | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt5_5In_ R19_CEC_Default |  | Glass fiber batt - 5 1/2 in. R19 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt5_5In_ R21_CEC_Default |  | Glass fiber batt - 5 1/2 in. R21 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt5In |  | Glass fiber batt - 5 in. | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt6_5In |  | Glass fiber batt - 6 1/2 in. | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt6In |  | Glass fiber batt - 6 in. | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt7_25In_ R25_CEC_Default |  | Glass fiber batt - 7 1/4 in. R25 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt7_25In_ R30_CEC_Default |  | Glass fiber batt - 7 1/4 in. R30 (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
|  | GlassFiberBatt8_25In_ R30_CEC_Default |  | Glass fiber batt - 8 1/4 in. R30C (CEC Default) | CodeItem |  |  |  |  | InsulationBatt
CodeCategory
InsulationBoard |  |  | InsulationBoard | Insulation Board | CodeCategory
CodeItem
|  | CellularPolyisocyanurate0_125In_R0_7 |  | Cellular polyisocyanurate (unfaced) - 1/8 in. R0.7 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate0_25In_R1_5 |  | Cellular polyisocyanurate (unfaced) - 1/4 in. R1.5 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate0_5In_R2_9 |  | Cellular polyisocyanurate (unfaced) - 1/2 in. R2.9 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate1_5In_R8_8 |  | Cellular polyisocyanurate (unfaced) - 1 1/2 in. R8.8 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate1In_R5_9 |  | Cellular polyisocyanurate (unfaced) - 1 in. R5.9 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate2_5In_R15 |  | Cellular polyisocyanurate (unfaced) - 2 1/2 in. R15 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate2In_R12 |  | Cellular polyisocyanurate (unfaced) - 2 in. R12 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate3_5In_R21 |  | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate3In_R18 |  | Cellular polyisocyanurate (unfaced) - 3 in. R18 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate4_5In_R26 |  | Cellular polyisocyanurate (unfaced) - 4 1/2 in. R26 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate4In_R23 |  | Cellular polyisocyanurate (unfaced) - 4 in. R23 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate5_5In_R32 |  | Cellular polyisocyanurate (unfaced) - 5 1/2 in. R32 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate5In_R29 |  | Cellular polyisocyanurate (unfaced) - 5 in. R29 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate6_5In_R38 |  | Cellular polyisocyanurate (unfaced) - 6 1/2 in. R38 | CodeItem |  |  |  |  | InsulationBoard
|  | CellularPolyisocyanurate6In_R35 |  | Cellular polyisocyanurate (unfaced) - 6 in. R35 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR0_01 |  | Compliance Insulation R0.01 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR0_02 |  | Compliance Insulation R0.02 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR0_10 |  | Compliance Insulation R0.10 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR0_20 |  | Compliance Insulation R0.20 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR0_50 |  | Compliance Insulation R0.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR1_00 |  | Compliance Insulation R1.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR1_35 |  | Compliance Insulation R1.35 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR1_41 |  | Compliance Insulation R1.41 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR1_54 |  | Compliance Insulation R1.54 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR10_00 |  | Compliance Insulation R10.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR10_06 |  | Compliance Insulation R10.06 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR11_00 |  | Compliance Insulation R11.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR11_70 |  | Compliance Insulation R11.70 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR12_00 |  | Compliance Insulation R12.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR12_50 |  | Compliance Insulation R12.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR12_55 |  | Compliance Insulation R12.55 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR12_69 |  | Compliance Insulation R12.69 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR13_00 |  | Compliance Insulation R13.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR13_50 |  | Compliance Insulation R13.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR13_99 |  | Compliance Insulation R13.99 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR14_00 |  | Compliance Insulation R14.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR14_14 |  | Compliance Insulation R14.14 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR14_32 |  | Compliance Insulation R14.32 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR14_60 |  | Compliance Insulation R14.60 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR15_00 |  | Compliance Insulation R15.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR15_54 |  | Compliance Insulation R15.54 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR16_00 |  | Compliance Insulation R16.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR16_20 |  | Compliance Insulation R16.20 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR16_34 |  | Compliance Insulation R16.34 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR16_58 |  | Compliance Insulation R16.58 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR16_69 |  | Compliance Insulation R16.69 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR17_00 |  | Compliance Insulation R17.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR17_67 |  | Compliance Insulation R17.67 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR18_00 |  | Compliance Insulation R18.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR19_00 |  | Compliance Insulation R19.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR19_63 |  | Compliance Insulation R19.63 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR2_00 |  | Compliance Insulation R2.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR2_15 |  | Compliance Insulation R2.15 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR2_19 |  | Compliance Insulation R2.19 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR2_85 |  | Compliance Insulation R2.85 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR2_89 |  | Compliance Insulation R2.89 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR20_00 |  | Compliance Insulation R20.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR20_05 |  | Compliance Insulation R20.05 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR21_00 |  | Compliance Insulation R21.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR21_18 |  | Compliance Insulation R21.18 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR21_39 |  | Compliance Insulation R21.39 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR21_60 |  | Compliance Insulation R21.60 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR22_00 |  | Compliance Insulation R22.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR22_48 |  | Compliance Insulation R22.48 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR23_00 |  | Compliance Insulation R23.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR23_70 |  | Compliance Insulation R23.70 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR24_00 |  | Compliance Insulation R24.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR24_80 |  | Compliance Insulation R24.80 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR24_86 |  | Compliance Insulation R24.86 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR25_00 |  | Compliance Insulation R25.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR25_16 |  | Compliance Insulation R25.16 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR26_00 |  | Compliance Insulation R26.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR27_00 |  | Compliance Insulation R27.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR28_00 |  | Compliance Insulation R28.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR28_12 |  | Compliance Insulation R28.12 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR28_63 |  | Compliance Insulation R28.63 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR29_00 |  | Compliance Insulation R29.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR3_00 |  | Compliance Insulation R3.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR3_63 |  | Compliance Insulation R3.63 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR3_70 |  | Compliance Insulation R3.70 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR3_80 |  | Compliance Insulation R3.80 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR30_00 |  | Compliance Insulation R30.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR31_00 |  | Compliance Insulation R31.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR32_00 |  | Compliance Insulation R32.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR33_00 |  | Compliance Insulation R33.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR34_00 |  | Compliance Insulation R34.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR34_93 |  | Compliance Insulation R34.93 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR35_00 |  | Compliance Insulation R35.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR36_00 |  | Compliance Insulation R36.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR37_00 |  | Compliance Insulation R37.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR38_00 |  | Compliance Insulation R38.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR4_00 |  | Compliance Insulation R4.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR5_00 |  | Compliance Insulation R5.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR5_60 |  | Compliance Insulation R5.60 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR6_00 |  | Compliance Insulation R6.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR6_32 |  | Compliance Insulation R6.32 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR6_46 |  | Compliance Insulation R6.46 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR7_00 |  | Compliance Insulation R7.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR7_10 |  | Compliance Insulation R7.10 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR7_18 |  | Compliance Insulation R7.18 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR7_39 |  | Compliance Insulation R7.39 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR7_50 |  | Compliance Insulation R7.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR7_60 |  | Compliance Insulation R7.60 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR8_00 |  | Compliance Insulation R8.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR8_07 |  | Compliance Insulation R8.07 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR9_00 |  | Compliance Insulation R9.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR9_40 |  | Compliance Insulation R9.40 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR9_80 |  | Compliance Insulation R9.80 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR9_83 |  | Compliance Insulation R9.83 | CodeItem |  |  |  |  | InsulationBoard
|  | ComplianceInsulationR9_94 |  | Compliance Insulation R9.94 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPerliteOrganicBonded0_75In_R2_1 |  | Expanded perlite - organic bonded - 3/4 in. R2.1 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPerliteOrganicBonded1_5In_R4_2 |  | Expanded perlite - organic bonded - 1 1/2 in. R4.2 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPerliteOrganicBonded1In_R2_8 |  | Expanded perlite - organic bonded - 1 in. R2.8 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPerliteOrganicBonded2In_R5_6 |  | Expanded perlite - organic bonded - 2 in. R5.6 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPerliteOrganicBonded3In_R8_3 |  | Expanded perlite - organic bonded - 3 in. R8.3 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPerliteOrganicBonded4In_R11 |  | Expanded perlite - organic bonded - 4 in. R11 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPerliteOrganicBonded6In_R17 |  | Expanded perlite - organic bonded - 6 in. R17 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene0_25In_R1 |  | Expanded Polystyrene - EPS - 1/4 in. R1 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene0_5In_R2_1 |  | Expanded Polystyrene - EPS - 1/2 in. R2.1 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene0_75In_R3_1 |  | Expanded Polystyrene - EPS - 3/4 in. R3.1 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene1_25In_R5_2 |  | Expanded Polystyrene - EPS - 1 1/4 in. R5.2 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene1_5In_R6_3 |  | Expanded Polystyrene - EPS - 1 1/2 in. R6.3 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene1_75In_R7_3 |  | Expanded Polystyrene - EPS - 1 3/4 in. R7.3 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene1_875In_R8 |  | Expanded Polystyrene - EPS - 1 7/8 in. R8.0 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene1_9375In_R8_1 |  | Expanded Polystyrene - EPS - 1 15/16 in. R8.1 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene1In_R4_2 |  | Expanded Polystyrene - EPS - 1 in. R4.2 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene2_4375In_R10 |  | Expanded Polystyrene - EPS - 2 7/16 in. R10 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene2_4In_R10 |  | Expanded Polystyrene - EPS - 2 2/5 in. R10 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene2In_R8_3 |  | Expanded Polystyrene - EPS - 2 in. R8.3 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene3_3333In_R14 |  | Expanded Polystyrene - EPS - 3 1/3 in. R14 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene3_4In_R14 |  | Expanded Polystyrene - EPS - 3 2/5 in. R14 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene3_5In_R15 |  | Expanded Polystyrene - EPS - 3 1/2 in. R15 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene3In_ R13 |  | Expanded Polystyrene - EPS - 3 in. R13 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene4_0625In_R17 |  | Expanded Polystyrene - EPS - 4 1/16 in. R17 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene4_7In_R20 |  | Expanded Polystyrene - EPS - 4 7/10 in. R20 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene5_4In_R22 |  | Expanded Polystyrene - EPS - 5 2/5 in. R22 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene5_95In_R25 |  | Expanded Polystyrene - EPS - 5 19/20 in. R25 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene6_1In_R25 |  | Expanded Polystyrene - EPS - 6 1/10 in. R25 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene6_875In_R29 |  | Expanded Polystyrene - EPS - 6 7/8 in. R29 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyrene8_6In_R35 |  | Expanded Polystyrene - EPS - 8 3/5 in. R35 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS0_25In_R1_25 |  | Extruded Polystyrene - XPS - 1/4 in. R1.25 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS0_5In_R2_50 |  | Extruded Polystyrene - XPS - 1/2 in. R2.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS0_75In_R3_75 |  | Extruded Polystyrene - XPS - 3/4 in. R3.75 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS1_25In_R6_25 |  | Extruded Polystyrene - XPS - 1 1/4 in. R6.25 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS1_5In_R7_50 |  | Extruded Polystyrene - XPS - 1 1/2 in. R7.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS1_75In_R8_75 |  | Extruded Polystyrene - XPS - 1 3/4 in. R8.75 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS1_875In_R9_37 |  | Extruded Polystyrene - XPS - 1 78 in. R9.37 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS1In_R5 |  | Extruded Polystyrene - XPS - 1 in. R5.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS2_5In_R12_50 |  | Extruded Polystyrene - XPS - 2 1/2 in. R12.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS2In_R10 |  | Extruded Polystyrene - XPS - 2 in. R10.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS3_5In_R17_50 |  | Extruded Polystyrene - XPS - 3 1/2 in. R17.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS3In_R15 |  | Extruded Polystyrene - XPS - 3 in. R15.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS4_5In_R22_50 |  | Extruded Polystyrene - XPS - 4 1/2 in. R22.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS4In_R20 |  | Extruded Polystyrene - XPS - 4 in. R20.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS5_5In_R27_50 |  | Extruded Polystyrene - XPS - 5 1/2 in. R27.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS5In_R25 |  | Extruded Polystyrene - XPS - 5 in. R25.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS6_5In_R32_50 |  | Extruded Polystyrene - XPS - 6 1/2 in. R32.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS6In_R30 |  | Extruded Polystyrene - XPS - 6 in. R30.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS8_5In_R42_50 |  | Extruded Polystyrene - XPS - 8 1/2 in. R42.50 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolystyreneXPS8In_R40 |  | Extruded Polystyrene - XPS - 8 in. R40.00 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolyurethane0_5In_R3_1 |  | Expanded Polyurethane - 1/2 in. R3.1 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolyurethane0_75In_R4_7 |  | Expanded Polyurethane - 3/4 in. R4.7 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolyurethane1_25In_R7_8 |  | Expanded Polyurethane - 1 1/4 in. R7.8 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolyurethane1In_R6_3 |  | Expanded Polyurethane - 1 in. R6.3 | CodeItem |  |  |  |  | InsulationBoard
|  | ExpandedPolyurethane2In_R12_6 |  | Expanded Polyurethane - 2 in. R12.6 | CodeItem |  |  |  |  | InsulationBoard
|  | PerliteBoard0_75In_R1_9 |  | Perlite board - 3/4 in. R1.9 | CodeItem |  |  |  |  | InsulationBoard
|  | PerliteBoard1_5In_R3_8 |  | Perlite board - 1 1/2 in. R3.8 | CodeItem |  |  |  |  | InsulationBoard
|  | PerliteBoard1In_R2_5 |  | Perlite board - 1 in. R2.5 | CodeItem |  |  |  |  | InsulationBoard
|  | PerliteBoard2In_R5_0 |  | Perlite board - 2 in. R5.0 | CodeItem |  |  |  |  | InsulationBoard
|  | R24BattWall8In_R24 |  | R-24 Batt Wall - 8 in. R24 | CodeItem |  |  |  |  | InsulationBoard
CodeCategory
InsulationLooseFill |  |  | InsulationLooseFill | Insulation Loose Fill | CodeCategory
CodeItem
|  | LooseFillMineralFiber2LbPerFt3Thickness13_75In |  | Loose fill - Mineral fiber - 2 lb/ft3 - 13 3/4 in. | CodeItem |  |  |  |  | InsulationLooseFill
|  | LooseFillMineralFiber2LbPerFt3Thickness4In |  | Loose fill - Mineral fiber - 2 lb/ft3 - 4 in. | CodeItem |  |  |  |  | InsulationLooseFill
|  | LooseFillMineralFiber2LbPerFt3Thickness6_5In |  | Loose fill - Mineral fiber - 2 lb/ft3 - 6 1/2 in. | CodeItem |  |  |  |  | InsulationLooseFill
|  | LooseFillMineralFiber2LbPerFt3Thickness7_5In |  | Loose fill - Mineral fiber - 2 lb/ft3 - 7 1/2 in. | CodeItem |  |  |  |  | InsulationLooseFill
|  | LooseFillMineralFiber2LbPerFt3Thickness8_25In |  | Loose fill - Mineral fiber - 2 lb/ft3 - 8 1/4 in. | CodeItem |  |  |  |  | InsulationLooseFill
|  | LooseFillMineralFiberClosedSidewallsThickness3_5In |  | Loose fill - Mineral fiber - closed sidewalls - 3 1/2 in. | CodeItem |  |  |  |  | InsulationLooseFill
CodeCategory
InsulationOther |  |  | InsulationOther | Insulation Other | CodeCategory
CodeItem
|  | RammedEarth |  | Rammed Earth | CodeItem |  |  |  |  | InsulationOther
CodeCategory
InsulationSprayApplied |  |  | InsulationSprayApplied | Insulation Spray Applied | CodeCategory
CodeItem
|  | SprayCellulosicFiber4_6LbPerFt3Thickness3_5In |  | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 3 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayCellulosicFiber4_6LbPerFt3Thickness4_5In |  | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayCellulosicFiber4_6LbPerFt3Thickness4In |  | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayCellulosicFiber4_6LbPerFt3Thickness5_5In |  | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayCellulosicFiber4_6LbPerFt3Thickness5In |  | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayCellulosicFiber4_6LbPerFt3Thickness6_5In |  | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayCellulosicFiber4_6LbPerFt3Thickness6In |  | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayGlassFiber3_9LbPerFt3Thickness3_5In |  | Spray applied - Glass fiber - 3.9 lb/ft3 - 3 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayGlassFiber3_9LbPerFt3Thickness4_5In |  | Spray applied - Glass fiber - 3.9 lb/ft3 - 4 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayGlassFiber3_9LbPerFt3Thickness4In |  | Spray applied - Glass fiber - 3.9 lb/ft3 - 4 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayGlassFiber3_9LbPerFt3Thickness5_5In |  | Spray applied - Glass fiber - 3.9 lb/ft3 - 5 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayGlassFiber3_9LbPerFt3Thickness5In |  | Spray applied - Glass fiber - 3.9 lb/ft3 - 5 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayGlassFiber3_9LbPerFt3Thickness6_5In |  | Spray applied - Glass fiber - 3.9 lb/ft3 - 6 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayGlassFiber3_9LbPerFt3Thickness6In |  | Spray applied - Glass fiber - 3.9 lb/ft3 - 6 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam0_5LbPerFt3Thickness3_5In |  | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 3 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam0_5LbPerFt3Thickness4_5In |  | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam0_5LbPerFt3Thickness4In |  | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam0_5LbPerFt3Thickness5_5In |  | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam0_5LbPerFt3Thickness5In |  | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam0_5LbPerFt3Thickness6_5In |  | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam0_5LbPerFt3Thickness6In |  | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam3_0LbPerFt3Thickness3_5In |  | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 3 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam3_0LbPerFt3Thickness4_5In |  | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam3_0LbPerFt3Thickness4In |  | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam3_0LbPerFt3Thickness5_5In |  | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam3_0LbPerFt3Thickness5In |  | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam3_0LbPerFt3Thickness6_5In |  | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 1/2 in. | CodeItem |  |  |  |  | InsulationSprayApplied
|  | SprayPolyurethaneFoam3_0LbPerFt3Thickness6In |  | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 in. | CodeItem |  |  |  |  | InsulationSprayApplied
CodeCategory
MasonryMaterials |  |  | MasonryMaterials | Masonry Materials | CodeCategory
CodeItem
|  | Brick48LbPerFt3Thickness3_625In |  | Brick - 48 lb/ft3 - 3 5/8 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | BrickFiredClay140LbPerFt3Thickness3_625In |  | Brick - fired clay - 140 lb/ft3 - 3 5/8 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | ClayTileHollow1CellDeepThickness3In |  | Clay tile - hollow - 1 cell deep - 3 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | ClayTileHollow1CellDeepThickness4In |  | Clay tile - hollow - 1 cell deep - 4 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | ClayTileHollow2CellDeepThickness10In |  | Clay tile - hollow - 2 cells deep - 10 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | ClayTileHollow2CellDeepThickness6In |  | Clay tile - hollow - 2 cells deep - 6 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | ClayTileHollow2CellDeepThickness8In |  | Clay tile - hollow - 2 cells deep - 8 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | ClayTileHollow3CellDeepThickness12In |  | Clay tile - hollow - 3 cells deep - 12 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | ClayTilePaver |  | Clay Tile - Paver | CodeItem |  |  |  |  | MasonryMaterials
|  | Concrete_Paver |  | Concrete Paver | CodeItem |  |  |  |  | MasonryMaterials
|  | GypsumPartitionBlock3Cell4x12x30Thickness4In |  | Gypsum partition block - 3 cells - 4 in. x 12 in. x 30 in. - 4 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | GypsumPartitionBlock4Cell3x12x30Thickness3In |  | Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | Stone1In |  | Stone - 1 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | Stucco1Coat |  | 1 Coat Stucco | CodeItem |  |  |  |  | MasonryMaterials
|  | Stucco3Coat |  | 3 Coat Stucco | CodeItem |  |  |  |  | MasonryMaterials
|  | StuccoSyntheticEIFS_Finish1In | StuccoSyntheticEIFS_Finish1In | Synthetic Stucco - EIFS finish - 1 in. | CodeItem |  |  |  |  | MasonryMaterials
|  | Terrazzo1In | Terrazzo1In | Terrazzo - 1 in. | CodeItem |  |  |  |  | MasonryMaterials
CodeCategory
MasonryUnitsFill |  |  | MasonryUnitsFill | Masonry Units with Fill | CodeCategory
CodeItem
|  | ClayPartGroutedInsulated130LbPerFt3Thickness6In |  | Clay - Part Grouted and Insulated - 130 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ClayPartGroutedInsulated130LbPerFt3Thickness8In |  | Clay - Part Grouted and Insulated - 130 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated105LbPerFt3Thickness10In |  | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated105LbPerFt3Thickness12In |  | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated105LbPerFt3Thickness6In |  | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated105LbPerFt3Thickness8In |  | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated115LbPerFt3Thickness10In |  | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated115LbPerFt3Thickness12In |  | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated115LbPerFt3Thickness6In |  | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated115LbPerFt3Thickness8In |  | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated125LbPerFt3Thickness10In |  | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated125LbPerFt3Thickness12In |  | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated125LbPerFt3Thickness6In |  | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsFill
|  | ConcretePartGroutedInsulated125LbPerFt3Thickness8In |  | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsFill
CodeCategory
MasonryUnitsHollow |  |  | MasonryUnitsHollow | Masonry Units Hollow | CodeCategory
CodeItem
|  | ClayPartGrouted130LbPerFt3Thickness6In |  | Clay - Part Grouted and Empty - 130 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ClayPartGrouted130LbPerFt3Thickness8In |  | Clay - Part Grouted and Empty - 130 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted105LbPerFt3Thickness10In |  | Concrete - Part Grouted and Empty - 105 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted105LbPerFt3Thickness12In |  | Concrete - Part Grouted and Empty - 105 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted105LbPerFt3Thickness6In |  | Concrete - Part Grouted and Empty - 105 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted105LbPerFt3Thickness8In |  | Concrete - Part Grouted and Empty - 105 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted115LbPerFt3Thickness10In |  | Concrete - Part Grouted and Empty - 115 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted115LbPerFt3Thickness12In |  | Concrete - Part Grouted and Empty - 115 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted115LbPerFt3Thickness6In |  | Concrete - Part Grouted and Empty - 115 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted115LbPerFt3Thickness8In |  | Concrete - Part Grouted and Empty - 115 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted125LbPerFt3Thickness10In |  | Concrete - Part Grouted and Empty - 125 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted125LbPerFt3Thickness12In |  | Concrete - Part Grouted and Empty - 125 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted125LbPerFt3Thickness6In |  | Concrete - Part Grouted and Empty - 125 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
|  | ConcretePartGrouted125LbPerFt3Thickness8In |  | Concrete - Part Grouted and Empty - 125 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsHollow
CodeCategory
MasonryUnitsSolid |  |  | MasonryUnitsSolid | Masonry Units Solid | CodeCategory
CodeItem
|  | ClaySolidGrout130LbPerFt3Thickness6In |  | Clay - Solid Grout - 130 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ClaySolidGrout130LbPerFt3Thickness8In |  | Clay - Solid Grout - 130 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout105LbPerFt3Thickness10In |  | Concrete - Solid Grout - 105 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout105LbPerFt3Thickness12In |  | Concrete - Solid Grout - 105 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout105LbPerFt3Thickness6In |  | Concrete - Solid Grout - 105 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout105LbPerFt3Thickness8In |  | Concrete - Solid Grout - 105 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout115LbPerFt3Thickness10In |  | Concrete - Solid Grout - 115 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout115LbPerFt3Thickness12In |  | Concrete - Solid Grout - 115 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout115LbPerFt3Thickness6In |  | Concrete - Solid Grout - 115 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout115LbPerFt3Thickness8In |  | Concrete - Solid Grout - 115 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout125LbPerFt3Thickness10In |  | Concrete - Solid Grout - 125 lb/ft3 - 10 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout125LbPerFt3Thickness12In |  | Concrete - Solid Grout - 125 lb/ft3 - 12 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout125LbPerFt3Thickness6In |  | Concrete - Solid Grout - 125 lb/ft3 - 6 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
|  | ConcreteSolidGrout125LbPerFt3Thickness8In |  | Concrete - Solid Grout - 125 lb/ft3 - 8 in. | CodeItem |  |  |  |  | MasonryUnitsSolid
CodeCategory
MetalInsulatedPanelWall |  |  | MetalInsulatedPanelWall | Metal Insulated Panel Wall | CodeCategory
CodeItem
|  | MetalInsulatedPanel2_5In |  | Metal Insulated Panels - 2 1/2 in. | CodeItem |  |  |  |  | MetalInsulatedPanelWall
|  | MetalInsulatedPanel2In |  | Metal Insulated Panels - 2 in. | CodeItem |  |  |  |  | MetalInsulatedPanelWall
|  | MetalInsulatedPanel3In |  | Metal Insulated Panels - 3 in. | CodeItem |  |  |  |  | MetalInsulatedPanelWall
|  | MetalInsulatedPanel4In |  | Metal Insulated Panels - 4 in. | CodeItem |  |  |  |  | MetalInsulatedPanelWall
|  | MetalInsulatedPanel5In |  | Metal Insulated Panels - 5 in. | CodeItem |  |  |  |  | MetalInsulatedPanelWall
|  | MetalInsulatedPanel6In |  | Metal Insulated Panels - 6 in. | CodeItem |  |  |  |  | MetalInsulatedPanelWall
CodeCategory
PlasteringMaterials |  |  | Plastering | Plastering Materials | CodeCategory
CodeItem
|  | Aggregate45LbPerFt3Thickness0_5In |  | Aggregate - 45 lb/ft3 - 1/2 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | Aggregate45LbPerFt3Thickness0_625In |  | Aggregate - 45 lb/ft3 - 5/8 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | AggregateOnMetalLath45LbPerFt3Thickness0_75In |  | Aggregate - 45 lb/ft3 - on metal lath - 3/4 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | AggregatePerliteOnMetalLathThickness0_75In |  | Aggregate - Perlite - on metal lath - 3/4 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | AggregatePerliteThickness0_5In |  | Aggregate - Perlite - 1/2 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | AggregatePerliteThickness0_625In |  | Aggregate - Perlite - 5/8 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | ConcreteSandAggregateThickness6In |  | Concrete/Sand Aggregate - 6 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | GypsumPlaster80LbPerFt3Thickness0_5In |  | Gypsum plaster - 80 lb/ft3 - 1/2 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | GypsumPlaster80LbPerFt3Thickness0_625In |  | Gypsum plaster - 80 lb/ft3 - 5/8 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | GypsumPlasterOnMetalLath70LbPerFt3Thickness0_75In |  | Gypsum plaster - on metal lath 70 lb/ft3 - 3/4 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | GypsumPlasterOnMetalLath80LbPerFt3Thickness0_75In |  | Gypsum plaster - on metal lath 80 lb/ft3 - 3/4 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | MortarCementThickness1_75In |  | Mortar - Cement - 1 3/4 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | MortarCementThickness1In |  | Mortar - Cement - 1 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | PerlitePlaster25LbPerFt3Thickness0_5In |  | Perlite plaster - 25 lb/ft3 - 1/2 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | PerlitePlaster38LbPerFt3Thickness0_5In |  | Perlite plaster - 38 lb/ft3 - 1/2 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | PlasterSandAggregateThickness1In |  | Plaster/Sand Aggregate - 1 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | PulpboardOrPaperPlasterThickness0_5In |  | Pulpboard or paper plaster - 1/2 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | SandAggregateOnMetalLathThickness0_75In |  | Sand aggregate on metal lath - 3/4 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | SandAggregateThickness0_375In |  | Sand aggregate - 3/8 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | SandAggregateThickness0_5In |  | Sand aggregate - 1/2 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | SandAggregateThickness0_625In |  | Sand aggregate - 5/8 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | SandAggregateThickness0_75In |  | Sand aggregate - 3/4 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | Stucco0_375In |  | Stucco - 3/8 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | Stucco0_875In |  | Stucco - 7/8 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | StuccoSyntheticEIFS_Finish1In |  | Synthetic Stucco - EIFS finish - 1 in. | CodeItem |  |  |  |  | PlasteringMaterials
|  | VermiculiteAggregate45LbPerFt3Thickness0_5In |  | Vermiculite aggregate - 45 lb/ft3 - 1/2 in. | CodeItem |  |  |  |  | PlasteringMaterials
CodeCategory
Roofing |  |  | Roofing | Roofing | CodeCategory
CodeItem
|  | AsbestosOrCementShingles0_375In | AsbestosOrCementShingles0_375In | Asbestos or cement shingles - 3/8 in. | CodeItem |  |  |  |  | Roofing
|  | AsphaltBitumenInertFill100LbPerFt3Thickness0_75In | AsphaltBitumenInertFill100LbPerFt3Thickness0_75In | Asphalt - bitumen with inert fill - 100 lb/ft3 - 3/4 in. | CodeItem |  |  |  |  | Roofing
|  | AsphaltBitumenInertFill144LbPerFt3Thickness0_75In | AsphaltBitumenInertFill144LbPerFt3Thickness0_75In | Asphalt - bitumen with inert fill - 144 lb/ft3 - 3/4 in. | CodeItem |  |  |  |  | Roofing
|  | AsphaltRollRoofing0_25In | AsphaltRollRoofing0_25In | Asphalt roll roofing - 1/4 in. | CodeItem |  |  |  |  | Roofing
|  | AsphaltShingles0_25In | AsphaltShingles0_25In | Asphalt shingles - 1/4 in. | CodeItem |  |  |  |  | Roofing
|  | BuiltUpRoofing0_375In | BuiltUpRoofing0_375In | Built-up roofing - 3/8 in. | CodeItem |  |  |  |  | Roofing
|  | ClayTile0_5In | ClayTile0_5In | Clay tile - 1/2 in. | CodeItem |  |  |  |  | Roofing
|  | LightRoof0_4In | LightRoof0_4In | Light Roof - 2/5 in. | CodeItem |  |  |  |  | Roofing
|  | MasticAsphaltHeavy20PercentGrit1In | MasticAsphaltHeavy20PercentGrit1In | Mastic asphalt (heavy - 20% grit) - 1 in. | CodeItem |  |  |  |  | Roofing
|  | MetalStandingSeam0_0625In | MetalStandingSeam0_0625In | Metal Standing Seam - 1/16 in. | CodeItem |  |  |  |  | Roofing
|  | Roof10LbPerFt2Thickness1In | Roof10LbPerFt2Thickness1In | 10 PSF Roof - 1 in. | CodeItem |  |  |  |  | Roofing
|  | Roof15LbPerFt2Thickness1_5In | Roof15LbPerFt2Thickness1_5In | 15 PSF Roof - 1 1/2 in. | CodeItem |  |  |  |  | Roofing
|  | Roof25LbPerFt2Thickness2_5In | Roof25LbPerFt2Thickness2_5In | 25 PSF Roof - 2 1/2 in. | CodeItem |  |  |  |  | Roofing
|  | Roof5LbPerFt2Thickness0_5In | Roof5LbPerFt2Thickness0_5In | 5 PSF Roof - 1/2 in. | CodeItem |  |  |  |  | Roofing
|  | RoofGravel0_5In | RoofGravel0_5In | Roof Gravel - 1/2 in. | CodeItem |  |  |  |  | Roofing
|  | RoofGravel1In | RoofGravel1In | Roof Gravel - 1 in. | CodeItem |  |  |  |  | Roofing
|  | SinglePlyRoofing0_25In | SinglePlyRoofing0_25In | Single Ply Roofing - 1/4 in. | CodeItem |  |  |  |  | Roofing
|  | Slate0_5In | Slate0_5In | Slate - 1/2 in. | CodeItem |  |  |  |  | Roofing
|  | TileGap0_75In | TileGap0_75In | Tile Gap - 3/4 in. | CodeItem |  |  |  |  | Roofing
|  | WoodShingles0_75In | WoodShingles0_75In | Wood shingles - 3/4 in. | CodeItem |  |  |  |  | Roofing
|  | WoodShinglesPlainAndPlasticFilmFaced0_75In | WoodShinglesPlainAndPlasticFilmFaced0_75In | Wood shingles - plain and plastic film faced - 3/4 in. | CodeItem |  |  |  |  | Roofing
(no property)
SIPS_Floor
CodeItem
|  | SIPS_CrawlSpaceR36Double2xSpline10_25In |  | SIPS - Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPS_NoCrawlSpaceR36Double2xSpline10_25In |  | SIPS - No Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR22Double2xSpline6_5In |  | SIPS - Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR22IJoistSpline6_5In |  | SIPS - Crawl Space - R22 - I Joist Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR22Single2xSpline6_5In |  | SIPS - Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR28Double2xSpline8_25In |  | SIPS - Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR28IJoistSpline8_25In |  | SIPS - Crawl Space - R28 - I Joist Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR28Single2xSpline8_25In |  | SIPS - Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR33Double2xSpline6_5In |  | SIPS - Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR33IJoistSpline6_5In |  | SIPS - Crawl Space - R33 - I Joist Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR33Single2xSpline6_5In |  | SIPS - Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR36IJoistSpline10_25In |  | SIPS - Crawl Space - R36 - I Joist Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSCrawlSpaceR36Single2xSpline10_25In |  | SIPS - Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR22Double2xSpline6_5In |  | SIPS - No Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR22IJoistSpline6_5In |  | SIPS - No Crawl Space - R22 - I Joist Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR22Single2xSpline6_5In |  | SIPS - No Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR28Double2xSpline8_25In |  | SIPS - No Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR28IJoistSpline8_25In |  | SIPS - No Crawl Space - R28 - I Joist Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR28Single2xSpline8_25In |  | SIPS - No Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR33Double2xSpline6_5In |  | SIPS - No Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR33IJoistSpline6_5In |  | SIPS - No Crawl Space - R33 - I Joist Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR33Single2xSpline6_5In |  | SIPS - No Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR36IJoistSpline10_25In |  | SIPS - No Crawl Space - R36 - I Joist Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
|  | SIPSNoCrawlSpaceR36Single2xSpline10_25In |  | SIPS - No Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Floor
(no property)
SIPS_Roof
CodeItem
|  | SIPSR14MetalSpline48In |  | SIPS - R14 - Metal Spline - 48 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR22Double2xSpline6_5In |  | SIPS - R22 - Double 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR22IJoistSpline6_5In |  | SIPS - R22 - I joist Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR22MetalSpline48In |  | SIPS - R22 - Metal Spline - 48 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR22OSBSpline6_5In |  | SIPS - R22 - OSB Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR22Single2xSpline6_5In |  | SIPS - R22 - Single 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR28Double2xSpline8_5In |  | SIPS - R28 - Double 2x Spline - 8 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR28IJoistSpline8_5In |  | SIPS - R28 - I joist Spline - 8 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR28MetalSpline48In |  | SIPS - R28 - Metal Spline - 48 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR28OSBSpline8_5In |  | SIPS - R28 - OSB Spline - 8 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR28Single2xSpline8_5In |  | SIPS - R28 - Single 2x Spline - 8 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR33Double2xSpline6_5In |  | SIPS - R33 - Double 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR33IJoistSpline6_5In |  | SIPS - R33 - I joist Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR33OSBSpline6_5In |  | SIPS - R33 - OSB Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR33Single2xSpline6_5In |  | SIPS - R33 - Single 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR36Double2xSpline10_25In |  | SIPS - R36 - Double 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR36IJoistSpline10_25In |  | SIPS - R36 - I joist Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR36MetalSpline48In |  | SIPS - R36 - Metal Spline - 48 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR36OSBSpline10_25In |  | SIPS - R36 - OSB Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR36Single2xSpline10_25In |  | SIPS - R36 - Single 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR44Double2xSpline12_25In |  | SIPS - R44 - Double 2x Spline - 12 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR44IJoistSpline12_25In |  | SIPS - R44 - I joist Spline - 12 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR44OSBSpline12_25In |  | SIPS - R44 - OSB Spline - 12 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR44Single2xSpline12_25In |  | SIPS - R44 - Single 2x Spline - 12 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR55Double2xSpline10_25In |  | SIPS - R55 - Double 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR55IJoistSpline10_25In |  | SIPS - R55 - I joist Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR55OSBSpline10_25In |  | SIPS - R55 - OSB Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
|  | SIPSR55Single2xSpline10_25In |  | SIPS - R55 - Single 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Roof
(no property)
SIPS_Wall
CodeItem
|  | SIPSR14Double2xSpline4_5In |  | SIPS - R14 - Double 2x Spline - 4 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR14IJoistSpline4_5In |  | SIPS - R14 - I joist Spline - 4 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR14OSBSpline4_5In |  | SIPS - R14 - OSB Spline - 4 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR14Single2xSpline4_5In |  | SIPS - R14 - Single 2x Spline - 4 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR18Double2xSpline4_5In |  | SIPS - R18 - Double 2x Spline - 4 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR18IJoistSpline4_5In |  | SIPS - R18 - I joist Spline - 4 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR18OSBSpline4_5In |  | SIPS - R18 - OSB Spline - 4 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR18Single2xSpline4_5In |  | SIPS - R18 - Single 2x Spline - 4 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR22Double2xSpline6_5In | SIPSR22Double2xSpline6_5In | SIPS - R22 - Double 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR22IJoistSpline6_5In | SIPS_R22IJoistSpline6_5In | SIPS - R22 - I joist Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR22OSBSpline6_5In | SIPS_R22OSBSpline6_5In | SIPS - R22 - OSB Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR22Single2xSpline6_5In | SIPS_R22Single2xSpline6_5In | SIPS - R22 - Single 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR28Double2xSpline8_25In |  | SIPS - R28 - Double 2x Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR28IJoistSpline8_25In |  | SIPS - R28 - I joist Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR28OSBSpline8_25In |  | SIPS - R28 - OSB Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR28Single2xSpline8_25In |  | SIPS - R28 - Single 2x Spline - 8 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR33Double2xSpline6_5In | SIPSR33Double2xSpline6_5In | SIPS - R33 - Double 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR33IJoistSpline6_5In | SIPS_R33IJoistSpline6_5In | SIPS - R33 - I joist Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR33OSBSpline6_5In | SIPS_R33OSBSpline6_5In | SIPS - R33 - OSB Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR33Single2xSpline6_5In | SIPS_R33Single2xSpline6_5In | SIPS - R33 - Single 2x Spline - 6 1/2 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR36Double2xSpline10_25In | SIPS_R36Double2xSpline10_25In | SIPS - R36 - Double 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR36IJoistSpline10_25In | SIPS_R36IJoistSpline10_25In | SIPS - R36 - I joist Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR36OSBSpline10_25In | SIPS_R36OSBSpline10_25In | SIPS - R36 - OSB Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR36Single2xSpline10_25In | SIPS_R36Single2xSpline10_25In | SIPS - R36 - Single 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR44Double2xSpline12_25In | SIPS_R44Double2xSpline12_25In | SIPS - R44 - Double 2x Spline - 12 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR44IJoistSpline12_25In | SIPS_R44IJoistSpline12_25In | SIPS - R44 - I joist Spline - 12 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR44OSBSpline12_25In | SIPS_R44OSBSpline12_25In | SIPS - R44 - OSB Spline - 12 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR44Single2xSpline12_25In | SIPS_R44Single2xSpline12_25In | SIPS - R44 - Single 2x Spline - 12 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR55Double2xSpline10_25In | SIPS_R55Double2xSpline10_25In | SIPS - R55 - Double 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR55IJoistSpline10_25In | SIPS_R55IJoistSpline10_25In | SIPS - R55 - I joist Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR55OSBSpline10_25In | SIPS_R55OSBSpline10_25In | SIPS - R55 - OSB Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
|  | SIPSR55Single2xSpline10_25In | SIPS_R55Single2xSpline10_25In | SIPS - R55 - Single 2x Spline - 10 1/4 in. | CodeItem |  |  |  |  | SIPS_Wall
(no property)
SpaceOccupancyType
FunctionScheduleGroup
| Restaurant |  | Restaurant |  | FunctionScheduleGroup
SpaceFunction
|  | KitchenCommercialFoodPreparation | KitchenCommercialFoodPreparation |  | SpaceFunction |  |  | Restaurant |  | SpaceOccupancyType
| TransportationFunctionConcourseBaggage |  | TransportationFunctionConcourseBaggage | Transportation Function, Concourse and Baggage | SpaceFunction |  |  |  |  | SpaceOccupancyType |  | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | TransportationFunctionTicketing | TransportationFunctionTicketing | Transportation Function, Ticketing | SpaceFunction |  |  |  |  | SpaceOccupancyType |  | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | UnoccupiedExcludeInGrossFloorArea | UnoccupiedExcludeInGrossFloorArea | Unoccupied-Exclude from Gross Floor Area | SpaceFunction |  |  |  |  | SpaceOccupancyType
|  | UnoccupiedIncludeInGrossFloorArea | UnoccupiedIncludeInGrossFloorArea | Unoccupied-Include in Gross Floor Area | SpaceFunction |  |  |  |  | SpaceOccupancyType
CodeCategory
SpandrelPanelsCurtainWalls |  |  | SpandrelPanelsCurtainWalls | Spandrel Panels Curtain Walls | CodeCategory
CodeItem
|  | AluminumNoThermalBreakDoubleNoLowENoIns |  | Aluminum w/out Thrml Break - Double glass with no low e coatings - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakDoubleNoLowER10Ins |  | Aluminum w/out Thrml Break - Double glass with no low e coatings - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakDoubleNoLowER15Ins |  | Aluminum w/out Thrml Break - Double glass with no low e coatings - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakDoubleNoLowER20Ins |  | Aluminum w/out Thrml Break - Double glass with no low e coatings - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakDoubleNoLowER25Ins |  | Aluminum w/out Thrml Break - Double glass with no low e coatings - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakDoubleNoLowER30Ins |  | Aluminum w/out Thrml Break - Double glass with no low e coatings - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakDoubleNoLowER4Ins |  | Aluminum w/out Thrml Break - Double glass with no low e coatings - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakDoubleNoLowER7Ins |  | Aluminum w/out Thrml Break - Double glass with no low e coatings - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakSingleGlassStoneMetalNoIns |  | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakSingleGlassStoneMetalR10Ins |  | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakSingleGlassStoneMetalR15Ins |  | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakSingleGlassStoneMetalR20Ins |  | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakSingleGlassStoneMetalR25Ins |  | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakSingleGlassStoneMetalR30Ins |  | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakSingleGlassStoneMetalR4Ins |  | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakSingleGlassStoneMetalR7Ins |  | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakTripleOrLowENoIns |  | Aluminum w/out Thrml Break - Triple or low e glass - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakTripleOrLowER10Ins |  | Aluminum w/out Thrml Break - Triple or low e glass - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakTripleOrLowER15Ins |  | Aluminum w/out Thrml Break - Triple or low e glass - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakTripleOrLowER20Ins |  | Aluminum w/out Thrml Break - Triple or low e glass - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakTripleOrLowER25Ins |  | Aluminum w/out Thrml Break - Triple or low e glass - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakTripleOrLowER30Ins |  | Aluminum w/out Thrml Break - Triple or low e glass - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakTripleOrLowER4Ins |  | Aluminum w/out Thrml Break - Triple or low e glass - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumNoThermalBreakTripleOrLowER7Ins |  | Aluminum w/out Thrml Break - Triple or low e glass - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakDoubleNoLowENoIns |  | Aluminum w/ Thrml Break - Double glass with no low e - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakDoubleNoLowER10Ins |  | Aluminum w/ Thrml Break - Double glass with no low e - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakDoubleNoLowER15Ins |  | Aluminum w/ Thrml Break - Double glass with no low e - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakDoubleNoLowER20Ins |  | Aluminum w/ Thrml Break - Double glass with no low e - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakDoubleNoLowER25Ins |  | Aluminum w/ Thrml Break - Double glass with no low e - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakDoubleNoLowER30Ins |  | Aluminum w/ Thrml Break - Double glass with no low e - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakDoubleNoLowER4Ins |  | Aluminum w/ Thrml Break - Double glass with no low e - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakDoubleNoLowER7Ins |  | Aluminum w/ Thrml Break - Double glass with no low e - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakSingleGlassStoneMetalNoIns |  | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakSingleGlassStoneMetalR10Ins |  | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakSingleGlassStoneMetalR15Ins |  | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakSingleGlassStoneMetalR20Ins |  | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakSingleGlassStoneMetalR25Ins |  | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakSingleGlassStoneMetalR30Ins |  | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakSingleGlassStoneMetalR4Ins |  | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakSingleGlassStoneMetalR7Ins |  | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakTripleOrLowENoIns |  | Aluminum w/ Thrml Break - Triple or low e glass - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakTripleOrLowER10Ins |  | Aluminum w/ Thrml Break - Triple or low e glass - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakTripleOrLowER15Ins |  | Aluminum w/ Thrml Break - Triple or low e glass - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakTripleOrLowER20Ins |  | Aluminum w/ Thrml Break - Triple or low e glass - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakTripleOrLowER25Ins |  | Aluminum w/ Thrml Break - Triple or low e glass - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakTripleOrLowER30Ins |  | Aluminum w/ Thrml Break - Triple or low e glass - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakTripleOrLowER4Ins |  | Aluminum w/ Thrml Break - Triple or low e glass - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | AluminumThermalBreakTripleOrLowER7Ins |  | Aluminum w/ Thrml Break - Triple or low e glass - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationDoubleNoLowENoIns |  | Continuous Ins. - Double glass with no low e coatings - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationDoubleNoLowER10Ins |  | Continuous Ins. - Double glass with no low e coatings - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationDoubleNoLowER15Ins |  | Continuous Ins. - Double glass with no low e coatings - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationDoubleNoLowER20Ins |  | Continuous Ins. - Double glass with no low e coatings - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationDoubleNoLowER25Ins |  | Continuous Ins. - Double glass with no low e coatings - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationDoubleNoLowER30Ins |  | Continuous Ins. - Double glass with no low e coatings - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationDoubleNoLowER4Ins |  | Continuous Ins. - Double glass with no low e coatings - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationDoubleNoLowER7Ins |  | Continuous Ins. - Double glass with no low e coatings - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationSingleGlassStoneMetalNoIns |  | Continuous Ins. - Single glass pane. stone. or metal pane - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationSingleGlassStoneMetalR10Ins |  | Continuous Ins. - Single glass pane. stone. or metal pane - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationSingleGlassStoneMetalR15Ins |  | Continuous Ins. - Single glass pane. stone. or metal pane - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationSingleGlassStoneMetalR20Ins |  | Continuous Ins. - Single glass pane. stone. or metal pane - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationSingleGlassStoneMetalR25Ins |  | Continuous Ins. - Single glass pane. stone. or metal pane - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationSingleGlassStoneMetalR30Ins |  | Continuous Ins. - Single glass pane. stone. or metal pane - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationSingleGlassStoneMetalR4Ins |  | Continuous Ins. - Single glass pane. stone. or metal pane - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationSingleGlassStoneMetalR7Ins |  | Continuous Ins. - Single glass pane. stone. or metal pane - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationTripleOrLowENoIns |  | Continuous Ins. - Triple or low e glass - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationTripleOrLowER10Ins |  | Continuous Ins. - Triple or low e glass - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationTripleOrLowER15Ins |  | Continuous Ins. - Triple or low e glass - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationTripleOrLowER20Ins |  | Continuous Ins. - Triple or low e glass - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationTripleOrLowER25Ins |  | Continuous Ins. - Triple or low e glass - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationTripleOrLowER30Ins |  | Continuous Ins. - Triple or low e glass - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationTripleOrLowER4Ins |  | Continuous Ins. - Triple or low e glass - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | ContinuousInsulationTripleOrLowER7Ins |  | Continuous Ins. - Triple or low e glass - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingDoubleNoLowENoIns |  | Structural Glazing - Double glass with no low e coatings - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingDoubleNoLowER10Ins |  | Structural Glazing - Double glass with no low e coatings - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingDoubleNoLowER15Ins |  | Structural Glazing - Double glass with no low e coatings - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingDoubleNoLowER20Ins |  | Structural Glazing - Double glass with no low e coatings - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingDoubleNoLowER25Ins |  | Structural Glazing - Double glass with no low e coatings - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingDoubleNoLowER30Ins |  | Structural Glazing - Double glass with no low e coatings - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingDoubleNoLowER4Ins |  | Structural Glazing - Double glass with no low e coatings - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingDoubleNoLowER7Ins |  | Structural Glazing - Double glass with no low e coatings - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingSingleGlassStoneMetalNoIns |  | Structural Glazing - Single glass pane. stone. or metal pane - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingSingleGlassStoneMetalR10Ins |  | Structural Glazing - Single glass pane. stone. or metal pane - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingSingleGlassStoneMetalR15Ins |  | Structural Glazing - Single glass pane. stone. or metal pane - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingSingleGlassStoneMetalR20Ins |  | Structural Glazing - Single glass pane. stone. or metal pane - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingSingleGlassStoneMetalR25Ins |  | Structural Glazing - Single glass pane. stone. or metal pane - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingSingleGlassStoneMetalR30Ins |  | Structural Glazing - Single glass pane. stone. or metal pane - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingSingleGlassStoneMetalR4Ins |  | Structural Glazing - Single glass pane. stone. or metal pane - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingSingleGlassStoneMetalR7Ins |  | Structural Glazing - Single glass pane. stone. or metal pane - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingTripleOrLowENoIns |  | Structural Glazing - Triple or low e glass - No Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingTripleOrLowER10Ins |  | Structural Glazing - Triple or low e glass - R10 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingTripleOrLowER15Ins |  | Structural Glazing - Triple or low e glass - R15 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingTripleOrLowER20Ins |  | Structural Glazing - Triple or low e glass - R20 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingTripleOrLowER25Ins |  | Structural Glazing - Triple or low e glass - R25 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingTripleOrLowER30Ins |  | Structural Glazing - Triple or low e glass - R30 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingTripleOrLowER4Ins |  | Structural Glazing - Triple or low e glass - R4 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
|  | StructuralGlazingTripleOrLowER7Ins |  | Structural Glazing - Triple or low e glass - R7 Ins. | CodeItem |  |  |  |  | SpandrelPanelsCurtainWalls
(no property)
StrawBale
CodeItem
|  | StrawBaleIntExtStucco18In |  | Straw Bale - Int and Ext Stucco - 18 in. | CodeItem |  |  |  |  | StrawBale
(no property)
WoodMaterial
CodeItem
|  | Ash1In |  | Ash - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Birch1In |  | Birch - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | CaliforniaRedwood1In |  | California Redwood - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | DouglasFirLarch1In |  | Douglas Fir-Larch - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Hardwood0_5In |  | Hardwood - 1/2 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Hardwood0_75In |  | Hardwood - 3/4 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Hardwood1In |  | Hardwood - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Maple1In |  | Maple - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Oak1In |  | Oak - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | PineOvenDried1In |  | Pine (oven-dried) - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Wood0_5In |  | Wood - 1/2 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Wood1In |  | Wood - 1 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Wood2In |  | Wood - 2 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Wood4In |  | Wood - 4 in. | CodeItem |  |  |  |  | WoodMaterial
|  | WoodSiding0_5In | WoodSiding0_5In | Wood siding - 1/2 in. | CodeItem |  |  |  |  | WoodMaterial
|  | Plenum | Plenum |  | ConditioningType | [5 empty] | NonResidential (includes Hotel, Motel and High-rise Residential)
NonresidentialBuildingOccupancyType |  |  | NonresidentialBuildingOccupancyType |  | TopLevelOccupancy |  | The whole building occupancy type for a building defined as nonresidential which includes hotels, motels and high-rise residential. |  |  |  | NonResidential (includes Hotel, Motel and High-rise Residential)
| Assembly |  | Assembly |  | FunctionScheduleGroup
|  | AuditoriumBuilding | AuditoriumBuilding | Auditorium Building |  |  | Part of a public building where an audience sits in fixed seating, or a room, area, with fixed seats used for public meetings or gatherings not specifically for the viewing of dramatic performances. | Assembly | GroupAssembly | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Whole building occupancy
|  | ConventionCenterBuilding | ConventionCenterBuilding | Convention Center Building |  |  | A building that is used for meetings, conventions and multiple purposes, including, but not limited to, dramatic performances, and that has neither fixed seating nor fixed staging. | Assembly | GroupAssembly | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Whole building occupancy
|  | ReligiousBuilding | ReligiousBuilding | Religious Building |  |  | A building in which the primary function is for an assembly of people to worship, Religious facilities do not include classroom, housing, or gymnasium buildings. | Assembly | GroupAssembly | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy COMNET Whole building occupancy 2013 NR ACM: Whole building occupancy
|  | TheaterBuilding | TheaterBuilding | Theater Building |  |  | From Title 24 Part 6 Section 101 Definitions, an assembly room, a hall, or a building with tiers of rising seats or steps for the showing of motion pictures. | Assembly | GroupAssembly | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy 2013 NR ACM: Whole building occupancy
| Health |  | Health |  | FunctionScheduleGroup
|  | MedicalClinicBuilding | MedicalClinicBuilding | Medical Clinic Building |  |  | Medical buildings and clinics: a building where medical and clinical care is provided and does not provide overnight patient care. | Health | GroupBusiness | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy COMNET Whole building occupancy 2013 NR ACM: Whole building occupancy
| Manufacturing |  | Manufacturing |  | FunctionScheduleGroup
|  | GeneralCommercialIndustrialWorkBuilding | GeneralCommercialIndustrialWorkBuilding | General Commerical or Industrial Work Building |  |  | A room, area, or building in which an art, craft, assembly or manufacturing operation is performed and the luminaires 25 feet or more above the floor. | Manufacturing | GroupFactory | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy 2013 NR ACM: Whole building occupancy
| Office |  | Office |  | FunctionScheduleGroup
|  | AllOthersBuildings | AllOthersBuildings |  |  |  | In most tables that evaluate occupancy in order to assign a rule target value, there is a catch all category of All Others | Office |  | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Whole building occupancy
|  | AnyBuildings | AnyBuildings |  |  |  |  | Office |  | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Whole building occupancy
|  | FinancialInstitutionBuilding | FinancialInstitutionBuilding | Financial Institution Building |  |  | Financial institution: a public establishment used for conducting financial transactions including the custody, loan, exchange, or issue of money, for the extension of credit, and for facilitating the transmission of funds. Financial transactions is the teller, work stations, and customers waiting areas to complete financial transactions. Financial transaction areas do not include private offices, hallways, restrooms, or other support areas. | Office | GroupBusiness | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Whole building occupancy
|  | LibraryBuilding | LibraryBuilding | Library Building |  |  | A building that contains repository for literary materials, such as books, periodicals, newspapers, pamphlets and prints, and provides areas for reading and stacks as well as amenities for the library patrons. | Office | GroupAssembly | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy COMNET Whole building occupancy 2013 NR ACM: Whole building occupancy
|  | OfficeBuilding | OfficeBuilding | Office Building |  |  | Office: a room, area, or building of CBC Group B Occupancy | Office | GroupBusiness | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy COMNET Whole building occupancy 2013 NR ACM: Whole building occupancy
| Parking |  | Parking |  | FunctionScheduleGroup
|  | ParkingGarageBuilding | ParkingGarageBuilding | Parking Garage Building |  |  | A covered building or structure for the purpose of parking vehicles | Parking |  | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | COMNET Whole building occupancy 2013 NR ACM: Whole building occupancy
| Retail |  | Retail |  | FunctionScheduleGroup
|  | GroceryStoreBuilding | GroceryStoreBuilding | Grocery Store Building |  |  | A building that has as its primary purpose the sale of foodstuffs requiring additional preparation priorto consumption | Retail | GroupMercantile | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy
| School |  | School |  | FunctionScheduleGroup
|  | ClassroomBuilding | ClassroomBuilding | Classroom Building |  |  | A building or group of buildings that is predominately classrooms used by an organization that provides instruction to students. A classroom building does not include auditorium, gymnasium, kitchen, library, multi-purpose, dining and cafeteria, student union, maintenance staff workroom, or storage buildings. | School | GroupEducational | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Not included as a whole building occupancy type
|  | SchoolBuilding | SchoolBuilding | School Building |  |  | A building or group of buildings that is used by an organization that provides instruction to students, whichis predominately classroom buildings but may also include auditorium, gymnasium, kitchen, library, multi-purposerooms, dining and cafeteria, student union, maintenance staff workroom, and small storage spaces. | School | GroupEducational | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy COMNET Whole building occupancy 2013 NR ACM: Whole building occupancy
| Warehouse |  | Warehouse |  | FunctionScheduleGroup
|  | CommercialIndustrialStorageBuilding | CommercialIndustrialStorageBuilding | Commercial and Insustrial Storage Building |  |  | Commercial and industrial storage is a room, area, or building used for storing items. | Warehouse |  | NonresidentialBuildingOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy 2013 NR ACM: Whole building occupancy
SpaceOccupancyType
| Assembly |  | Assembly |  | FunctionScheduleGroup
|  | AuditoriumArea | AuditoriumArea | Auditorium Area | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
|  | CivicMeetingPlaceArea | CivicMeetingPlaceArea | Civic Meeting Place Area | SpaceFunction |  | Civic meeting place: a city council or board of supervisors meeting chamber, courtroom, or other official meetingspace accessible to the public. | Assembly | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | ConventionConferenceMultipurposeMeetingCenterArea | ConventionConferenceMultipurposeMeetingCenterArea | Convention, Conference, Multipurpose and Meeting Center Areas | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy 90.1 2007 Table 9.6.1
|  | ExhibitMuseumArea | ExhibitMuseumArea | Exhibit, Museum Areas | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy 90.1 2007 Table 9.6.1
|  | LobbyHotel | LobbyHotel | Lobby, Hotel | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | LobbyMainEntry | LobbyMainEntry | Lobby, Main Entry | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | LockerDressingRoom | LockerDressingRoom | Locker/Dressing Room | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
|  | LoungeRecreational | LoungeRecreational | Lounge, Recreation | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
|  | ReligiousWorshipArea | ReligiousWorshipArea | Religious Worship Area | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Space occupancy
|  | TheaterMotionPicture | TheaterMotionPicture | Theater, Motion Picture | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | TheaterPerformance | TheaterPerformance | Theater, Performance | SpaceFunction |  |  | Assembly | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | TransportationFunction | TransportationFunction | Transportation Function | SpaceFunction |  |  | Assembly | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | ComputerRoom | ComputerRoom |  | SpaceFunction |  |  | DataCenter | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Space occupancy
| Health |  | Health |  | FunctionScheduleGroup
|  | MedicalAndClinicalCare | MedicalAndClinicalCare | Medical and Clinical Care | SpaceFunction |  | A room or area in a building that does not provide overnight patient care and that is used to provide physical and mental care through medical, dental, or psychological examination and treatment, including, but not limited to, laboratories and treatment spaces. | Health | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | HighRiseResidentialLivingSpace | HighRiseResidentialLivingSpace | High-Rise Residential Living Spaces | SpaceFunction |  |  | HighRiseResidential | GroupResidentialR2 | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Space occupancy
|  | PoliceStationFireStation | PoliceStationFireStation | Police Station and Fire Station | SpaceFunction |  |  | HighRiseResidential | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
|  | HotelFunctionArea | HotelFunctionArea | Hotel Function Area | SpaceFunction |  | A hotel room or area such as a hotel ballroom, meeting room, exhibit hall or conference room,together with pre-function areas and other spaces ancillary to its function. | HotelFunction | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
| Laboratory |  | Laboratory |  | FunctionScheduleGroup
|  | LaboratoryEquipmentRoom | LaboratoryEquipmentRoom |  | SpaceFunction |  |  | Laboratory |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
|  | LaboratoryScientific | LaboratoryScientific |  | SpaceFunction |  |  | Laboratory | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
| Manufacturing |  | Manufacturing |  | FunctionScheduleGroup
|  | AutoRepairArea | AutoRepairArea | Auto Repair Area | SpaceFunction |  |  | Manufacturing | GroupFactory | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy 90.1 2007 Table 9.6.1
|  | DryCleanCoinOperated | DryCleanCoinOperated | Dry Cleaning (Coin Operated) | SpaceFunction |  |  | Manufacturing | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | DryCleaningFullServiceCommercial | DryCleaningFullServiceCommercial | Dry Cleaning (Full Service Commercial) | SpaceFunction |  |  | Manufacturing | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | GeneralCommercialIndustrialWorkAreaHighBay | GeneralCommercialIndustrialWorkAreaHighBay | General Commercial and Industrial Work Areas, High Bay | SpaceFunction |  |  | Manufacturing | GroupFactory | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy 2007 90.1 Table 9.6.1
|  | GeneralCommercialIndustrialWorkAreaLowBay | GeneralCommercialIndustrialWorkAreaLowBay | General Commercial and Industrial Work Areas, Low Bay | SpaceFunction |  |  | Manufacturing | GroupFactory | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy 2007 90.1 Table 9.6.1
|  | GeneralCommercialIndustrialWorkAreaPrecision | GeneralCommercialIndustrialWorkAreaPrecision | General Commercial and Industrial Work Areas, Precision | SpaceFunction |  |  | Manufacturing | GroupFactory | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy 2007 90.1 Table 9.6.1
|  | Laundry | Laundry | Laundry | SpaceFunction |  |  | Manufacturing | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
| Office |  | Office |  | FunctionScheduleGroup
|  | CorridorRestroomStairsSupportArea | CorridorRestroomStairsSupportArea | Corridors, Restrooms, Stairs, and Support Areas | SpaceFunction |  |  | Office | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | FinancialTransactionsArea | FinancialTransactionsArea | Financial Transaction Area | SpaceFunction |  |  | Office | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | LibraryReadingArea | LibraryReadingArea | Library, Reading Areas | SpaceFunction |  |  | Office | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy 2007 90.1 Table 9.6.1
|  | LibraryStacks | LibraryStacks | Library, Stacks | SpaceFunction |  |  | Office | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy 2007 90.1 Table 9.6.1
|  | Office250FtOrLess | Office250FtOrLess | Office (250 square feet in floor area or less) | SpaceFunction |  |  | Office | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | OfficeGreaterThan250Ft | OfficeGreaterThan250Ft | Office (Greater than 250 square feet in floor area) | SpaceFunction |  |  | Office | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | VideoConferencingStudio | VideoConferencingStudio | Videoconferencing Studio | SpaceFunction |  |  | Office | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Space occupancy
|  | WaitingArea | WaitingArea | Waiting Area | SpaceFunction |  |  | Office | GroupBusiness | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
| Parking |  | Parking |  | FunctionScheduleGroup
|  | ParkingGarageAreaDaylightAdaptationZone | ParkingGarageAreaDaylightAdaptationZone | Parking Garage Area Daylight Adaptation Zones | SpaceFunction |  |  | Parking |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Space occupancy
|  | ParkingGarageAreaDedicatedRamp | ParkingGarageAreaDedicatedRamp | Parking Garage Area Dedicated Ramps | SpaceFunction |  |  | Parking |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Space occupancy
|  | ParkingGarageBuildingParkingArea | ParkingGarageBuildingParkingArea | Parking Garage Building, Parking Area | SpaceFunction |  |  | Parking |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2013 NR ACM: Space occupancy 90.1 2007 Table 9.6.1
|  | HousingPublicCommonAreaMultifamilyDormitory | HousingPublicCommonAreaMultifamilyDormitory | Housing, Public and Common Areas: Multi-family, Dormitory | SpaceFunction |  | Shared spaces in a building where group sleeping accommodations are provided in one room, or in a series of closely associated rooms, for persons not members of the same family group. | ResidentialWithOutSetback | GroupResidentialR2 | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | HousingPublicCommonAreaSeniorHousing | HousingPublicCommonAreaSeniorHousing | Housing, Public and Common Areas: Senior Housing | SpaceFunction |  | May include dining, reading, study, library or other community spaces and/or medical treatment or hospice facilities. | ResidentialWithOutSetback | GroupResidentialR2 | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM whole building occupancy COMNET Whole building occupancy 2013 NR ACM: Not included as a whole building occupancy type
|  | HotelMotelGuestRoom | HotelMotelGuestRoom | Hotel/Motel Guest Room | SpaceFunction |  |  | ResidentialWithSetback | GroupResidentialR1 | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy 90.1 2007 Table 9.6.1
| Restaurant |  | Restaurant |  | FunctionScheduleGroup
|  | BarCocktailLoungeCasinoArea | BarCocktailLoungeCasinoArea | Bar, Cocktail Lounge and Casino Areas | SpaceFunction |  |  | Restaurant | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | DiningArea | DiningArea | Dining Area | SpaceFunction |  |  | Restaurant | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
|  | KitchenetteResidentialKitchen | KitchenetteResidentialKitchen | Kitchenette or Residential Kitchen | SpaceFunction |  |  | Restaurant | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
| Retail |  | Retail |  | FunctionScheduleGroup
|  | BeautySalonArea | BeautySalonArea | Beauty Salon Area | SpaceFunction |  |  | Retail | GroupMercantile | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | GrocerySalesArea | GrocerySalesArea | Grocery Sales Areas | SpaceFunction |  | A room or area, in a building that has as its primary purpose the sale of foodstuffs requiring additional preparation prior to consumption. | Retail | GroupMercantile | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | MallAndAtria | MallAndAtria | Malls and Atria | SpaceFunction |  |  | Retail | GroupMercantile | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | RetailMerchandiseSalesWholesaleShowroom | RetailMerchandiseSalesWholesaleShowroom | Retail Merchandise Sales, Wholesale Showroom | SpaceFunction |  | A room or area in which the primary activity is the sale of merchandise. This includes wholesale showroom is a room where samples of merchandise are displayed | Retail | GroupMercantile | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
| School |  | School |  | FunctionScheduleGroup
|  | ClassroomLectureTrainingVocationalAreas | ClassroomLectureTrainingVocationalArea | Classroom, Lecture, Training, Vocational Areas | SpaceFunction |  |  | School | GroupEducational | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy COMNET: Space occupancy 2013 NR ACM: Space occupancy
| Warehouse |  | Warehouse |  | FunctionScheduleGroup
|  | CommercialIndustrialStorageArea | CommercialIndustrialStorageArea | Commercial and Industrial Storage Areas (conditioned or unconditioned) | SpaceFunction |  |  | Warehouse |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | CommercialIndustrialStorageAreaRefrigerated | CommercialIndustrialStorageAreaRefrigerated | Commercial and Industrial Storage Areas (refrigerated) | SpaceFunction |  |  | Warehouse |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | ElectricalMechancialTelephoneRoom | ElectricalMechancialTelephoneRoom | Electrical, Mechanical, Telephone Rooms | SpaceFunction |  |  | Warehouse |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential) | 2008 NR ACM Space occupancy 2013 NR ACM: Space occupancy
|  | ExerciseRoom | ExerciseRoom | Exercise Room | SpaceFunction |  |  |  | GroupAssembly | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | GymnasiumSportsArena | GymnasiumSportsArena | Gymnasium/Sports Arena | SpaceFunction |  |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | NurseriesForChildrenDayCare | NurseriesForChildrenDayCare | Nurseries for Children - Day Care | SpaceFunction |  |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)
|  | UnleasedTenantArea | UnleasedTenantArea | Unleased Tenant Area | SpaceFunction |  |  |  |  | SpaceOccupancyType | NonResidential (includes Hotel, Motel and High-rise Residential)

## HvacObjects
CBECC NR Term | CBECC NR Term Short Form | CBECC NR Building Parent | CBECC NR Parent | T24Objects NR CBECC Parent | Properties | Properties Short Form | Library Object | Compliance Use | Components | Definition | Standards Reference | Compliance Reporting Properties | Collapsed From
AirSegment | AirSeg |  | AirSys |  | Name | Name |  | Optional | CoilClg | A duct that carries supply, return, makeup, relief or exhaust air in an AirSystem. | 2013 NR ACM: 5.7.5 Cooling Systems
[5 empty] | Path | Path |  |  | CoilHtg
[5 empty] | Type | Type |  |  | EvapClr
Fan
AirSystem | AirSys | Bldg |  |  | ControlSystemType | CtrlSysType |  | Optional | AirSeg | Provides conditioned air or ventilation to one or more thermal zones in a building. | 2013 NR ACM 5.6 HVAC Zone Level Systems | AcceptanceTestReq
[5 empty] | ControlZoneReference | CtrlZnRef |  |  | HtRcvry |  |  | HERSDuctReq
[5 empty] | CoolResetOutdoorHigh | ClRstOutdrHi |  |  | OACtrl |  |  | HERSDuctTested
[5 empty] | CoolResetOutdoorLow | ClRstOutdrLow |  |  | TrmlUnit |  |  | NRCAMch02A
[5 empty] | CoolResetSupplyHigh | ClRstSupHi | [5 empty] | NRCAMch03A
[5 empty] | CoolResetSupplyLow | ClRstSupLow | [5 empty] | NRCAMch04H
[5 empty] | CoolingControl | ClgCtrl | [5 empty] | NRCAMch05A
[5 empty] | CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp | [5 empty] | NRCAMch06A
[5 empty] | CoolingFixedSupplyAirTemperature | ClgFixedSupTemp | [5 empty] | NRCAMch07A
[5 empty] | CoolingSetPointScheduleReference | ClgSetptSchRef | [5 empty] | NRCAMch08A
[5 empty] | Count | Cnt | [5 empty] | NRCAMch09A
[5 empty] | Description | Desc | [5 empty] | NRCAMch10A
[5 empty] | DuctInsulation | DuctIns | [5 empty] | NRCAMch11A
[5 empty] | DuctLocation | DuctLctn | [5 empty] | NRCAMch12A
[5 empty] | DuctStatus | DuctStatus | [5 empty] | NRCAMch13A
[5 empty] | ExhaustControlMethod | ExhCtrlMthd | [5 empty] | NRCAMch14A
[5 empty] | ExhaustOperationMode | ExhOperMode | [5 empty] | NRCAMch15A
[5 empty] | ExhaustSystemType | ExhSysType | [5 empty] | NRCAMch16A
[5 empty] | FanControl | FanCtrl | [5 empty] | NRCAMch17A
[5 empty] | FanPosition | FanPos | [5 empty] | NRCAMch18A
[5 empty] | HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp
[5 empty] | HeatingFixedSupplyTemperature | HtgFixedSupTemp
[5 empty] | HeatingSetPointScheduleReference | HtgSetPtSchRef
[5 empty] | IsAllOutsideAir | IsAllOA
[5 empty] | IsComplexSystem | IsComplexSystem
[5 empty] | Name | Name
[5 empty] | NightCycleFanControl | NightCycleFanCtrl
[5 empty] | OptimumStart | OptStart
[5 empty] | ReheatControlMethod | ReheatCtrlMthd
[5 empty] | Status | Status
[5 empty] | SubType | SubType
[5 empty] | Type | Type
Boiler | Blr |  | FluidSys |  | AFUE | AFUE |  | Optional | Pump | A device for generating steam or hot water, which consists of a source of heat and a chamber that holds water which absorbs the heat. The steam or hot water is then recirculated out of the boiler for use in FluidSystem | 2013 NR ACM: 5.8.1 Boilers;
[5 empty] | CapacityRated | CapRtd
[5 empty] | CombustionEfficiency | CombEff
[5 empty] | DraftFanHorsePower | DraftFanHp
[5 empty] | DraftType | DraftType
[5 empty] | EIR | EIR
[5 empty] | EnteringTemperatureDesign | EntTempDsgn
[5 empty] | FluidSegmentInReference | FluidSegInRef
[5 empty] | FluidSegmentOutReference | FluidSegOutRef
[5 empty] | FuelFullLoad | FuelFullLd
[5 empty] | FuelSource | FuelSrc
[5 empty] | HasBypass | HasBypass
[5 empty] | HeatLoss | HtLoss
[5 empty] | LeavingTemperatureDesign | LvgTempDsgn
[5 empty] | Name | Name
[5 empty] | ParasiticLoad | ParasiticLd
[5 empty] | Status | Status
[5 empty] | ThermalEfficiency | ThrmlEff
[5 empty] | Type | Type
[5 empty] | UnloadRatioMinimum | UnldRatMin
Chiller | Chlr |  | FluidSys |  | AuxiliaryPower | AuxPwr |  | Optional | Pump | Cooling equipment that produces chilled water for cooling systems. A chiller plant consists one or more chillers, evaporator and condenser pumps, and cooling towers. | 2013 NR ACM: 5.8.2 Chillers
[5 empty] | COP | COP
[5 empty] | CapacityRated | CapRtd
[5 empty] | CondenserFluidSegmentInReference | CndsrInRef
[5 empty] | CondenserFluidSegmentOutReference | CndsrOutRef
[5 empty] | CondenserPowerRated | CndsrPwrRtd
[5 empty] | CondenserType | CndsrType
[5 empty] | DesignGeneratorFluidDeltaTemperature | DsgnGenFluidDelT
[5 empty] | EER | EER
[5 empty] | EnableOnThermalEnergyStorageDischarge | EnableOnThrmlEngyStorDischrg
[5 empty] | EnteringGeneratorTemperatureDesign | EntGenTempDsgn
[5 empty] | EnteringTemperatureDesign | EntTempDsgn
[5 empty] | EnteringTemperatureRated | EntTempRtd
[5 empty] | EvaporatorFluidSegmentInReference | EvapInRef
[5 empty] | EvaporatorFluidSegmentOutReference | EvapOutRef
[5 empty] | EvaporatorHasBypass | EvapHasBypass
[5 empty] | FuelSource | FuelSrc
[5 empty] | GeneratorFluidFlowCapacity | GenFluidFlowCap
[5 empty] | GeneratorFluidSegmentInReference | GenFluidSegInRef
[5 empty] | GeneratorFluidSegmentOutReference | GenFluidSegOutRef
[5 empty] | IPLVCOP | IPLVCOP
[5 empty] | IPLVEER | IPLVEER
[5 empty] | IPLVKwPerTon | IPLVKwPerTon
[5 empty] | KwPerTon | KwPerTon
[5 empty] | LeavingTemperatureDesign | LvgTempDsgn
[5 empty] | LeavingTemperatureRated | LvgTempRtd
[5 empty] | Name | Name
[5 empty] | PartLoadRatioMinimum | PLRMin
[5 empty] | Status | Status
[5 empty] | Type | Type
[5 empty] | UnloadRatioMinimum | UnldRatMin
CoilCooling | CoilClg |  | AirSeg |  | AuxiliaryPower | AuxPwr |  | Optional |  | An arrangement of pipe or tubing used in heating, cooling and refrigeration systems. Coils carry a heated or cooled medium and air or water surrounds the coil to absorb heat from the medium or reject heat into the medium. | 2013 NR ACM: 5.7.5 Cooling Systems
|  |  | ZnSys |  | BypassMinimumEfficiencyCheck | BypassMinEffCheck
[5 empty] | CapacityTotalGrossRated | CapTotGrossRtd
[5 empty] | CapacityTotalNetRated | CapTotNetRtd
[5 empty] | CapacityTotalRatedStageFraction | CapTotRtdStageFrac
[5 empty] | CoilHeadDesign | CoilHdDsgn
[5 empty] | CondenserType | CndsrType
[5 empty] | DXCrankcaseControlTemperature | DXCrankcaseCtrlTemp
[5 empty] | DXCrankcaseHeatCapacity | DXCrankcaseHtCap
[5 empty] | DXEER | DXEER
[5 empty] | DXIEER | DXIEER
[5 empty] | DXSEER | DXSEER
[5 empty] | FluidFlowRateDesign | FluidFlowRtDsgn
[5 empty] | FluidSegmentInReference | FluidSegInRef
[5 empty] | FluidSegmentOutReference | FluidSegOutRef
[5 empty] | MinimumHotGasRatio | MinHotGasRat
[5 empty] | Name | Name
[5 empty] | NumberCoolingStages | NumClgStages
[5 empty] | Type | Type
CoilHeating | CoilHtg |  | AirSeg |  | AuxilliaryPower | AuxPwr |  | Optional |  |  | 2013 NR ACM: 5.7.6 Heating Systems
|  |  | TrmlUnit |  | BypassMinimumEfficiencyCheck | BypassMinEffCheck
|  |  | ZnSys |  | CapacityTotalGrossRated | CapTotGrossRtd
[5 empty] | CapacityTotalNetRated | CapTotNetRtd
[5 empty] | CoilHeadDesign | CoilHdDsgn
[5 empty] | CondenserType | CndsrType
[5 empty] | FluidFlowRateDesign | FluidFlowRtDsgn
[5 empty] | FluidSegmentInReference | FluidSegInRef
[5 empty] | FluidSegmentOutReference | FluidSegOutRef
[5 empty] | FuelSource | FuelSrc
[5 empty] | FurnaceAFUE | FurnAFUE
[5 empty] | FurnaceIgnitionType | FurnIgnType
[5 empty] | FurnacePilotFuelInput | FurnPilotFuelInp
[5 empty] | FurnaceThermalEfficiency | FurnThrmlEff
[5 empty] | HeatPumpCOP | HtPumpCOP
[5 empty] | HeatPumpCompressorLockoutTemperature | HtPumpCprsrLockoutTemp
[5 empty] | HeatPumpCrankcaseControlTemperature | HtPumpCrankcaseCtrlTemp
[5 empty] | HeatPumpCrankcaseHeatCapacity | HtPumpCrankcaseHtCap
[5 empty] | HeatPumpDefrostControl | HtPumpDefCtrl
[5 empty] | HeatPumpDefrostHeatCapacity | HtPumpDefHtCap
[5 empty] | HeatPumpDefrostHeatSource | HtPumpDefHtSrc
[5 empty] | HeatPumpHSPF | HtPumpHSPF
[5 empty] | HeatPumpSupplementalCoilHeatingReference | HtPumpSuppCoilHtgRef
[5 empty] | HeatPumpSupplementalTemperature | HtPumpSuppTemp
[5 empty] | Name | Name
[5 empty] | Type | Type
EvaporativeCooler | EvapClr |  | AirSeg |  | Effectiveness | Eff |  | Optional |  | Equipment that pre-cools the outside air that is brought into the building. It may be used with any type of cooling system that brings in outside air. | 2013 NR ACM 5.7.5.3 Evaporative Cooler
[5 empty] | IndirectDewPointEffectiveness | IndirectDewPtEff
[5 empty] | Name | Name
[5 empty] | PumpPower | PumpPwr
[5 empty] | SecondaryAirSource | SecAirSrc
[5 empty] | SecondaryFanFlowCapacity | SecFanFlowCap
[5 empty] | SecondaryFanTotalEfficiency | SecFanTotEff
[5 empty] | SecondaryFanTotalStaticPressure | SecFanTotStaticPress
[5 empty] | Type | Type
Fan | Fan |  | AirSeg |  | CentrifugalType | CentType |  | Optional |  |  | 2013 NR ACM 5.7.3 Fan Systems
|  |  | TrmlUnit |  | Classification | Class
|  |  | ZnSys |  | ControlMethod | CtrlMthd
[5 empty] | FlowCapacity | FlowCap
[5 empty] | FlowEfficiency | FlowEff
[5 empty] | FlowMinimum | FlowMin
[5 empty] | ModelingMethod | ModelingMthd
[5 empty] | MotorBHP | MtrBHP
[5 empty] | MotorEfficiency | MtrEff
[5 empty] | MotorHP | MtrHP
[5 empty] | MotorPoleCount | MtrPoleCnt
[5 empty] | MotorPosition | MtrPos
[5 empty] | MotorType | MtrType
[5 empty] | Name | Name
[5 empty] | TotalStaticPressure | TotStaticPress
FluidSegment | FluidSeg |  | FluidSys |  | Name | Name |  | Optional | Pump | A pipe that carries supply, return, makeup, or discharge fluid in an FluidSystem.
[5 empty] | PrimarySegmentReference | PriSegRef
[5 empty] | Source | Src
[5 empty] | Type | Type
FluidSystem | FluidSys |  |  | Project | AngleFromTrueNorth | AngleFromTrueNorth |  | Optional | Blr | Provides conditioned fluid for a heating or cooling system, or service water heating system. | 2013 NR ACM 5.8 HVAC Primary Systems; 5.9.1 Water Heating | NRCAMch02A | SolarWaterHeatingProperties
[5 empty] | AnnualSolarFraction | AnnualSolFrac |  |  | Chlr |  |  | NRCAMch03A
[5 empty] | Area | Area |  |  | FluidSeg |  |  | NRCAMch04H
[5 empty] | AvailabiltyScheduleReference | AvailSchRef |  |  | HX |  |  | NRCAMch05A
[5 empty] | Brand | Brand |  |  | HtRej |  |  | NRCAMch06A
[5 empty] | CentralSystem | CentralSys |  |  | ThrmlEngyStor |  |  | NRCAMch07A
[5 empty] | CollectorType | CollectorType |  |  | WtrHtr |  |  | NRCAMch08A
[5 empty] | ControlType | CtrlType | [5 empty] | NRCAMch09A
[5 empty] | CoolingSupplyTemperature | ClgSupTemp | [5 empty] | NRCAMch10A
[5 empty] | Count | Cnt | [5 empty] | NRCAMch11A
[5 empty] | Description | Desc | [5 empty] | NRCAMch12A
[5 empty] | DesignSupplyWaterTemperature | DsgnSupWtrTemp | [5 empty] | NRCAMch13A
[5 empty] | DesignSupplyWaterTemperatureDeltaT | DsgnSupWtrTempDelT | [5 empty] | NRCAMch14A
[5 empty] | EquipmentList1Name | EquipList1Name | [5 empty] | NRCAMch15A
[5 empty] | EquipmentList2Name | EquipList2Name | [5 empty] | NRCAMch16A
[5 empty] | EquipmentList3Name | EquipList3Name | [5 empty] | NRCAMch17A
[5 empty] | EquipmentList4Name | EquipList4Name | [5 empty] | NRCAMch18A
[5 empty] | FixedSupplyTemperature | FixedSupTemp
[5 empty] | Fluid | Fluid
[5 empty] | HeatingDesignSupplyWaterTemperature | HtgDsgnSupWtrTemp
[5 empty] | HeatingFixedSupplyTemperature | HtgFixedSupTemp
[5 empty] | HeatingSupplyTemperature | HtgSupTemp
[5 empty] | HeatingTemperatureSetPointScheduleReference | HtgTempSetptSchRef
[5 empty] | HotWaterSupplyTemperature | HotWtrSupTemp
[5 empty] | LoadRangeLimit | LdRngLim
[5 empty] | Manufacturer | Manufacturer
[5 empty] | ModelNumber | ModelNum
[5 empty] | Name | Name
[5 empty] | NameOfProgramUsed | NameOfProgramUsed
[5 empty] | NumberOfIdenticalDwellingUnits | NumOfIdenticalDwellingUnits
[5 empty] | RatedEfficiencyCurveIntercept | RatedEffCurveIntercept
[5 empty] | RatedEfficiencyCurveSlope | RatedEffCurveSlope
[5 empty] | ResetOutdoorHigh | RstOutdrHi
[5 empty] | ResetOutdoorLow | RstOutdrLow
[5 empty] | ResetSupplyHigh | RstSupHi
[5 empty] | ResetSupplyLow | RstSupLow
[5 empty] | SRRCCertificationNumber | SRRCCertNum
[5 empty] | SecondaryTankVolume | SecondaryTankVol
[5 empty] | SlopeFromHorizontal | SlopeFromHorizontal
[5 empty] | SolarCollectorCount | SolCollectorCnt
[5 empty] | Status | Status
[5 empty] | TemperatureControl | TempCtrl
[5 empty] | TemperatureSetPointScheduleReference | TempSetptSchRef
[5 empty] | Type | Type
[5 empty] | Version | Version
[5 empty] | WaterHeaterTankVolume | WtrHtrTankVol
[5 empty] | WetBulbApproach | WetBulbApproach
HeatExchanger | HX |  | FluidSys |  | CapacityRated | CapRtd |  | Optional |  |  | 2013 NR ACM 5.8.4 Water-side Economizers
[5 empty] | ChilledWaterEnteringTemperatureDesign | CHWEntTempDsgn
[5 empty] | ChilledWaterFluidSegmentInReference | CHWFluidSegInRef
[5 empty] | ChilledWaterFluidSegmentOutReference | CHWFluidSegOutRef
[5 empty] | ChilledWaterLeavingTemperatureDesign | CHWLvgTempDsgn
[5 empty] | CondenserWaterFluidSegmentInReference | CWFluidSegInRef
[5 empty] | CondenserWaterFluidSegmentOutReference | CWFluidSegOutRef
[5 empty] | CondenserWaterLeavingTemperatureDesign | CWLvgTempDsgn
[5 empty] | EconomizerIntegration | EconoIntegration
[5 empty] | Name | Name
[5 empty] | Status | Status
[5 empty] | Type | Type
HeatRecovery | HtRcvry |  | AirSys |  | AuxiliaryPower | AuxPwr
[5 empty] | CoolingLatentEffectiveness100 | ClgLatEff100
[5 empty] | CoolingLatentEffectiveness75 | ClgLatEff75
[5 empty] | CoolingSensibleEffectiveness100 | ClgSensEff100
[5 empty] | CoolingSensibleEffectiveness75 | ClgSensEff75
[5 empty] | CoolingTotalEffectiveness100 | ClgTotEff100
[5 empty] | CoolingTotalEffectiveness75 | ClgTotEff75
[5 empty] | DefrostControl | DefrostCtrl
[5 empty] | DefrostControlTemperature | DefrostCtrlTemp
[5 empty] | EconomizerLockout | EconoLockout
[5 empty] | FixedSupplyTemperature | FixedSupTemp
[5 empty] | HasHeatExchangerBypass | HasHXBypass
[5 empty] | HeatingLatentEffectiveness100 | HtgLatEff100
[5 empty] | HeatingLatentEffectiveness75 | HtgLatEff75
[5 empty] | HeatingSensibleEffectiveness100 | HtgSensEff100
[5 empty] | HeatingSensibleEffectiveness75 | HtgSensEff75
[5 empty] | HeatingTotalEffectiveness100 | HtgTotEff100
[5 empty] | HeatingTotalEffectiveness75 | HtgTotEff75
[5 empty] | RecoveryType | RcvryType
[5 empty] | SupplyFlowRated | SupFlowRtd
[5 empty] | TemperatureControl | TempCtrl
[5 empty] | TemperatureSetpointScheduleReference | TempSetptSchRef
[5 empty] | Type | Type
HeatRejection | HtRej |  | FluidSys |  | AirFlowCapacity | AirFlowCap |  | Optional | Pump
[5 empty] | CapacityRated | CapRtd
[5 empty] | CellCount | CellCnt
[5 empty] | DesignWBTemperature | DsgnWBTemp
[5 empty] | EnteringTemperatureDesign | EntTempDsgn
[5 empty] | FanType | FanType
[5 empty] | FluidSegmentInReference | FluidSegInRef
[5 empty] | FluidSegmentOutReference | FluidSegOutRef
[5 empty] | LeavingTemperatureDesign | LvgTempDsgn
[5 empty] | LowSpeedAirFlowRatio | LowSpdAirFlowRat
[5 empty] | MinimumSpeedRatio | MinSpdRat
[5 empty] | ModulationControl | ModCtrl
[5 empty] | Name | Name
[5 empty] | Status | Status
[5 empty] | TotalFanHP | TotFanHP
[5 empty] | Type | Type
[5 empty] | WaterFlowCapacity | WtrFlowCap
OutsideAirControl | OACtrl |  | AirSys |  | AirSegmentReturnReference | AirSegRetRef |  | Optional |  | The outside air control and its supply segment must have the same air sytem parent. | 2013 NR ACM 5.7.4 Outdoor Air Control and Economizers
[5 empty] | AirSegmentSupplyReference | AirSegSupRef
[5 empty] | EconomizerControlMethod | EconoCtrlMthd
[5 empty] | EconomizerHighTemperatureLockout | EconoHiTempLockout
[5 empty] | EconomizerIntegration | EconoIntegration
[5 empty] | EconomizerLowTemperatureLockout | EconoLowTempLockout
[5 empty] | HeatRecoveryReference | HtRcvryRef
[5 empty] | Name | Name
Pump | Pump |  | Blr |  | FlowCapacity | FlowCap |  | Optional |  |  | 2013 NR ACM 5.8.5 Pumps
|  |  | Chlr |  | FlowMinimum | FlowMin
|  |  | FluidSeg |  | ImpellerEfficiency | ImpellerEff
|  |  | HtRej |  | MinimumSpeedRatio | MinSpdRat
|  |  | ThrmlEngyStor |  | ModelingMethod | ModelingMthd
|  |  | WtrHtr |  | MotorEfficiency | MtrEff
[5 empty] | MotorHP | MtrHP
[5 empty] | Name | Name
[5 empty] | OperationControl | OperCtrl
[5 empty] | SpeedControl | SpdCtrl
[5 empty] | Status | Status
[5 empty] | TotalHead | TotHd
ResidentialDHWSystem | ResDHWSys |  |  | Project | AngleFromTrueNorth | AngleFromTrueNorth | [5 empty] | BuriedReport | SolarWaterHeatingProperties
[5 empty] | AnnualSolarFraction | AnnualSolFrac | [5 empty] | OutsideReport
[5 empty] | Area | Area | [5 empty] | PlenumReport
[5 empty] | BaselineResidentialWaterHeaterReference | BaseResWtrHtrRef | [5 empty] | SolFracRpt
[5 empty] | Brand | Brand
[5 empty] | CentralSystem | CentralSys
[5 empty] | CollectorType | CollectorType
[5 empty] | DistributionType | DistType
[5 empty] | Fluid | Fluid
[5 empty] | LoopCount | LpCnt
[5 empty] | LoopPipeInsulationThickness | LpPipeInsThkns
[5 empty] | Manufacturer | Manufacturer
[5 empty] | Manufacturer | Manufacturer
[5 empty] | ModelNumber | ModelNum
[5 empty] | Multiplier | Mult
[5 empty] | Name | Name
[5 empty] | NameOfProgramUsed | NameOfProgramUsed
[5 empty] | NumberOfIdenticalDwellingUnits | NumOfIdenticalDwellingUnits
[5 empty] | PipeLocation | PipeLctn
[5 empty] | PumpBreakHorsepower | PumpBHP
[5 empty] | PumpEfficiency | PumpEff
[5 empty] | PumpPower | PumpPwr
[5 empty] | RatedEfficiencyCurveIntercept | RatedEffCurveIntercept
[5 empty] | RatedEfficiencyCurveSlope | RatedEffCurveSlope
[5 empty] | SRRCCertificationNumber | SRRCCertNum
[5 empty] | SecondaryTankVolume | SecondaryTankVol
[5 empty] | SlopeFromHorizontal | SlopeFromHorizontal
[5 empty] | SolarCollectorCount | SolCollectorCnt
[5 empty] | SolarFractionFluidSystemName | SolFracFluidSysName
[5 empty] | Status | Status
[5 empty] | SupplementalStorageTankVolume | SuppStorTankVol
[5 empty] | SystemStoryCount | SysStoryCnt
[5 empty] | TotalInputRating | TotInpRating
[5 empty] | TotalTankVolume | TotTankVol
[5 empty] | Type | Type
[5 empty] | Version | Version
[5 empty] | WaterHeaterTankVolume | WtrHtrTankVol
ResidentialWaterHeater | ResWtrHtr |  | ResDHWSys |  | AmbientCondition | AmbCond
[5 empty] | CompressorZone | CprsrZn
[5 empty] | Count | Cnt
[5 empty] | ElectricMiniTank | ElecMiniTank
[5 empty] | ElectricMiniTankPower | ElecMiniTankPwr
[5 empty] | ElementType | ElementType
[5 empty] | EnergyFactor | EngyFac
[5 empty] | FirstHourRating | FirstHrRating
[5 empty] | FlowRate | FlowRt
[5 empty] | HeatPumpWaterHeaterBrand | HPWHBrand
[5 empty] | HeatPumpWaterHeaterModel | HPWHModel
[5 empty] | HeatPumpWaterHeaterNEEARated | HtPumpWtrHtrNEEARtd
[5 empty] | InputRating | InpRating
[5 empty] | InputRatingElectric | InpRatingElec
[5 empty] | IsUniformEnergyFactorRated | IsUEFRtd
[5 empty] | Name | Name
[5 empty] | RecoveryEfficiency | RE
[5 empty] | StandbyLossFraction | StdbyLossFrac
[5 empty] | Status | Status
[5 empty] | TankCategory | TankCat
[5 empty] | TankExteriorInsulationRValue | TankExtInsR
[5 empty] | TankInteriorInsulationRValue | TankIntInsR
[5 empty] | TankVolume | TankVol
[5 empty] | TankZone | TankZn
[5 empty] | ThermalEfficiency | ThrmlEff
[5 empty] | UniformEnergyFactor | UEF
TerminalUnit | TrmlUnit |  | AirSys |  | Count | Cnt |  | Optional | CoilHtg |  | 2013 NR ACM 5.6 HVAC Zone Level Systems
[5 empty] | HeatingAirFlowMaximum | HtgAirFlowMax |  |  | Fan
[5 empty] | InducedAirZoneReference | InducedAirZnRef
[5 empty] | InductionRatio | InductionRat
[5 empty] | Name | Name
[5 empty] | ParallelBoxFanFlowFraction | ParallelBoxFanFlowFrac
[5 empty] | PrimaryAirFlowMaximum | PriAirFlowMax
[5 empty] | PrimaryAirFlowMinimum | PriAirFlowMin
[5 empty] | PrimaryAirSegmentReference | PriAirSegRef
[5 empty] | ReheatControlMethod | ReheatCtrlMthd
[5 empty] | Status | Status
[5 empty] | TotalAirFlow | TotAirFlow
[5 empty] | Type | Type
[5 empty] | ZoneServedReference | ZnServedRef
ThermalEnergyStorage | ThrmlEngyStor |  | FluidSys |  | CapacityRated | CapRtd |  |  | Pump
[5 empty] | ChargeFluidSegmentInReference | ChrgFluidSegInRef
[5 empty] | ChargeFluidSegmentOutReference | ChrgFluidSegOutRef
[5 empty] | DischargeFluidSegmentInReference | DischrgFluidSegInRef
[5 empty] | DischargeFluidSegmentOutReference | DischrgFluidSegOutRef
[5 empty] | DischargePriority | DischargePriority
[5 empty] | ModeScheduleReference | ModeSchRef
[5 empty] | StorageCapacity | StorCap
[5 empty] | StorageLocation | StorLctn
[5 empty] | StorageLocationSimulated | StorLctnSim
[5 empty] | StorageZoneReference | StorageZoneReference
[5 empty] | TankHeight | TankHgt
[5 empty] | TankLengthToWidthRatio | TankLenToWdRat
[5 empty] | TankNodeCount | TankNodeCnt
[5 empty] | TankRValue | TankR
[5 empty] | TankShape | TankShape
[5 empty] | Type | Type
ThermalZone | ThrmlZn | Bldg |  |  | CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp |  | Required |  | A collection of spaces within a building having sufficiently similar space conditioning requirements so that those conditions could be maintained with a single thermal controlling device. | Zone is a space or group of spaces that have the same space conditioning requirements and are controlled by a single thermostat. 2013 NR ACM Uses Thermal Block for this object but same definition. 2013 NR ACM 5.3 Thermal Blocks | AddClgSys
[5 empty] | CoolingDesignSupplyAirTemperatureDifference | ClgDsgnSupAirTempDiff | [5 empty] | HasNoClg
[5 empty] | DaylightingControlLightingFraction1 | DayltgCtrlLtgFrac1 | [5 empty] | HasUnknownHVAC
[5 empty] | DaylightingControlLightingFraction2 | DayltgCtrlLtgFrac2 | [5 empty] | VentStd
[5 empty] | DaylightingControlType | DayltgCtrlType
[5 empty] | DaylightingMinimumDimmingLightFraction | DayltgMinDimLtgFrac
[5 empty] | DaylightingMinimumDimmingPowerFraction | DayltgMinDimPwrFrac
[5 empty] | DaylightingNumberOfControlSteps | DayltgNumCtrlSteps
[5 empty] | Description | Desc
[5 empty] | ExhaustSystemReference | ExhSysRef
[5 empty] | HVACZoneCount | HVACZnCnt
[5 empty] | HeatingDesignMaximumFlowFraction | HtgDsgnMaxFlowFrac
[5 empty] | HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp
[5 empty] | HeatingDesignSupplyAirTemperatureDifference | HtgDsgnSupAirTempDiff
[5 empty] | Name | Name
[5 empty] | OperableWindowInterlock | OperableWinInterlock
[5 empty] | OperableWindowsHaveInterlock | OperableWinHaveInterlock
[5 empty] | PrimaryAirConditioningSystemPriority | PriAirCondgSysPriority
[5 empty] | PrimaryAirConditioningSystemReference | PrimAirCondgSysRef
[5 empty] | ReturnPlenumZoneReference | RetPlenumZnRef
[5 empty] | SupplyPlenumZoneReference | SupPlenumZnRef
[5 empty] | Type | Type
[5 empty] | VentilationControlMethod | VentCtrlMthd
[5 empty] | VentilationSource | VentSrc
[5 empty] | VentilationSpecificationMethod | VentSpecMthd
[5 empty] | VentilationStandardDescription | VentStdDesc
[5 empty] | VentilationSystemPriority | VentSysPriority
[5 empty] | VentilationSystemReference | VentSysRef
WaterHeater | WtrHtr |  | FluidSys |  | CapacityRated | CapRtd |  | Optional | Pump |  | 2013 NR ACM 5.9.1 Water Heating
[5 empty] | CompressorLocation | CprsrLoc
[5 empty] | CompressorZoneReference | CprsrZnRef
[5 empty] | Count | Cnt
[5 empty] | DraftFanPower | DraftFanPwr
[5 empty] | ElectricalIgnition | ElecIgnit
[5 empty] | EnergyFactor | EF
[5 empty] | FirstHourRating | FirstHrRating
[5 empty] | FlowRate | FlowRt
[5 empty] | FluidSegmentMakeupReference | FluidSegMakeupRef
[5 empty] | FluidSegmentOutReference | FluidSegOutRef
[5 empty] | FluidSystemCount | FluidSysCnt
[5 empty] | FuelSource | FuelSrc
[5 empty] | InputPower | InpPwr
[5 empty] | MinimumCapacity | MinCap
[5 empty] | Name | Name
[5 empty] | RecoveryEfficiency | RE
[5 empty] | StandbyLossFraction | StdbyLossFrac
[5 empty] | Status | Status
[5 empty] | StorageCapacity | StorCap
[5 empty] | StorageCapacitySimulated | StorCapSim
[5 empty] | StorageLocation | StorLoc
[5 empty] | StorageZoneReference | StorZnRef
[5 empty] | TankHeightSimulated | TankHgtSim
[5 empty] | ThermalEfficiency | ThrmlEff
[5 empty] | Type | Type
[5 empty] | UniformEnergyFactor | UEF
ZoneSystem | ZnSys | Bldg |  |  | CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp |  |  | CoilClg | Provides conditioned air or ventilation to one or more thermal zones in a building. | 2013 NR ACM 5.6 HVAC Zone Level Systems | AcceptanceTestReq
[5 empty] | Count | Cnt |  |  | CoilHtg |  |  | HERSDuctReq
[5 empty] | Description | Desc |  |  | Fan |  |  | HERSDuctTested
[5 empty] | DuctInsulation | DuctIns | [5 empty] | NRCAMch02A
[5 empty] | DuctLocation | DuctLctn | [5 empty] | NRCAMch03A
[5 empty] | DuctStatus | DuctStatus | [5 empty] | NRCAMch04H
[5 empty] | ExhaustControlMethod | ExhCtrlMthd | [5 empty] | NRCAMch05A
[5 empty] | ExhaustOperationMode | ExhOperMode | [5 empty] | NRCAMch06A
[5 empty] | ExhaustSystemType | ExhSysType | [5 empty] | NRCAMch07A
[5 empty] | FanControl | FanCtrl | [5 empty] | NRCAMch08A
[5 empty] | HVACAutoSizing | HVACAutoSizing | [5 empty] | NRCAMch09A
[5 empty] | HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp | [5 empty] | NRCAMch10A
[5 empty] | IsComplexSystem | IsComplexSystem | [5 empty] | NRCAMch11A
[5 empty] | Name | Name | [5 empty] | NRCAMch12A
[5 empty] | Status | Status | [5 empty] | NRCAMch13A
[5 empty] | SubType | SubType | [5 empty] | NRCAMch14A
[5 empty] | Type | Type | [5 empty] | NRCAMch15A
NRCAMch16A
NRCAMch17A
NRCAMch18A

## HvacObjProps
Object | CBECC NR Property | CBECC NR Property Short Form | DataType | Units | HvacEnumerations | CBECC NR Array | XSD ELEMATTRIB minOccurs | XSD ELEMATTRIB maxOccurs | XSD RESTRICT minInclusive | XSD RESTRICT maxInclusive | Compliance Use | Referenced Objects | Referenced Building Objects | XSD Base Type | Definition | Standards Reference | Calculations And Rules | CBECC NR Different Data Type
AirSegment
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| Path | Path | enumerated list | none | Direct | [5 empty] | Defaulted
Ducted
PlenumZones
| Type | Type | enumerated list | none | Connector | [5 empty] | Compulsory |  |  |  |  | AirSegmentType
ExhaustSegment
OutsideAir
Relief
Return
Supply
AirSystem
| ControlSystemType | CtrlSysType | enumerated list | none | DDCToZone | [5 empty] | Defaulted |  |  |  | The type of control system for multizone HVAC systems and their related equipment.This input affects the proposed design system specification for zone levelcontrols, supply air temperature reset controls, ventilation controls and fanand pump static pressure part-load curves. | 2013 NR ACM: 5.6.5.1, 5.7.2.1 The type of control system for multizone HVAC systems and their related equipment.This input affects the proposed design system specification for zone levelcontrols, supply air temperature reset controls, ventilation controls and fanand pump static pressure part-load curves.
Other
| ControlZoneReference | CtrlZnRef | reference | none | [6 empty] | CondRequired | ThermalZone
| CoolingControl | ClgCtrl | enumerated list | none | Fixed | [5 empty] | Defaulted |  |  |  | Defines the cooling supply air temperature control method used for systems with cooling coils | 2013 NR ACM: 5.7.2.2 Cooling Control
FixedDualSetpoint
NoSATControl
OutsideAirReset
Scheduled
WarmestResetFlowFirst
WarmestResetTemperatureFirst
| CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
| CoolingFixedSupplyAirTemperature | ClgFixedSupTemp | decimal | F | [6 empty] | Defaulted
| CoolingSetPointScheduleReference | ClgSetptSchRef | reference | none | [6 empty] | CondRequired |  | Schedule
| CoolResetOutdoorHigh | ClRstOutdrHi | decimal | F | [6 empty] | Defaulted
| CoolResetOutdoorLow | ClRstOutdrLow | decimal | F | [6 empty] | Defaulted
| CoolResetSupplyHigh | ClRstSupHi | decimal | F | [6 empty] | Defaulted
| CoolResetSupplyLow | ClRstSupLow | decimal | F | [6 empty] | Defaulted
| Count | Cnt | integer | none | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM sections 2.3.1 and 5.3 The number of duplicate HVAC systems represented by the modeled system.
| Description | Desc | string | none | [6 empty] | Optional |  |  |  | This is a brief description of the object that summarizes its essential characteristics
| DuctInsulation | DuctIns | enumerated list | h ft2 F per Btu | [6 empty] | Optional |  |  | dtyp:EnumerationConstantPermissive | This is the required R Value for ducts in lowrise residential buildings | Required for the residential prescriptive certificate of compliance.
| DuctLocation | DuctLctn | enumerated list | none | Conditioned | [5 empty] | Required |  |  |  |  | CF2R-MCH01a, old CF1RPerNAA
None
Other
Unconditioned
| DuctStatus | DuctStatus | integer | none |  | No |  |  |  |  | Defaulted
| ExhaustControlMethod | ExhCtrlMthd | enumerated list | none | COControl | [5 empty] | Defaulted
ConstantFlowConstantSpeedFan
NoCOControl
VariableFlowConstantSpeedFan
VariableFlowVariableSpeedFan
| ExhaustOperationMode | ExhOperMode | enumerated list | none | CoupledToSystem | [5 empty] | Defaulted
DecoupledFromSystem
| ExhaustSystemType | ExhSysType | enumerated list | none | CommercialKitchen | [5 empty] | Defaulted
General
Laboratory
ParkingGarage
| FanControl | FanCtrl | enumerated list | none | Continuous | [5 empty] | Defaulted
Cycling
| FanPosition | FanPos | enumerated list | none | BlowThrough | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM
| HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
| HeatingFixedSupplyTemperature | HtgFixedSupTemp | decimal | F | [6 empty] | Optional
| HeatingSetPointScheduleReference | HtgSetPtSchRef | reference | none | [6 empty] | Optional |  | Schedule
| IsAllOutsideAir | IsAllOA | boolean | none |  | No |  |  |  |  | Defaulted
| IsComplexSystem | IsComplexSystem | boolean | none | [6 empty] | Defaulted
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| NightCycleFanControl | NightCycleFanCtrl | enumerated list | none | CycleOnCallAnyZone | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.2 System Controls
CycleOnCallPrimaryZone
CycleZoneFansOnly
StaysOff
| OptimumStart | OptStart | boolean | none | [6 empty] | Defaulted
| ReheatControlMethod | ReheatCtrlMthd | enumerated list | none | DualMaximum | [5 empty] | Defaulted |  |  |  | The air/temperature control strategy for VAV systems with reheat boxes during heating mode.
SingleMaximum
| Status | Status | enumerated list | none | Altered | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for AirSystem and ZoneSystem; Required for FluidSystem and RecirculationDHWSystem
Existing
New
| SubType | SubType | enumerated list | none | CRAC | [5 empty] | Defaulted |  |  |  | Air System equipment subtype | 2013 NR ACM
CRAH
SinglePackaged1Phase
SinglePackaged3Phase
Split1Phase
Split3Phase
| Type | Type | enumerated list | none | DOASCV | [5 empty] | Compulsory |  |  |  |  | 2013 NR ACM: 5.7 HVAC Secondary Systems; Tables 15 and N2-16 to N2-23
DOASVAV
Exhaust
PVAV
SPVAC
SPVHP
SZAC
SZHP
SZVAVAC
SZVAVHP
VAV
Boiler
| AFUE | AFUE | decimal | none | [6 empty] | CondRequired |  |  |  | The full load efficiency of a boiler or furnace at AFUE rated conditions | 2013 NR ACM: 5.7.6.4 Furnace equation 41 5.8.1 Boilers equation 59
| CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | Required |  |  |  | The rated measure of energy ouput of Boilers. | 2013 NR ACM: 5.8.1 Boilers Boiler Design Capacity;
| CombustionEfficiency | CombEff | decimal | none | [6 empty] | CondRequired |  |  |  | The measure of how much energy is extracted from the fuel and is the ratio of heat transferred to the combustion air divided by the heat input of the fuel. | 2013 NR ACM: 5.8.1 Boilers Boiler Efficiency Type
| DraftFanHorsePower | DraftFanHp | decimal | hp | [6 empty] | CondRequired |  |  |  | Nameplate horsepower of the draft fan motor (HP), | 2013 NR ACM 5.8.3
| DraftType | DraftType | enumerated list | none | Condensing | [5 empty] | CondRequired |  |  |  | How combustion airflow is drawn through the boiler | 2013 NR ACM 5.8.1 Boilers equation 59
MechanicalNoncondensing
Natural
| EIR | EIR | decimal | none | [6 empty] | CondRequired |  |  |  | The ratio of energy used by the system to the heating capacity in the same units. EIR is used in calculating a performance curve for heating equipment. It is the reciprocal of the coefficient of performance (COP) Represented as EIR | 2013 NR ACM: 5.8.1 Boilers Boiler Part-Load Performance Curve;
| EnteringTemperatureDesign | EntTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
| FluidSegmentInReference | FluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSegment |  |  | The name of the fluid segment that brings fluid into HVAC equipment
| FluidSegmentOutReference | FluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSegment |  |  | The name of the fluid segment that takes fluid out of HVAC equipment
| FuelFullLoad | FuelFullLd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The fuel consumption at design conditions | 2013 NR ACM 5.7.6.4 Furnace, equation 42 5.8.1 Boilers equation 60; 5.9.1.2 Water Heaters equation 76
| FuelSource | FuelSrc | enumerated list | none | Electric | [5 empty] | Required |  |  |  | Defines the type of energy used to run the equipment or provide heat. Values: electricity, natural gas, propane, fuel oil, hot water, steam, solar thermal. | 2013 NR ACM: 5.8.1 Boiler fuel
Gas
| HasBypass | HasBypass | boolean | none | [6 empty] | Optional
| HeatLoss | HtLoss | decimal | Btu per h | [6 empty] | Optional |  |  |  | The heat lost when the Boiler is firing and is expressed as a fraction of full load output capacity. The default is .02 for electric boilers and heat-exchangers and 0 for fuel-fired boilers | 2013 NR ACM: 5.8.1 Boilers Boiler Heat Loss
| LeavingTemperatureDesign | LvgTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| ParasiticLoad | ParasiticLd | decimal | W | [6 empty] | CondRequired |  |  |  | Electricity consumption of mechanical draft equipment (W) | 2013 NR ACM 5.8.3
| Status | Status | enumerated list | none | Existing | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| ThermalEfficiency | ThrmlEff | decimal | none | [6 empty] | CondRequired |  |  |  | The full load of a boiler or water heater or heating coil efficiency calculated as the ratio of heat transferred to the water divided by the heat input of the fuel. | 2013 NR ACM 5.8.1 Boilers equation 59 Used in residential CF1R-PRF
| Type | Type | enumerated list | none | HotWater | [5 empty] | Required |  |  |  |  | 2013 NR ACM: 5.8.1 Boilers Boiler Type;
Steam
| UnloadRatioMinimum | UnldRatMin | decimal | none | [6 empty] | Defaulted |  |  |  | The minimum unloading capacity of the Boiler,expressed as a fraction of the rated capacity. Below this level the equipment must cycle to meet the load. | 2013 NR ACM: 5.8.1 Boilers Boiler Minimum Unloading Ratio, Table 64,
Chiller
| AuxiliaryPower | AuxPwr | decimal | W | [6 empty] | Defaulted
| CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | Required |  |  |  | Cooling capacity of chiller equipment at prescribed rating conditions. | 2013 NR ACM 5.8.2 Chillers Chiller Rated Capacity equations
| CondenserFluidSegmentInReference | CndsrInRef | reference | none | [6 empty] | CondRequired | FluidSegment
| CondenserFluidSegmentOutReference | CndsrOutRef | reference | none | [6 empty] | CondRequired | FluidSegment
| CondenserPowerRated | CndsrPwrRtd | decimal | kW | [6 empty] | Optional |  |  |  | The energy usage of the condenser fan(s) at design conditions on an air-cooled chiller. This unit should only be used for chillers composed of separate evaporator and condenser sections where the fan energy is not part of the chiller COP. | 2013 NR ACM: 5.8.2 Chillers
| CondenserType | CndsrType | enumerated list | none | Air | [5 empty] | Required |  |  |  | Defines the type condenser used for a chiller
Fluid
| COP | COP | decimal | none | [6 empty] | CondRequired |  |  |  | The efficiency of the chiller expressed as the ARI rated coefficient of performance | 2013 NR ACM 5.8.2 Chillers Chiller Rated Efficiency
| DesignGeneratorFluidDeltaTemperature | DsgnGenFluidDelT | decimal | F | [6 empty] | Defaulted
| EER | EER | decimal | none | [6 empty] | CondRequired
| EnableOnThermalEnergyStorageDischarge | EnableOnThrmlEngyStorDischrg | boolean | none |  | No |  |  |  |  | Defaulted
| EnteringGeneratorTemperatureDesign | EntGenTempDsgn | decimal | F | [6 empty] | Defaulted
| EnteringTemperatureDesign | EntTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
| EnteringTemperatureRated | EntTempRtd | decimal | F | [6 empty] | Optional
| EvaporatorFluidSegmentInReference | EvapInRef | reference | none | [6 empty] | Required | FluidSegment
| EvaporatorFluidSegmentOutReference | EvapOutRef | reference | none | [6 empty] | Required | FluidSegment
| EvaporatorHasBypass | EvapHasBypass | boolean | none | [6 empty] | Optional
| FuelSource | FuelSrc | enumerated list | none | Electric | [5 empty] | Required |  |  |  | Defines the type of energy used to run the Chiller. | 2013 NR ACM: 5.8.2 Chiller Fuel
Indirect
| GeneratorFluidFlowCapacity | GenFluidFlowCap | decimal | gal per min | [6 empty] | Optional
| GeneratorFluidSegmentInReference | GenFluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSegment
| GeneratorFluidSegmentOutReference | GenFluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSegment
| IPLVCOP | IPLVCOP | decimal | none | [6 empty] | CondRequired |  |  |  | IPLV is a metric of part load performance, but the units change based on the efficiency descriptor. This makes it three different properties in SDD terms. | 2013 NR ACM 5.8.2
| IPLVEER | IPLVEER | decimal | Btu per W h | [6 empty] | CondRequired |  |  |  | IPLV is a metric of part load performance, but the units change based on the efficiency descriptor. This makes it three different properties in SDD terms. | 2013 NR ACM 5.8.2
| IPLVKwPerTon | IPLVKwPerTon | decimal | kW per ton | [6 empty] | CondRequired |  |  |  | IPLV is a metric of part load performance, but the units change based on the efficiency descriptor. This makes it three different properties in SDD terms. | 2013 NR ACM 5.8.2
| KwPerTon | KwPerTon | decimal | kW per ton | [6 empty] | CondRequired
| LeavingTemperatureDesign | LvgTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
| LeavingTemperatureRated | LvgTempRtd | decimal | F | [6 empty] | Optional
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| PartLoadRatioMinimum | PLRMin | decimal | none | [6 empty] | Defaulted |  |  |  | The minimum chiller load which can be met with continuous operation. Below this load, the chiller cycles. The UnldRatMin is the lowest load which the chiller can meet with unloading. Between UnldRatMin and PartLdRatMin, the chiller is false loaded as with hot gas bypass. | 2013 NR ACM 5.8.2
| Status | Status | enumerated list | none | Existing | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| Type | Type | enumerated list | none | AbsorptionSingleEffect | [5 empty] | Required |  |  |  | ChillerType
Centrifugal
Reciprocating
Screw
Scroll
| UnloadRatioMinimum | UnldRatMin | decimal | none | [6 empty] | Defaulted |  |  |  | The minimum unloading capacity of the Chiller, expressed as a fraction of the rated capacity. Below this level the equipment must cycle to meet the load. | 2013 NR ACM: 5.8.2 Chillers Table 85 Default Minimum Unloading Ratios;
CoilCooling
| AuxiliaryPower | AuxPwr | decimal | W | [6 empty] | Optional
| BypassMinimumEfficiencyCheck | BypassMinEffCheck | boolean | none | [6 empty] | Defaulted
| CapacityTotalGrossRated | CapTotGrossRtd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The total cooling capacity of a coil at rated conditions | 2013 NR ACM 5.7.5 Cooling Systems
| CapacityTotalNetRated | CapTotNetRtd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The total cooling capacity of a coil at design conditions | 2013 NR ACM 5.7.5 Cooling Systems
| CapacityTotalRatedStageFraction | CapTotRtdStageFrac | decimal | none |  | Yes | 0 | 2 | 0 | 1 | Defaulted |  |  |  | Total cooling capacity of each cooling stage, at ARI rated conditions. The capacity is expressed as an array, with each entry a fraction of the total rated cooling capacity for the unit. | 2013 NR ACM 5.7.5.2
| CoilHeadDesign | CoilHdDsgn | decimal | ft H2O | [6 empty] | Defaulted
| CondenserType | CndsrType | enumerated list | none | Air | [5 empty] | Defaulted |  |  |  | Defines the type condenser used for a cooling or heating coil
WaterSource
| DXCrankcaseControlTemperature | DXCrankcaseCtrlTemp | decimal | F | [6 empty] | Optional
| DXCrankcaseHeatCapacity | DXCrankcaseHtCap | decimal | Btu per h | [6 empty] | Optional |  |  |  | The capacity of the electric resistance heater in the crank case of a direct expansion (DX) compressor. The crank case heater operates only when the compressor is off. | 2013 NR ACM 5.7.6.5
| DXEER | DXEER | decimal | Btu per h W | [6 empty] | CondRequired |  |  |  | The energy efficiency ratio (EER) of net cooling capacity (in Btu/hr) to total rate of electrical energy input (in watts), of cooling equipment under designated operating conditions. | 2013 NR ACM 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency, equations 21 and 22
| DXIEER | DXIEER | decimal | Btu per h W | [6 empty] | CondRequired
| DXSEER | DXSEER | decimal | Btu per h W | [6 empty] | CondRequired |  |  |  | The Seasonal Energy Efficiency Ratio (SEER) of the coil in a DX cooling system | 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency
| FluidFlowRateDesign | FluidFlowRtDsgn | decimal | gal per min | [6 empty] | CondRequired |  |  |  | The maximum possible water volume flow rate through a hydronic coil. Used to define capacity for coils not explicilty defined by capacity in terms of Btu/h.
| FluidSegmentInReference | FluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSegment |  |  | The name of the fluid segment that brings fluid into HVAC equipment
| FluidSegmentOutReference | FluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSegment |  |  | The name of the fluid segment that takes fluid out of HVAC equipment
| MinimumHotGasRatio | MinHotGasRat | decimal | none | [6 empty] | Optional |  |  |  |  | 2013 NR ACM 5.7.5.2
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| NumberCoolingStages | NumClgStages | integer | none | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.5.2
| Type | Type | enumerated list | none | ChilledWater | [5 empty] | Compulsory |  |  |  | CoilCoolingType | 2013 NR ACM 5.7.5.1 Cooling Systems General
DirectExpansion
CoilHeating
| AuxilliaryPower | AuxPwr | decimal | W | [6 empty] | Optional
| BypassMinimumEfficiencyCheck | BypassMinEffCheck | boolean | none | [6 empty] | Defaulted
| CapacityTotalGrossRated | CapTotGrossRtd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The cooling or heating capacity of HVAC equipment at prescribed rating conditions. | 2013 NR ACM: 5.8.1 Boilers Boiler Design Capacity; 5.8.2 Chillers Chiller Rated Capacity equations; 5.8.3 Cooling Towers Cooling Tower Capacity
| CapacityTotalNetRated | CapTotNetRtd | decimal | Btu per h | [6 empty] | CondRequired
| CoilHeadDesign | CoilHdDsgn | decimal | ft H2O | [6 empty] | Defaulted
| CondenserType | CndsrType | enumerated list | none | Air | [5 empty] | Defaulted |  |  |  | Defines the type condenser used for a cooling or heating coil
WaterSource
| FluidFlowRateDesign | FluidFlowRtDsgn | decimal | gal per min | [6 empty] | CondRequired |  |  |  | The maximum possible water volume flow rate through a hydronic coil. Used to define capacity for coils not explicilty defined by capacity in terms of Btu/h.
| FluidSegmentInReference | FluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSegment |  |  | The name of the fluid segment that brings fluid into HVAC equipment
| FluidSegmentOutReference | FluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSegment |  |  | The name of the fluid segment that takes fluid out of HVAC equipment
| FuelSource | FuelSrc | enumerated list | none | Electric | [5 empty] | Defaulted |  |  |  | This lists all sources of heat for a heating coil | 2013 NR ACM 5.7.6 Heating Systems 5.7.6.1 General Heating Source
Gas
OilNoLongerValid
| FurnaceAFUE | FurnAFUE | decimal | none | [6 empty] | CondRequired |  |  |  | The Annual Fuel Utilization Efficiency (AFUE) season-long, average efficiency of that piece of equipment | 2013 NR ACM 5.7.6.4
| FurnaceIgnitionType | FurnIgnType | enumerated list | none | IntermittentIgnitionDevice | [5 empty] | Defaulted |  |  |  | Either pilot or an intermittent ignition device (IID) in furnaces. An IID is mandatory for furnaces with capacities of 225,000 Btu/h and greater. | 2008 Title 24: Section 112 Mandatory Requirements For Space-Conditioning Equipment (d) Gas- and Oil-Fired Furnace Standby Loss Controls
PilotLight
| FurnacePilotFuelInput | FurnPilotFuelInp | decimal | Btu per h | [6 empty] | Defaulted |  |  |  | The measure of energy required by the Furnace pilot light. | 2013 NR ACM: 5.7.6.4 Furnace Furnace Fuel Heating Pilot
| FurnaceThermalEfficiency | FurnThrmlEff | decimal | none | [6 empty] | CondRequired |  |  |  | The full load of a water heater or heating coil efficiency calculated as the ratio of heat transferred to the water divided by the heat input of the fuel. | 2013 NR ACM 5.7.6.4 Furnace equation 41
| HeatPumpCompressorLockoutTemperature | HtPumpCprsrLockoutTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.5.6.5
| HeatPumpCOP | HtPumpCOP | decimal | none | [6 empty] | CondRequired |  |  |  | The ARI rated coefficient of performance for the heating equipment such as a heat pump | 2013 NR ACM 5.7.6.5 Electric Heat Pump Electric Heat Pump Heating Efficiency
| HeatPumpCrankcaseControlTemperature | HtPumpCrankcaseCtrlTemp | decimal | F | [6 empty] | Defaulted |  |  |  | The dry bulb temperature at which the crank case in an electric heat pump is shut off. | 2013 NR ACM: 5.7.6.5 Electric Heat Pump Heat Pumps Crank Case Heater Shutoff Temperature
| HeatPumpCrankcaseHeatCapacity | HtPumpCrankcaseHtCap | decimal | Btu per h | [6 empty] | Optional |  |  |  | The capacity of the electric resistance heater in the crank case of a direct expansion (DX) compressor. The crank case heater operates only when the compressor is off. | 2013 NR ACM 5.7.6.5
| HeatPumpDefrostControl | HtPumpDefCtrl | enumerated list | none | OnDemand | [5 empty] | Defaulted |  |  |  | Defines how the defrosting is activated, either on demand or on a timed cycle which is by default 3.5 minutes in length | 2013 NR ACM: 5.7.6.5 Heat Pumps Coil Defrost
TimedCycle
| HeatPumpDefrostHeatCapacity | HtPumpDefHtCap | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The capacity of the electric resistance defrost heater. | 2013 NR ACM: 5.7.6.5
| HeatPumpDefrostHeatSource | HtPumpDefHtSrc | enumerated list | none | Electric | [5 empty] | Defaulted |  |  |  | Defines the source of the defrosting heat which is usually hot gas or electric resisitance | 2013 NR ACM: 5.7.6.5 Heat Pumps Coil Defrost
HotGas
| HeatPumpHSPF | HtPumpHSPF | decimal | Btu per W h | [6 empty] | CondRequired |  |  |  | A measure of efficiency of heating equipment using Heating Season Performance Factor (HSPF) | 2013 NR ACM 5.7.6.5 Electric Heat Pump Electric Heat Pump Heating Efficiency
| HeatPumpSupplementalCoilHeatingReference | HtPumpSuppCoilHtgRef | reference | none | [6 empty] | Optional | CoilHeating |  |  | Reference to the coil object that provides supplemental heating when the heat pump compressor is cannot meet load or is disabled. | 2013 NR ACM: 5.7.6.5
| HeatPumpSupplementalTemperature | HtPumpSuppTemp | decimal | F | [6 empty] | Defaulted |  |  |  | The dry bulb temperature at which supplemental heating equipment is allowed to be turned on | 2013 NR ACM 5.7.6.5 Heat Pumps Electric Heat Pump Electric Supplemental Heating Control Temp
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| Type | Type | enumerated list | none | Furnace | [5 empty] | Compulsory |  |  |  | CoilHeatingType
HeatPump
HotWater
Resistance
EvaporativeCooler
| Effectiveness | Eff | decimal | none | [6 empty] | Required |  |  |  | A ratio that represents the effectiveness of an EvaporativeCooler | 2013 NR ACM 5.7.5.3 Evaporative Cooler equations 37 and 38
| IndirectDewPointEffectiveness | IndirectDewPtEff | decimal | none | [6 empty] | Defaulted |  |  |  | Effectiveness applied to the dewpoint depression. The cooler uses the warmer of the temperatures determined from the wetbulb depression and dewpoint depression | 2013 NR ACM 5.7.5.3
| Name | Name | name | none | [6 empty] | Required
| PumpPower | PumpPwr | decimal | W | [6 empty] | Required |  |  |  |  | 2013 NR ACM 5.7.5.3 Evaporative Cooler
| SecondaryAirSource | SecAirSrc | enumerated list | none | OutdoorAir | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.5.3
ReturnAir
| SecondaryFanFlowCapacity | SecFanFlowCap | decimal | ft3 per min | [6 empty] | CondRequired |  |  |  |  | 2013 NR ACM 5.7.5.3 Evaporative Cooler Evaporative Cooling
| SecondaryFanTotalEfficiency | SecFanTotEff | decimal | none | [6 empty] | Defaulted |  |  |  | includes motor eff | 2013 NR ACM 5.7.5.3 Evaporative Cooler
| SecondaryFanTotalStaticPressure | SecFanTotStaticPress | decimal | in water column | [6 empty] | CondRequired |  |  |  |  | 2013 NR ACM 5.7.5.3 Evaporative Cooler
| Type | Type | enumerated list | none | Direct | [5 empty] | Required |  |  |  | Defines the type of EvaporativeCooler operation | 2013 NR ACM 5.7.5.3 Evaporative Cooler Evaporative Cooling Type
Indirect
Fan
| CentrifugalType | CentType | enumerated list | none | AirFoil | [5 empty] | Defaulted |  |  |  | Defines the mechanism of a centrifugal fan | 2013 NR ACM 5.7.3 Fan Systems Part Load Power Curve Table 46 – Fan Curve Default Values
BackwardInclined
ForwardCurved
| Classification | Class | enumerated list | none | Axial | [5 empty] | Defaulted |  |  |  | The classification of the fan design. | 2013 NR ACM: 5.7.3.2
Centrifugal
| ControlMethod | CtrlMthd | enumerated list | none | ConstantVolume | [5 empty] | Required |  |  |  |  | 2013 NACR ACM 5.7.3.2,
Dampers
InletVanes
TwoSpeed
VariablePitchBlades
VariableSpeedDrive
| FlowCapacity | FlowCap | decimal | ft3 per min | [6 empty] | Required |  |  |  | Defines the volumetric capacity of the fan measured in cubic ft per minute (cfm). The fan's peak airflow is what it is rated at when running at full capacity. | 2013 Title 24: Section 140.4 (c) Power Consumption of Fans; Used in Residential compliance document CF2R-MCH-27.for exhause fan; 2013 NR ACM 5.6.5.3 Zone Exhaust Exhaust Air Flow Rate; 5.7.3.4 Exhaust Fan Systems Exhaust Fan Rated Capacity; 5.7.3.2 Supply Fans Supply Fan Design Air Rated Capacity
| FlowEfficiency | FlowEff | decimal | none | [6 empty] | Defaulted |  |  |  | The efficiency of the Fan as a whole at design conditions | 2013 NR ACM: 5.7.3 Fan Systems Supply Fan Efficiency, Return/Relief Fan Efficiency
| FlowMinimum | FlowMin | decimal | ft3 per min | [6 empty] | CondRequired |  |  |  | The lowest flow rate rated for a fan | 2013 NR ACM 5.7.5.2
| ModelingMethod | ModelingMthd | enumerated list | none | BrakeHorsePower | [5 empty] | Required |  |  |  | Defines how the FanSystem is modeled. | 2013 NR ACM 5.7.3.2 Supply Fans; 5.7.3.4 Exhaust Fan Systems
PowerPerUnitFlow
StaticPressure
| MotorBHP | MtrBHP | decimal | hp | [6 empty] | Optional |  |  |  | The brake horsepower of the motor before the loss in power caused by the gearbox, alternator, differential, and other auxiliary components. | 2013 NR ACM 5.7.3 Fan systems, 5.7.5 Cooling Systems Total Cooling Capacity equation 11;
| MotorEfficiency | MtrEff | decimal | none | [6 empty] | Required |  |  |  | Indicates how well the motor converts electrical power into mechanical power and is defined as output power divided by input power expressed as a percentage . | 2013 NR ACM 5.7.3.2 Supply Fans Supply Motor Efficiency; 5.8.5 Pumps Motor Efficiency
| MotorHP | MtrHP | decimal | hp | [6 empty] | Required |  |  |  | The nameplate (rated) horsepower of the motor. | 2013 NR ACM Supply Motor Efficiency Table N2-20 Minimum Nominal Efficiency for Electric Motors (from 2008 NR ACM); 5.8.5 Pumps Motor Efficiency
| MotorPoleCount | MtrPoleCnt | integer | none | [6 empty] | Defaulted |  |  |  | The number of pole electromagnetic windings in the motor's stator and used to assign MotorEfficiency. Poles is always paired, so PoleCount is always a multiple of 2. | 2013 NR ACM 5.7.3 Fan systems, References 2008 NR ACM Table N2-20 which requires PoleCount of the motor
| MotorPosition | MtrPos | enumerated list | none | InAirStream | [5 empty] | Defaulted |  |  |  | Defines where the Fan motor is located relative to the cooling air stream. Values: InAirStream, NotInAirStream | 2013 NR ACM 5.7.3 Fan systems, Motor position
NotInAirStream
| MotorType | MtrType | enumerated list | none | Enclosed | [5 empty] | Defaulted |  |  |  | Defines if the motor is Open or Enclosed | 2013 NR ACM 5.7.3 Fan systems, References 2008 NR ACM Table N2-20 which requires EnclosedType of the motor
Open
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| TotalStaticPressure | TotStaticPress | decimal | in water column | [6 empty] | CondRequired |  |  |  | The design static pressure for the Fan | 2013 NR ACM 5.7.3 Fan Systems Supply Fan Static Pressure Return/Relief Design Static Pressure
FluidSegment
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| PrimarySegmentReference | PriSegRef | reference | none | [6 empty] | CondRequired | FluidSegment
| Source | Src | enumerated list | none | MunicipalWater | [5 empty] | Required
NoExternalSource
| Type | Type | enumerated list | none | MakeupFluid | [5 empty] | Compulsory |  |  |  | FluidSegmentType
PrimaryReturn
PrimarySupply
SecondaryReturn
SecondarySupply
FluidSystem
| AngleFromTrueNorth | AngleFromTrueNorth | decimal | deg arc | [6 empty] | Optional
| AnnualSolarFraction | AnnualSolFrac | decimal | none | [6 empty] | Defaulted
| Area | Area | integer | ft2 |  | No
| AvailabiltyScheduleReference | AvailSchRef | reference | none | [6 empty] | Defaulted |  | Schedule |  |  | 2013 NR ACM: 5.7
| Brand | Brand | string | none |  | No | [7 empty] | dtyp:String50Char
| CentralSystem | CentralSys | boolean | none | [6 empty] | Optional
| CollectorType | CollectorType | string | none |  | No | [7 empty] | dtyp:String50Char
| ControlType | CtrlType | enumerated list | none | DDC | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM
Other
| CoolingSupplyTemperature | ClgSupTemp | decimal | F | [6 empty] | Optional |  |  |  | The design cooling temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also is cold deck temp | 2013 NR ACM 5.7.2.2 Cooling Control
| Count | Cnt | integer | none | [6 empty] | Optional |  |  |  |  | 2013 NR ACM sections 2.3.1 and 5.3 The number of duplicate HVAC systems represented by the modeled system.
| Description | Desc | string | none | [6 empty] | Optional |  |  |  | This is a brief description of the object that summarizes its essential characteristics
| DesignSupplyWaterTemperature | DsgnSupWtrTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
| DesignSupplyWaterTemperatureDeltaT | DsgnSupWtrTempDelT | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
| EquipmentList1Name | EquipList1Name | reference | none |  | Yes | 0 | 10 |  |  | Optional | Boiler; Chiller
| EquipmentList2Name | EquipList2Name | reference | none |  | Yes | 0 | 10 |  |  | Optional | Boiler; Chiller
| EquipmentList3Name | EquipList3Name | reference | none |  | Yes | 0 | 10 |  |  | Optional | Boiler; Chiller
| EquipmentList4Name | EquipList4Name | reference | none |  | Yes | 0 | 10 |  |  | Optional | Boiler; Chiller
| FixedSupplyTemperature | FixedSupTemp | decimal | F | [6 empty] | Defaulted
| Fluid | Fluid | string | none |  | No | [7 empty] | dtyp:String50Char
| HeatingDesignSupplyWaterTemperature | HtgDsgnSupWtrTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
| HeatingFixedSupplyTemperature | HtgFixedSupTemp | decimal | F | [6 empty] | Defaulted
| HeatingSupplyTemperature | HtgSupTemp | decimal | F | [6 empty] | Optional |  |  |  | The design heating temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also hot deck temp | 2013 NR ACM 5.7.2.3 Heating Control;
| HeatingTemperatureSetPointScheduleReference | HtgTempSetptSchRef | reference | none | [6 empty] | CondRequired |  | Schedule
| HotWaterSupplyTemperature | HotWtrSupTemp | decimal | F | [6 empty] | Defaulted
| LoadRangeLimit | LdRngLim | integer | Btu per h |  | Yes | 0 | 4 |  |  | Optional |  |  | dtyp:IntegerNonnegative
| Manufacturer | Manufacturer | string | none |  | No | [7 empty] | dtyp:String50Char
| ModelNumber | ModelNum | string | none |  | No | [7 empty] | dtyp:String50Char
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| NameOfProgramUsed | NameOfProgramUsed | string | none |  | No
| NumberOfIdenticalDwellingUnits | NumOfIdenticalDwellingUnits | integer | none |  | No
| RatedEfficiencyCurveIntercept | RatedEffCurveIntercept | decimal | none |  | No | [7 empty] | dtyp:Decimal3Places
| RatedEfficiencyCurveSlope | RatedEffCurveSlope | decimal | none |  | No | [7 empty] | dtyp:Decimal3Places
| ResetOutdoorHigh | RstOutdrHi | decimal | F | [6 empty] | CondRequired
| ResetOutdoorLow | RstOutdrLow | decimal | F | [6 empty] | CondRequired
| ResetSupplyHigh | RstSupHi | decimal | F | [6 empty] | CondRequired
| ResetSupplyLow | RstSupLow | decimal | F | [6 empty] | CondRequired
| SecondaryTankVolume | SecondaryTankVol | decimal | gal | [6 empty] | Optional
| SlopeFromHorizontal | SlopeFromHorizontal | decimal | deg arc | [6 empty] | Optional
| SolarCollectorCount | SolCollectorCnt | integer | none |  | No | [9 empty] | CF1RSTH02E, CBECC Com NR SDD
| SRRCCertificationNumber | SRRCCertNum | string | none |  | No
| Status | Status | enumerated list | none | Altered | [5 empty] | Required |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for AirSystem and ZoneSystem; Required for FluidSystem and RecirculationDHWSystem
Existing
New
| TemperatureControl | TempCtrl | enumerated list | none | Fixed | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.2.2 Cooling Control
FixedDualSetpoint
OutsideAirReset
Scheduled
WetBulbReset
| TemperatureSetPointScheduleReference | TempSetptSchRef | reference | none | [6 empty] | CondRequired |  | Schedule
| Type | Type | enumerated list | none | ChilledWater | [5 empty] | Compulsory |  |  |  | FluidSystemType
CondenserWater
HotWater
ServiceHotWater
| Version | Version | string | none |  | No
| WaterHeaterTankVolume | WtrHtrTankVol | decimal | gal | [6 empty] | Optional
| WetBulbApproach | WetBulbApproach | decimal | F | [6 empty] | CondRequired
HeatExchanger
| CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | Required
| ChilledWaterEnteringTemperatureDesign | CHWEntTempDsgn | decimal | F | [6 empty] | Required
| ChilledWaterFluidSegmentInReference | CHWFluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSegment
| ChilledWaterFluidSegmentOutReference | CHWFluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSegment
| ChilledWaterLeavingTemperatureDesign | CHWLvgTempDsgn | decimal | F | [6 empty] | Required
| CondenserWaterFluidSegmentInReference | CWFluidSegInRef | reference | none | [6 empty] | Required | FluidSegment
| CondenserWaterFluidSegmentOutReference | CWFluidSegOutRef | reference | none | [6 empty] | Required | FluidSegment
| CondenserWaterLeavingTemperatureDesign | CWLvgTempDsgn | decimal | F | [6 empty] | Required
| EconomizerIntegration | EconoIntegration | enumerated list | none | Integrated | [5 empty] | Defaulted
NonIntegrated
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| Status | Status | enumerated list | none | Existing | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| Type | Type | enumerated list | none | CounterFlow | [5 empty] | Defaulted |  |  |  | HeatExchangerType
HeatRecovery
| AuxiliaryPower | AuxPwr | decimal | W | [6 empty] | Defaulted
| CoolingLatentEffectiveness100 | ClgLatEff100 | decimal | [7 empty] | Defaulted
| CoolingLatentEffectiveness75 | ClgLatEff75 | decimal | [7 empty] | Defaulted
| CoolingSensibleEffectiveness100 | ClgSensEff100 | decimal | [7 empty] | Defaulted
| CoolingSensibleEffectiveness75 | ClgSensEff75 | decimal | [7 empty] | Defaulted
| CoolingTotalEffectiveness100 | ClgTotEff100 | decimal | [7 empty] | Defaulted
| CoolingTotalEffectiveness75 | ClgTotEff75 | decimal | [7 empty] | Defaulted
| DefrostControl | DefrostCtrl | enumerated list | none | ExhaustAirRecirculation | [5 empty] | Defaulted
ExhaustOnly
MinimumExhaustTemperature
None
| DefrostControlTemperature | DefrostCtrlTemp | decimal | F | [6 empty] | Defaulted
| EconomizerLockout | EconoLockout | boolean | none | [6 empty] | Defaulted
| FixedSupplyTemperature | FixedSupTemp | decimal | F | [6 empty] | Defaulted
| HasHeatExchangerBypass | HasHXBypass | boolean | none | [6 empty] | Defaulted
| HeatingLatentEffectiveness100 | HtgLatEff100 | decimal | [7 empty] | Defaulted
| HeatingLatentEffectiveness75 | HtgLatEff75 | decimal | [7 empty] | Defaulted
| HeatingSensibleEffectiveness100 | HtgSensEff100 | decimal | [7 empty] | Defaulted
| HeatingSensibleEffectiveness75 | HtgSensEff75 | decimal | [7 empty] | Defaulted
| HeatingTotalEffectiveness100 | HtgTotEff100 | decimal | [7 empty] | Defaulted
| HeatingTotalEffectiveness75 | HtgTotEff75 | decimal | [7 empty] | Defaulted
| RecoveryType | RcvryType | enumerated list | none | LatentOnly | [5 empty] | Defaulted
SensibleOnly
Total
| SupplyFlowRated | SupFlowRtd | decimal | ft3 per min | [6 empty] | Defaulted
| TemperatureControl | TempCtrl | enumerated list | none | Fixed | [5 empty] | Defaulted
None
Scheduled
| TemperatureSetpointScheduleReference | TempSetptSchRef | reference | [7 empty] | CondRequired |  | Schedule
| Type | Type | enumerated list | none | Plate | [5 empty] | Defaulted
Wheel
HeatRejection
| AirFlowCapacity | AirFlowCap | decimal | ft3 per min | [6 empty] | Required
| CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | Required |  |  |  | The rated cooling capacity at CTI test conditions. | 2013 NR ACM 5.8.3 Cooling Towers Cooling Tower Capacity
| CellCount | CellCnt | decimal | none | [6 empty] | Defaulted |  |  |  | The number of cells in the cooling tower. Each cell has its own fan, water flow allowing for responding to lower load conditions | 2013 NR ACM: 5.8.3 Cooling Towers Cooling Tower number of Cells;
| DesignWBTemperature | DsgnWBTemp | decimal | F | [6 empty] | Optional
| EnteringTemperatureDesign | EntTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
| FanType | FanType | enumerated list | none | Axial | [5 empty] | Defaulted
Centrifugal
| FluidSegmentInReference | FluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSegment |  |  | For coil, this is defined for Coil type = HotWater, ChilledWater, WaterEconomizer only
| FluidSegmentOutReference | FluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSegment |  |  | Defined for Coil type = HotWater, ChilledWater, WaterEconomizer only
| LeavingTemperatureDesign | LvgTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
| LowSpeedAirFlowRatio | LowSpdAirFlowRat | decimal | none | [6 empty] | Defaulted |  |  |  | The percentage of full load airflow at low speed which is equivalent to the percentage of full load capacity at low speed. | 2013 NR ACM 5.8.3 Cooling Towers
| MinimumSpeedRatio | MinSpdRat | decimal | none | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.8.3 Cooling Towers Fan minimum speed ratio
| ModulationControl | ModCtrl | enumerated list | none | Bypass | [5 empty] | Defaulted |  |  |  | Defines how the CoolingTower modulates capacity to respond to changing loads. Assignment of value depends on FanSystem and Fan attributes e.g. operation mode and Fan speed and pony motor attributes. | 2013 NR ACM: 5.8.3 Cooling Towers Cooling Tower Capacity Control
Cycling
TwoSpeed
VariableSpeedDrive
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| Status | Status | enumerated list | none | Existing | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| TotalFanHP | TotFanHP | decimal | hp | [6 empty] | Required |  |  |  | The sum of the nameplate rated horsepower (hp) of all fan motors on the cooling tower | 2013 NR ACM: 5.8.3 Cooling Towers CoolingTower Total Fan Power
| Type | Type | enumerated list | none | ClosedTower | [5 empty] | Defaulted |  |  |  | HeatRejectionType
OpenTower
| WaterFlowCapacity | WtrFlowCap | decimal | gal per min | [6 empty] | Defaulted
OutsideAirControl
| AirSegmentReturnReference | AirSegRetRef | reference | none | [6 empty] | Optional | AirSegment
| AirSegmentSupplyReference | AirSegSupRef | reference | none | [6 empty] | Required | AirSegment
| EconomizerControlMethod | EconoCtrlMthd | enumerated list | none | DifferentialDryBulb | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.4.2 Air Side Economizers
DifferentialDryBulbAndEnthalpy
DifferentialEnthalpy
FixedDryBulb
NoEconomizer
| EconomizerHighTemperatureLockout | EconoHiTempLockout | decimal | F | [6 empty] | Optional |  |  |  | The outside air temperature above which the economizer will return to minimum position. This applies if ControlType is FixedDB | 2013 NR ACM 5.7.4.2 Air Side Economizers; Economizer High Temperature Lockout
| EconomizerIntegration | EconoIntegration | enumerated list | none | Integrated | [5 empty] | Defaulted
NonIntegrated
| EconomizerLowTemperatureLockout | EconoLowTempLockout | decimal | F | [6 empty] | Defaulted |  |  |  | The outside air temperature below which the economizer will return to the minimum position. This appears to apply to all types of air-side economizers. | 2013 NR ACM 5.7.4.2 Air Side Economizers; Economizer Economizer Low Temperature Lockout
| HeatRecoveryReference | HtRcvryRef | reference | none | [6 empty] | Optional | HeatRecovery
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
Pump
| FlowCapacity | FlowCap | decimal | gal per min | [6 empty] | Required |  |  |  | The flow rate of fluid through the Pump in gallons per minute. | 2013 NR ACM 5.8.5 Pumps
| FlowMinimum | FlowMin | decimal | gal per min | [6 empty] | CondRequired |  |  |  | The lowest flow rate rated for a pump | 2008 NR ACM: Table N2-21 2013 ?
| ImpellerEfficiency | ImpellerEff | decimal | none | [6 empty] | Required
| MinimumSpeedRatio | MinSpdRat | decimal | none | [6 empty] | Optional |  |  |  | The ratio of the lowest speed to the full load speed | 2013 NR ACM 5.8.3 Cooling Towers Fan minimum speed ratio; 5.8.5 Pumps Pump Minimum Speed
| ModelingMethod | ModelingMthd | enumerated list | none | Detailed | [5 empty] | Defaulted |  |  |  | Defines how the Pump is modeled. | 2013 NR ACM 5.8.5 Pumps Pump Motor Modeling Method
PowerPerUnitFlow
| MotorEfficiency | MtrEff | decimal | none | [6 empty] | Required |  |  |  | Indicates how well the motor converts electrical power into mechanical power and is defined as output power divided by input power expressed as a percentage . | 2013 NR ACM 5.8.5 Pumps Motor Efficiency
| MotorHP | MtrHP | decimal | hp | [6 empty] | Required |  |  |  | The rated horsepower of the pump motor. | 2013 NR ACM 5.8.5 Pumps Motor Efficiency Table N2-20 Minimum Nominal Efficiency for Electric Motors (from 2008 NR ACM)
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| OperationControl | OperCtrl | enumerated list | none | OnDemand | [5 empty] | Defaulted |  |  |  | Defines how pump operation is controlled. Values: OnDemand, StandBy, Schedule | 2013 NR ACM 5.8.5 Pumps Pump Operation
Scheduled
StandBy
| SpeedControl | SpdCtrl | enumerated list | none | ConstantSpeed | [5 empty] | Defaulted
VariableSpeed
| Status | Status | enumerated list | none | Existing | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| TotalHead | TotHd | decimal | ft | [6 empty] | Required
ResidentialDHWSystem
| AngleFromTrueNorth | AngleFromTrueNorth | decimal | deg arc | [6 empty] | Optional
| AnnualSolarFraction | AnnualSolFrac | decimal | none | [6 empty] | Optional
| Area | Area | integer | ft2 |  | No
| BaselineResidentialWaterHeaterReference | BaseResWtrHtrRef | reference | none | [6 empty] | Optional | ResidentialWaterHeaterNR
| Brand | Brand | string | none |  | No | [7 empty] | dtyp:String50Char
| CentralSystem | CentralSys | boolean | none | [6 empty] | Optional
| CollectorType | CollectorType | string | none |  | No | [7 empty] | dtyp:String50Char
| DistributionType | DistType | enumerated list | none | DemandControl | [5 empty] | CondRequired |  |  |  |  | NRCV-PLB22
NoControlContinuousPumping
NoLoopsNoCentralPump
TemperatureModulation
TemperatureModulationMonitoring
| Fluid | Fluid | string | none |  | No | [7 empty] | dtyp:String50Char
| LoopCount | LpCnt | integer | none | [6 empty] | CondRequired
| LoopPipeInsulationThickness | LpPipeInsThkns | decimal | in |  | Yes | 6 | 6 |  |  | Required
| Manufacturer | Manufacturer | string | none | [6 empty] | Optional |  |  | xsd:string
| Manufacturer | Manufacturer | string | none |  | No | [7 empty] | dtyp:String50Char
| ModelNumber | ModelNum | string | none |  | No | [7 empty] | dtyp:String50Char
| Multiplier | Mult | integer | none | [6 empty] | Optional
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| NameOfProgramUsed | NameOfProgramUsed | string | none |  | No
| NumberOfIdenticalDwellingUnits | NumOfIdenticalDwellingUnits | integer | none |  | No
| PipeLocation | PipeLctn | enumerated list | none | Conditioned |  | 0 | 6 |  |  | CondRequired
SemiConditioned
Unconditioned
Underground
| PumpBreakHorsepower | PumpBHP | decimal | hp
| PumpEfficiency | PumpEff | decimal | none | [6 empty] | Optional
| PumpPower | PumpPwr | decimal | kW | [6 empty] | Optional
| RatedEfficiencyCurveIntercept | RatedEffCurveIntercept | decimal | none |  | No | [7 empty] | dtyp:Decimal3Places
| RatedEfficiencyCurveSlope | RatedEffCurveSlope | decimal | none |  | No | [7 empty] | dtyp:Decimal3Places
| SecondaryTankVolume | SecondaryTankVol | decimal | gal | [6 empty] | Optional
| SlopeFromHorizontal | SlopeFromHorizontal | decimal | deg arc | [6 empty] | Optional
| SolarCollectorCount | SolCollectorCnt | integer | none |  | No | [9 empty] | CF1RSTH02E, CBECC Com NR SDD
| SolarFractionFluidSystemName | SolFracFluidSysName | string | none | [6 empty] | Optional |  |  | xsd:string
| SRRCCertificationNumber | SRRCCertNum | string | none |  | No
| Status | Status | enumerated list | none | Altered | [5 empty] | Required |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for AirSystem and ZoneSystem; Required for FluidSystem and RecirculationDHWSystem
Existing
New
| SupplementalStorageTankVolume | SuppStorTankVol | decimal | gal | [6 empty] | Optional
| SystemStoryCount | SysStoryCnt | integer | none | [6 empty] | CondRequired
| TotalInputRating | TotInpRating | decimal | none | [6 empty] | Optional
| TotalTankVolume | TotTankVol | decimal | gal | [6 empty] | Optional
| Type | Type | enumerated list | none | CompactHotWaterDistributionSystemHERS | [5 empty] | Required |  |  |  | RecirculationDHWSystemType
DemandRecirculationSensorControlsHERS
DemandRecirculationSensorControlsNR
RecirculatingDemandControlPushButtonHERS
RecirculatingDemandControlledPushButton
RecirculationNonDemandHERS_NR
RecirculationNonDemandNR
StandardDistributionCentralParallelPipingHERS
StandardDistributionCentralParallelPipingNR
StandardDistributionInsulatedPipesBelowGradeNR
StandardDistributionInsulatedPipesHERS
StandardDistributionInsulatedPipesNR
StandardDistributionNR
| Version | Version | string | none |  | No
| WaterHeaterTankVolume | WtrHtrTankVol | decimal | gal | [6 empty] | Optional
ResidentialWaterHeater
| AmbientCondition | AmbCond | enumerated list | none | Conditioned | [5 empty] | CondRequired
Unconditioned
| CompressorZone | CprsrZn | enumerated list | none | Conditioned | No |  |  |  |  | CondRequired
Outside or in Exterior Closet
Unconditioned
| Count | Cnt | integer | none | [6 empty] | Required |  |  |  | The number of RecirculationWaterHeaters
| ElectricMiniTank | ElecMiniTank | boolean | none | [6 empty] | Optional
| ElectricMiniTankPower | ElecMiniTankPwr | decimal | W | [6 empty] | Optional
| ElementType | ElementType | enumerated list | none | ElectricResistance | [5 empty] | Required
Gas
HeatPump
| EnergyFactor | EngyFac | decimal | none | [6 empty] | CondRequired
| FirstHourRating | FirstHrRating | decimal | gal |  | No |  |  |  |  | CondRequired
| FlowRate | FlowRt | decimal | gal per min |  | No |  |  |  |  | CondRequired
| HeatPumpWaterHeaterBrand | HPWHBrand | enumerated list | none | A. O. Smith | No |  |  |  |  | CondRequired
American
Bradford White
EcoSense
GE
Kenmore
Lochinvar
Reliance
Rheem
Richmond
Ruud
Sanden
State
Stiebel Eltron
US Craftmaster
Whirlpool
| HeatPumpWaterHeaterModel | HPWHModel | enumerated list | none | 10 50 DHPHT 120 (50 gal) | [5 empty] | CondRequired
10 50 DHPHTNE 120 (50 gal)
10 60 DHPT 120 (60 gal)
10 66 DHPHT 120 (66 gal)
10 66 DHPHTN 120 (66 gal)
10 80 DHPHT 120 (80 gal)
10 80 DHPHTNE 120 (80 gal)
10 80 DHPT 120 (80 gal)
10E50-HP4D (50 gal)
10E65-HP4D (65 gal)
10E80-HP4D (80 gal)
12E50-HP (50 gal)
12E80-HP (80 gal)
153.32116 (60 gal)
153.32118 (80 gal)
153.5925 (50 gal)
153.5926 (60 gal)
153.5928 (80 gal)
6 50 DHPHT 120 (50 gal)
6 66 DHPHT 120 (66 gal)
6 80 DHPHT 120 (80 gal)
6 80 DHPT 102 (80 gal)
Accelera 220 E (58 gal)
Accelera 300/WHP 300 (80 gal)
BEH50DCEJSB (50 gal)
BEH80DCEJSB (80 gal)
EP6 80 DHPT 102 (80 gal)
EPX 60 DHPT (60 gal)
EPX 80 DHPT (80 gal)
FPTU 50 120 (50 gal)
FPTU 66 120 (66 gal)
FPTU 80 120 (80 gal)
GEH50DEEJSC (50 gal)
GEH50DEEJXXX (50 gal)
GEH50DFEJSR (50 gal)
GEH50DHEKSC (50 gal)
GEH80DEEJSC (80 gal)
GEH80DFEJSR (80 gal)
GEH80DHEKSC (80 gal)
GS3-45HPA-US & GAUS-1315EQTD (83 gal)
GS3-45HPA-US & GAUS-160QTA (43 gal)
GS3-45HPA-US & SAN-43SSAQA (43 gal)
GS3-45HPA-US & SAN-83SSAQA (83 gal)
GUS-45HPA-US & GAUS-1315EQTD (83 gal)
GUS-45HPA-US & SAN-83SSAQA (83 gal)
HB50ES (50 gal)
HB50RH (50 gal)
HB50RM (50 gal)
HB50RU (50 gal)
HHPT 80 120 (80 gal)
HP10-50H45DV (50 gal)
HP10-80H45DV (80 gal)
HP6 50 DHPT 120 (50 gal)
HP6 66 DHPT 120 (66 gal)
HP6 80 DHPT 120 (80 gal)
HPA051KD 120 (50 gal)
HPA052KD 120 (50 gal)
HPA067KD 120 (66 gal)
HPA068KD 120 (66 gal)
HPA081KD 120 (80 gal)
HPA082KD 120 (80 gal)
HPE10260H045DV (60 gal)
HPE10280H045DV (80 gal)
HPE2F80HD045VU 102 (80 gal)
HPE2K60HD045V (60 gal)
HPE2K60HD045V (60 gal)
HPE2K80HD045V (80 gal)
HPE2K80HD045V (80 gal)
HPE6280H045DV 102 (80 gal)
HPHE10250H045DV 102 (50 gal)
HPHE10250H045DVN 102 (50 gal)
HPHE10266H045DV 102 (66 gal)
HPHE10266H045DVN 102 (66 gal)
HPHE10280H045DV 102 (80 gal)
HPHE10280H045DVN 102 (80 gal)
HPHE2F50HD045VU 120 (50 gal)
HPHE2F66HD045VU 120 (66 gal)
HPHE2F80HD045VU 120 (80 gal)
HPHE2K50HD045V 120 (50 gal)
HPHE2K50HD045VC 120 (50 gal)
HPHE2K50HD045VN 120 (50 gal)
HPHE2K50HD045VUN 120 (50 gal)
HPHE2K66HD045V 120 (66 gal)
HPHE2K66HD045VC 120 (66 gal)
HPHE2K66HD045VUN 120 (66 gal)
HPHE2K80HD045V 120 (80 gal)
HPHE2K80HD045VC 120 (80 gal)
HPHE2K80HD045VUN 120 (80 gal)
HPHE6250H045DV (50 gal)
HPHE6266H045DV (66 gal)
HPHE6280H045DV (80 gal)
HPHE650H045DV (50 gal)
HPSE2K50HD045V 100 (WP) (50 gal)
HPSE2K50HD045VC 100 (WP) (50 gal)
HPSE2K80HD045V (80 gal)
HPSE2K80HD045VC (80 gal)
HPTU 50 120 (50 gal)
HPTU 50N 120 (50 gal)
HPTU 66 120 (66 gal)
HPTU 66N 120 (66 gal)
HPTU 80 120 (80 gal)
HPTU 80N 120 (80 gal)
HPX 50 DHPT 120 (50 gal)
HPX 50 DHPTNE 120 (50 gal)
HPX 66 DHPT 120 (66 gal)
HPX 66 DHPTNE 120 (66 gal)
HPX 80 DHPT 120 (80 gal)
HPX 80 DHPTNE 120 (80 gal)
PHPT 60 (60 gal)
PHPT 80 (80 gal)
PROPH50 T2 RH245 (50 gal)
PROPH50 T2 RH350 D (50 gal)
PROPH80 T2 RH245 (80 gal)
PROPH80 T2 RH350 D (80 gal)
PROUH50 T2 RU245 (50 gal)
PROUH50 T2 RU350 D (50 gal)
PROUH65 T2 RU350 D (65 gal)
PROUH80 T2 RU245 (80 gal)
PROUH80 T2 RU350 D (80 gal)
RE2H50R10B-1NCWT (50 gal)
RE2H80R10B-1NCWT (80 gal)
XE50T10HD50U0 (50 gal)
XE50T12EH45U0 (50 gal)
XE50T12EH45U0W (50 gal)
XE65T10HD50U0 (65 gal)
XE80T10HD50U0 (80 gal)
XE80T12EH45U0 (80 gal)
XE80T12EH45U0W (80 gal)
| HeatPumpWaterHeaterNEEARated | HtPumpWtrHtrNEEARtd | boolean | none | [6 empty] | Optional
| InputRating | InpRating | integer | Btu per h | [6 empty] | Required
| InputRatingElectric | InpRatingElec | integer | W | [6 empty] | CondRequired
| IsUniformEnergyFactorRated | IsUEFRtd | boolean | none |  | No |  |  |  |  | Required |  |  |  |  | CBECC-Com 2016 Input data model
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| RecoveryEfficiency | RE | decimal | none |  |  |  |  | 0 | 1 | CondRequired
| StandbyLossFraction | StdbyLossFrac | decimal | none | [6 empty] | Optional
| Status | Status | enumerated list | none | Existing | [5 empty] | Required |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| TankCategory | TankCat | enumerated list | none | Boiler | [5 empty] | Optional
Commercial Instantaneous (TE)
Commercial Storage (TE & SBL)
Indirect
Instantaneous
Storage
| TankExteriorInsulationRValue | TankExtInsR | decimal | h ft2 F per Btu | [6 empty] | Optional
| TankInteriorInsulationRValue | TankIntInsR | decimal | h ft2 F per Btu | [6 empty] | Optional
| TankVolume | TankVol | decimal | gal | [6 empty] | CondRequired
| TankZone | TankZn | enumerated list | none | Conditioned | [5 empty] | Optional
Outside or in Exterior Closet
Unconditioned
| ThermalEfficiency | ThrmlEff | decimal | none | [6 empty] | CondRequired
| UniformEnergyFactor | UEF | decimal | none |  | No |  |  |  |  | CondRequired
TerminalUnit
| Count | Cnt | integer | none | [6 empty] | Defaulted
| HeatingAirFlowMaximum | HtgAirFlowMax | decimal | ft3 per min | [6 empty] | CondRequired
| InducedAirZoneReference | InducedAirZnRef | reference | none | [6 empty] | CondRequired | ThermalZone |  |  | The Name of ThermalZone that air is induced from
| InductionRatio | InductionRat | decimal | none | [6 empty] | Defaulted |  |  |  | The fraction of induced air, divided by AirFlowPrimary
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| ParallelBoxFanFlowFraction | ParallelBoxFanFlowFrac | decimal | none | [6 empty] | Defaulted
| PrimaryAirFlowMaximum | PriAirFlowMax | decimal | ft3 per min | [6 empty] | Required
| PrimaryAirFlowMinimum | PriAirFlowMin | decimal | ft3 per min | [6 empty] | CondRequired
| PrimaryAirSegmentReference | PriAirSegRef | reference | none | [6 empty] | Required | AirSegment |  |  | Name of primary AirFlowSegment, or cooling AirFlowSegment for DualDuct systems
| ReheatControlMethod | ReheatCtrlMthd | enumerated list | none | DualMaximum_TU | [5 empty] | Defaulted
SingleMaximum_TU
| Status | Status | enumerated list | none | Existing | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| TotalAirFlow | TotAirFlow | decimal | ft3 per min |  | No |  |  |  |  | Defaulted
| Type | Type | enumerated list | none | ParallelFanBox | [5 empty] | Compulsory |  |  |  | TerminalUnitType | 2013 NR ACM 5.6.2 Terminal Device Data
SeriesFanBox
Uncontrolled
VAVNoReheatBox
VAVReheatBox
| ZoneServedReference | ZnServedRef | reference | none | [6 empty] | Compulsory | ThermalZone
ThermalEnergyStorage
| CapacityRated | CapRtd | decimal | Btu per h |  | No |  |  |  |  | Required
| ChargeFluidSegmentInReference | ChrgFluidSegInRef | reference |  |  | No |  |  |  |  | Required | FluidSegment
| ChargeFluidSegmentOutReference | ChrgFluidSegOutRef | reference |  |  | No |  |  |  |  | Required | FluidSegment
| DischargeFluidSegmentInReference | DischrgFluidSegInRef | reference |  |  | No |  |  |  |  | Required | FluidSegment
| DischargeFluidSegmentOutReference | DischrgFluidSegOutRef | reference |  |  | No |  |  |  |  | Required | FluidSegment
| DischargePriority | DischargePriority | enumerated list | none | Chiller | No |  |  |  |  | Required
Storage
| ModeScheduleReference | ModeSchRef | reference |  |  | No |  |  |  |  | Required |  | ThermalEnergyStorageModeScheduleDay
| StorageCapacity | StorCap | decimal | gal |  | No |  |  |  |  | Required
| StorageLocation | StorLctn | enumerated list | none | Indoor | No |  |  |  |  | Required
Outdoor
Underground
| StorageLocationSimulated | StorLctnSim | enumerated list | none | Outdoor | No |  |  |  |  | Required
Zone
| StorageZoneReference | StorageZoneReference | reference |  |  | No |  |  |  |  | CondRequired | ThermalZone
| TankHeight | TankHgt | decimal | ft |  | No |  |  |  |  | Required
| TankLengthToWidthRatio | TankLenToWdRat | decimal |  |  | No |  |  |  |  | CondRequired
| TankNodeCount | TankNodeCnt | enumerated list | none | 10 | No |  |  |  |  | Required
5
6
7
8
9
| TankRValue | TankR | decimal | h ft2 F per Btu |  | No |  |  |  |  | Required
| TankShape | TankShape | enumerated list | none | HorizontalCylinder | No |  |  |  |  | Required
Rectangular
VerticalCylinder
| Type | Type | enumerated list | none | ChilledWater | No |  |  |  |  | Required
ThermalZone
| CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted
| CoolingDesignSupplyAirTemperatureDifference | ClgDsgnSupAirTempDiff | decimal | F | [6 empty] | Defaulted
| DaylightingControlLightingFraction1 | DayltgCtrlLtgFrac1 | decimal | none | [6 empty] | Optional |  |  |  | Fraction of total zone lighitng controlled by the first DayltgCtrlRefPt | 2013 NR ACM: 5.4.5 Daylighting Controls
| DaylightingControlLightingFraction2 | DayltgCtrlLtgFrac2 | decimal | none | [6 empty] | Optional |  |  |  | Fraction of total zone lighitng controlled by the second DayltgCtrlRefPt | 2013 NR ACM: 5.4.5 Daylighting Controls
| DaylightingControlType | DayltgCtrlType | enumerated list | none | Continuous | [5 empty] | Optional |  |  |  | The type of control that is used to control the electric lighting in response to daylight available at the reference point. | 2013 NR ACM: 5.4.5 Daylighting Controls
ContinuousPlusOff
None
SteppedDimming
SteppedSwitching
| DaylightingMinimumDimmingLightFraction | DayltgMinDimLtgFrac | decimal | none | [6 empty] | Optional |  |  |  | Minimum light output of controlled lighting when fully dimmed. Minimum light fraction = (Minimum light output) / (Rated light output). | 2013 NR ACM: 5.4.5 Daylighting Controls
| DaylightingMinimumDimmingPowerFraction | DayltgMinDimPwrFrac | decimal | none | [6 empty] | Optional |  |  |  | The minimum power fraction when controlled lighting is fully dimmed. Minimum power fraction = (Minimum power) / (Full rated power). | 2013 NR ACM: 5.4.5 Daylighting Controls
| DaylightingNumberOfControlSteps | DayltgNumCtrlSteps | integer | none | [6 empty] | Optional |  |  |  | For ZnDayltgCtrlType = SteppedDimming or SteppedDimmingPlusOff, the number of equally spaced control steps | 2013 NR ACM: 5.4.5 Daylighting Controls
| Description | Desc | string | none | [6 empty] | Optional |  |  |  | This is a brief description of the object that summarizes its essential characteristics
| ExhaustSystemReference | ExhSysRef | reference | none | [6 empty] | Optional | AirSystem; ZoneSystem
| HeatingDesignMaximumFlowFraction | HtgDsgnMaxFlowFrac | decimal | none | [6 empty] | Defaulted
| HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted
| HeatingDesignSupplyAirTemperatureDifference | HtgDsgnSupAirTempDiff | decimal | F | [6 empty] | Defaulted
| HVACZoneCount | HVACZnCnt | integer | none | [6 empty] | Defaulted
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| OperableWindowInterlock | OperableWinInterlock | boolean | none | [6 empty] | CondRequired
| OperableWindowsHaveInterlock | OperableWinHaveInterlock | boolean | none | [6 empty] | CondRequired
| PrimaryAirConditioningSystemPriority | PriAirCondgSysPriority | integer | none |  |  | 2 | 2 |  |  | Defaulted
| PrimaryAirConditioningSystemReference | PrimAirCondgSysRef | reference | none |  |  |  | 2 |  |  | CondRequired | AirSystem; ZoneSystem |  |  | Defines the primary HVAC system that provides heating or cooling to the space. The same system might also provide ventilation air to the space. In this case, the VentSysRef property should reference the same system name. Both AirSystem and ZoneSystem are valid object assignments for this property. However, if the ventilation and primary air conditioning systems are different, the ventilation system must be defined as an AirSystem, and the primary air conditioning system defined as a ZoneSystem/
| ReturnPlenumZoneReference | RetPlenumZnRef | reference | none | [6 empty] | Optional | ThermalZone |  |  |  | 2013 NR ACM: 2.3.2
| SupplyPlenumZoneReference | SupPlenumZnRef | reference | none | [6 empty] | Optional | ThermalZone |  |  |  | 2013 NR ACM: 2.3.2
| Type | Type | enumerated list | none | Conditioned | [5 empty] | Defaulted |  |  |  | Defines the type of conditioning in the thermal zone | 2013 NR ACM 5.3 Thermal Zones Thermal Zone type values are: directly conditioned, indirectly conditioned, unconditioned or plenum
Plenum
Unconditioned
| VentilationControlMethod | VentCtrlMthd | enumerated list | none | CO2Sensors | [5 empty] | Defaulted |  |  |  | The method used to determine outside air ventilation needed for each hour in the simulation | 2013 NR ACM 5.6.5.4 Outdoor Air Ventilation Ventilation Control Method
Fixed
| VentilationSource | VentSrc | enumerated list | none | Forced | [5 empty] | Required
Natural
None
| VentilationSpecificationMethod | VentSpecMthd | enumerated list | none | AirChangesPerHour | [5 empty] | Defaulted
FlowPerArea
FlowPerPerson
FlowPerZone
Maximum
NoVentilation
Sum
| VentilationStandardDescription | VentStdDesc | string | none |  | No |  |  |  |  | CondRequired
| VentilationSystemPriority | VentSysPriority | integer | none | [6 empty] | Defaulted
| VentilationSystemReference | VentSysRef | reference | none | [6 empty] | CondRequired | AirSystem; ZoneSystem |  |  | Defines the HVAC system that provides ventlation air to the space. The same system might also be the primary source of space heating/cooling. In this case, the PrimAirCondgSysRef property should reference the same system name. Both AirSystem and ZoneSystem are valid object assignments for this property. However, if the ventilation and primary air conditioning systems are different, the ventilation system must be defined as the only AirSystem serving the zone.
WaterHeater
| CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | Cooling capacity of water heater equipment at prescribed rating conditions. | 2013 NR ACM
| CompressorLocation | CprsrLoc | integer | none |  | No |  |  |  |  | CondRequired
| CompressorZoneReference | CprsrZnRef | reference | none |  | No |  |  |  |  | CondRequired | ThermalZone
| Count | Cnt | integer | none | [6 empty] | Defaulted |  |  |  | The number of WaterHeaters in the water heating system that are identical. Because all the features are the same in each unit, the Count can be used as a multiplier for calculating values like capacity of all the units
| DraftFanPower | DraftFanPwr | decimal | W | [6 empty] | CondRequired
| ElectricalIgnition | ElecIgnit | boolean | none | [6 empty] | Optional
| EnergyFactor | EF | decimal | none | [6 empty] | CondRequired |  |  |  | The ratio of the energy delivered by the water heater divided by the energy used, in the same units.This property is used for Energy Factor values and the new Uniform Energy Factor values which has a more sophisticated approach to establishing efficiency as Energy Factor. | 2013 NR ACM 5.9.1.2 Water Heaters Energy Factor; CF1R-PRF
| FirstHourRating | FirstHrRating | decimal | gal |  | No |  |  |  |  | CondRequired
| FlowRate | FlowRt | decimal | gal per min |  | No |  |  |  |  | CondRequired
| FluidSegmentMakeupReference | FluidSegMakeupRef | reference | none | [6 empty] | Required | FluidSegment
| FluidSegmentOutReference | FluidSegOutRef | reference | none |  | No |  |  |  |  | Required | FluidSegment |  |  | The name of the fluid segment that takes fluid out of HVAC equipment
| FluidSystemCount | FluidSysCnt | integer | none | [6 empty] | Optional |  |  |  |  | 2013 NR ACM sections 2.3.1 and 5.3 The number of duplicate HVAC systems represented by the modeled system.
| FuelSource | FuelSrc | enumerated list | none | Gas | [5 empty] | Required |  |  |  |  | CF1R-NCB/ALT/ADD-01
| InputPower | InpPwr | decimal | kW |  | No |  |  |  |  | CondRequired
| MinimumCapacity | MinCap | decimal | Btu per h | [6 empty] | Defaulted
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| RecoveryEfficiency | RE | decimal | none |  |  |  |  | 0 | 1 | CondRequired
| StandbyLossFraction | StdbyLossFrac | decimal | none | [11 empty] | The tank standby loss fraction for storage tanks.
| Status | Status | enumerated list | none | Existing | [5 empty] | Required |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| StorageCapacity | StorCap | decimal | gal | [6 empty] | Required
| StorageCapacitySimulated | StorCapSim | decimal | gal |  | No |  |  |  |  | Optional
| StorageLocation | StorLoc | integer | none |  | No |  |  |  |  | CondRequired
| StorageZoneReference | StorZnRef | reference | none |  | No |  |  |  |  | CondRequired | ThermalZone
| TankHeightSimulated | TankHgtSim | decimal | ft |  | No |  |  |  |  | CondRequired
| ThermalEfficiency | ThrmlEff | decimal | none | [6 empty] | CondRequired
| Type | Type | enumerated list | none | Conventional | [5 empty] | Defaulted
HeatPumpPackaged
HeatPumpSplit
| UniformEnergyFactor | UEF | decimal | none |  | No |  |  |  |  | CondRequired
ZoneSystem
| CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted |  |  |  | The design cooling temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also is cold deck temp | 2013 NR ACM 5.7.2.2 Cooling Control
| Count | Cnt | integer | none | [6 empty] | Defaulted |  |  |  | The number of duplicate HVAC systems represented by the modeled system. | 2013 NR ACM sections 2.3.1 and 5.3
| Description | Desc | string | none | [6 empty] | Optional |  |  |  | This is a brief description of the object that summarizes its essential characteristics
| DuctInsulation | DuctIns | enumerated list | h ft2 F per Btu | [6 empty] | Optional |  |  | dtyp:EnumerationConstantPermissive | This is the required R Value for ducts in lowrise residential buildings | Required for the residential prescriptive certificate of compliance.
| DuctLocation | DuctLctn | enumerated list | none | Conditioned | [5 empty] | Required |  |  |  |  | CF2R-MCH01a, old CF1RPerNAA
None
Other
Unconditioned
| DuctStatus | DuctStatus | integer | none |  | No |  |  |  |  | Defaulted
| ExhaustControlMethod | ExhCtrlMthd | enumerated list | none | COControl | [5 empty] | Defaulted
ConstantFlowConstantSpeedFan
NoCOControl
VariableFlowConstantSpeedFan
VariableFlowVariableSpeedFan
| ExhaustOperationMode | ExhOperMode | enumerated list | none | CoupledToSystem | [5 empty] | Defaulted
DecoupledFromSystem
| ExhaustSystemType | ExhSysType | enumerated list | none | CommercialKitchen | [5 empty] | Defaulted
General
Laboratory
ParkingGarage
| FanControl | FanCtrl | enumerated list | none | Continuous | [5 empty] | Defaulted
Cycling
| HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted |  |  |  | The design heating temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also hot deck temp | 2013 NR ACM 5.7.2.3 Heating Control;
| HVACAutoSizing | HVACAutoSizing | boolean | none | [6 empty] | Optional
| IsComplexSystem | IsComplexSystem | boolean | none | [6 empty] | Defaulted
| Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
| Status | Status | enumerated list | none | Existing | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
| SubType | SubType | enumerated list | none | Floor | [5 empty] | Defaulted |  |  |  | Air System equipment subtype | 2013 NR ACM
Other
Room
SinglePackaged1Phase
SinglePackaged3Phase
Split1Phase
Split3Phase
Wall
| Type | Type | enumerated list | none | Baseboard | [5 empty] | Compulsory |  |  |  | ZoneSystemType | 2013 NR ACM: 5.7 HVAC Secondary Systems; Tables 15 and N2-16 to N2-23
Exhaust
FPFC
Furnace
MiniSplitAC
MiniSplitHP
PTAC
PTHP
PassiveBeam
SPVAC
SPVHP
SZAC
SZHP
WSHP

## HvacProperties
CBECC NR Term | CBECC NR Term Short Form | DataType | Units | HvacEnumerations | CBECC NR Array | XSD ELEMATTRIB minOccurs | XSD ELEMATTRIB maxOccurs | XSD RESTRICT minInclusive | XSD RESTRICT maxInclusive | Compliance Use | Referenced Objects | Referenced Building Objects | XSD Base Type | Definition | Standards Reference | Calculations And Rules | CBECC NR Different Data Type
AFUE | AFUE | decimal | none | [6 empty] | CondRequired |  |  |  | The full load efficiency of a boiler or furnace at AFUE rated conditions | 2013 NR ACM: 5.7.6.4 Furnace equation 41 5.8.1 Boilers equation 59
AggregatedHotWaterHeatingRate | AggHotWtrHtgRt | decimal | none | [6 empty] | Required |  |  |  |  | This is the aggregated hot water heating rate for the PROPOSED (at the Fluid System level) and BASELINE (at the Building level).
AggregatedHotWaterHeatingScheduleReference | AggHotWtrHtgSchRef | reference | none | [6 empty] | Required |  | Schedule |  | The Aggregation of a fractional schedule reflecting the time pattern of water heating use. This input modifies the hot water heating rate.
AirFlowCapacity | AirFlowCap | decimal | ft3 per min | [6 empty] | Required
AirSegmentReturnReference | AirSegRetRef | reference | none | [6 empty] | Optional | AirSeg
AirSegmentSupplyReference | AirSegSupRef | reference | none | [6 empty] | Required | AirSeg
AmbientCondition | AmbCond | enumerated list | none | Conditioned | [5 empty] | CondRequired
Unconditioned
AngleFromTrueNorth | AngleFromTrueNorth | decimal | deg arc | [6 empty] | Optional
AnnualSolarFraction | AnnualSolFrac | decimal | none | [6 empty] | Optional
AnnualSolarFraction | AnnualSolFrac | decimal | none | [6 empty] | Defaulted
Area | Area | integer | ft2 |  | No
AuxiliaryPower | AuxPwr | decimal | W | [6 empty] | Optional
AuxiliaryPower | AuxPwr | decimal | W | [6 empty] | Defaulted
AuxiliaryPower | AuxPwr | decimal | W | [6 empty] | Defaulted
AuxilliaryPower | AuxPwr | decimal | W | [6 empty] | Optional
AvailabiltyScheduleReference | AvailSchRef | reference | none | [6 empty] | Defaulted |  | Schedule |  |  | 2013 NR ACM: 5.7
BaselineResidentialWaterHeaterReference | BaseResWtrHtrRef | reference | none | [6 empty] | Optional | ResWtrHtr
BF_fAirFlowCurveReference | BF_fAirFlowCrvRef | reference | none | [6 empty] | NotInput |  |  |  | The bypass factor airflow curve is normally a quadratic curve | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Adjustment Curve, Table 51
BF_fPLRCurveReference | BF_fPLRCrvRef | reference | none | [6 empty] | NotInput |  |  |  | The bypass factor PLR curve is normally a linear curve | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Adjustment Curve, equation 20 Table 53
BF_fTemperatureCurveReference | BF_fTempCrvRef | reference | none | [6 empty] | NotInput |  |  |  | The bypass factor temperature curve is normally a double quadratic curve | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Adjustment Curve, Table 52
BFDesign | BFDsgn | decimal | none | [6 empty] | NotInput |  |  |  | The default design value assigned to the ratio of air that bypasses the cooling coil at design conditions to the total system airflow. | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Table 50 Default Coil Bypass Factors
BFRated | BFRtd | decimal | none | [6 empty] | NotInput |  |  |  | The rated coil bypass factor at ARI conditions and is used to calculate the adjusted coil bypass factor value | 2013 NR ACM 5.7.5 Cooling Systems Coil Bypass Factor Adjustment Curve, Equations 17
Brand | Brand | string | none |  | No | [7 empty] | dtyp:String50Char
BypassMinimumEfficiencyCheck | BypassMinEffCheck | boolean | none | [6 empty] | Defaulted
CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | Required |  |  |  | The rated measure of energy ouput of Boilers. | 2013 NR ACM: 5.8.1 Boilers Boiler Design Capacity;
CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | Required |  |  |  | Cooling capacity of chiller equipment at prescribed rating conditions. | 2013 NR ACM 5.8.2 Chillers Chiller Rated Capacity equations
CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | Required |  |  |  | The rated cooling capacity at CTI test conditions. | 2013 NR ACM 5.8.3 Cooling Towers Cooling Tower Capacity
CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | Cooling capacity of water heater equipment at prescribed rating conditions. | 2013 NR ACM
CapacityRated | CapRtd | decimal | Btu per h | [6 empty] | Required
CapacityRated | CapRtd | decimal | Btu per h |  | No |  |  |  |  | Required
CapacitySensibleAdjusted | CapSensAdj | decimal | Btu per h | [6 empty] | NotInput |  |  |  | Adjusts the CoilCapSensibleRated for supply fan heat | 2013 NR ACM 5.7.5 Cooling Systems Total Cooling Capacity Equation 12
CapacityTotalGrossRated | CapTotGrossRtd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The total cooling capacity of a coil at rated conditions | 2013 NR ACM 5.7.5 Cooling Systems
CapacityTotalGrossRated | CapTotGrossRtd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The cooling or heating capacity of HVAC equipment at prescribed rating conditions. | 2013 NR ACM: 5.8.1 Boilers Boiler Design Capacity; 5.8.2 Chillers Chiller Rated Capacity equations; 5.8.3 Cooling Towers Cooling Tower Capacity
CapacityTotalNetRated | CapTotNetRtd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The total cooling capacity of a coil at design conditions | 2013 NR ACM 5.7.5 Cooling Systems
CapacityTotalNetRated | CapTotNetRtd | decimal | Btu per h | [6 empty] | CondRequired
CapacityTotalRatedStageFraction | CapTotRtdStageFrac | decimal | none |  | Yes | 0 | 2 | 0 | 1 | Defaulted |  |  |  | Total cooling capacity of each cooling stage, at ARI rated conditions. The capacity is expressed as an array, with each entry a fraction of the total rated cooling capacity for the unit. | 2013 NR ACM 5.7.5.2
CellCount | CellCnt | decimal | none | [6 empty] | Defaulted |  |  |  | The number of cells in the cooling tower. Each cell has its own fan, water flow allowing for responding to lower load conditions | 2013 NR ACM: 5.8.3 Cooling Towers Cooling Tower number of Cells;
CentralSystem | CentralSys | boolean | none | [6 empty] | Optional
CentralSystem | CentralSys | boolean | none | [6 empty] | Optional
CentrifugalType | CentType | enumerated list | none | AirFoil | [5 empty] | Defaulted |  |  |  | Defines the mechanism of a centrifugal fan | 2013 NR ACM 5.7.3 Fan Systems Part Load Power Curve Table 46 – Fan Curve Default Values
BackwardInclined
ForwardCurved
ChargeFluidSegmentInReference | ChrgFluidSegInRef | reference |  |  | No |  |  |  |  | Required | FluidSeg
ChargeFluidSegmentOutReference | ChrgFluidSegOutRef | reference |  |  | No |  |  |  |  | Required | FluidSeg
ChilledWaterEnteringTemperatureDesign | CHWEntTempDsgn | decimal | F | [6 empty] | Required
ChilledWaterFluidSegmentInReference | CHWFluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSeg
ChilledWaterFluidSegmentOutReference | CHWFluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSeg
ChilledWaterLeavingTemperatureDesign | CHWLvgTempDsgn | decimal | F | [6 empty] | Required
Classification | Class | enumerated list | none | Axial | [5 empty] | Defaulted |  |  |  | The classification of the fan design. | 2013 NR ACM: 5.7.3.2
Centrifugal
CoilCoolingCapacity | CoilClgCap | decimal | Btu per h | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems also has Total Cooling Capacity units: cooling tons (12,000 BTU/h per ton) defined as the total cooling capacity (both sensible and latent) of a cooling coil or packaged DX system.
CoilCoolingReference | CoilClgRef | reference | none | [7 empty] | AirSys
CoilHeadDesign | CoilHdDsgn | decimal | ft H2O | [6 empty] | Defaulted
CoilHeatingCapacity | CoilHtgCap | decimal | Btu per h | [6 empty] | Defaulted
CoilHeatingReference | CoilHtgRef | reference | none | [7 empty] | AirSys
CollectorType | CollectorType | string | none |  | No | [7 empty] | dtyp:String50Char
CombustionEfficiency | CombEff | decimal | none | [6 empty] | CondRequired |  |  |  | The measure of how much energy is extracted from the fuel and is the ratio of heat transferred to the combustion air divided by the heat input of the fuel. | 2013 NR ACM: 5.8.1 Boilers Boiler Efficiency Type
CompressorLocation | CprsrLoc | integer | none |  | No |  |  |  |  | CondRequired
CompressorZone | CprsrZn | enumerated list | none | Conditioned | No |  |  |  |  | CondRequired
Outside or in Exterior Closet
Unconditioned
CompressorZoneReference | CprsrZnRef | reference | none |  | No |  |  |  |  | CondRequired | ThrmlZn
CondenserEvapCooledPower | CdnsrEvapCooledPwr | decimal | W | [6 empty] | Required |  |  |  | The power of the evaporative precooling unit. This includes any pump(s) and/or fans that are part of the precooling unit. | 2013 NR ACM 5.7.5.5
CondenserEvapCooledTemperatureMaximum | CdnsrEvapCooledTempMax | decimal | F | [6 empty] | Required |  |  |  | The threshold outside air dry-bulb temperature below which evaporative condenser operates. | 2013 NR ACM 5.7.5.5
CondenserEvapCooledTemperatureMinimum | CdnsrEvapCooledTempMin | decimal | F | [6 empty] | Required |  |  |  | The threshold outside air dry-bulb temperature above which evaporative condenser operates. | 2013 NR ACM 5.7.5.5
CondenserFluidSegmentInReference | CndsrInRef | reference | none | [6 empty] | CondRequired | FluidSeg
CondenserFluidSegmentOutReference | CndsrOutRef | reference | none | [6 empty] | CondRequired | FluidSeg
CondenserNominalCoolingCapacity | CndsrNominalClgCap | decimal | cooling ton (12,000 Btu per h) | [9 empty] | dtyp:Decimal1Place |  | CF2RMch01, MCH20a
CondenserPowerRated | CndsrPwrRtd | decimal | kW | [6 empty] | Optional |  |  |  | The energy usage of the condenser fan(s) at design conditions on an air-cooled chiller. This unit should only be used for chillers composed of separate evaporator and condenser sections where the fan energy is not part of the chiller COP. | 2013 NR ACM: 5.8.2 Chillers
CondenserTemperatureFactor | CndsrTempFac | decimal | F | [6 empty] | Optional |  |  |  | The number of degrees F to add to the design wet bulb or dry bulb temperatures to calculate the condensing temperature of the refrigerant in condensers in a RefrigerationSystem. | 2013 Title 24 Part 6 Section 120.6 (a) Mandatory Requirements for Refrigerated Warehouses 4. Condensers 2. Design saturated Condensing temperatures
CondenserTemperatureSaturated | CndsrTempSaturated | decimal | F | [6 empty] | Optional |  |  |  | The temperature at which the air cooling the condenser is saturated. This is evaluated in mandatory measures for condensers used in refrigeration equipment. | 2013 Title 24 Part 6 Section 120.6 (a) Mandatory Requirements for Refrigerated Warehouses 4. Condensers 2. Design saturated Condensing temperatures
CondenserTemperatureSetpointMinimum | CndsrTempSetptMin | decimal | F | [6 empty] | Optional |  |  |  | Minimum condensing temperature setpoint for Condensers in refrigerated warehouses, and used to control the speed of all condenser fans | 2013 Title 24 Part 6 Section 120.6 (a) Mandatory Requirements for Refrigerated Warehouses 4. Condensers C and D
CondenserTotalHeatOfRejection | CndsrTotHtOfRej | decimal | Btu per h | [6 empty] | Optional |  |  |  | A measure of the capacity of a refrigeration condenser in Btu per hour. Often expressed in MBH or 1000 BTU per hour, the total heat of rejection is used to calculate mandatory minimum efficiency of some types of fan-powered condensers used in refrigeration systems | 2013 Title 24 Part 6 Section 120.6 (a) Mandatory Requirements for Refrigerated Warehouses Table Fan-Powered Condensers Minimum Efficiency Requirements
CondenserType | CndsrType | enumerated list | none | Air | [5 empty] | Defaulted |  |  |  | Defines the type condenser used for a cooling or heating coil
WaterSource
CondenserType | CndsrType | enumerated list | none | Air | [5 empty] | Required |  |  |  | Defines the type condenser used for a chiller
Fluid
CondenserWaterEnteringTemperatureDesign | CWEntTempDsgn | decimal | F | [6 empty] | Required
CondenserWaterFluidSegmentInReference | CWFluidSegInRef | reference | none | [6 empty] | Required | FluidSeg
CondenserWaterFluidSegmentOutReference | CWFluidSegOutRef | reference | none | [6 empty] | Required | FluidSeg
CondenserWaterLeavingTemperatureDesign | CWLvgTempDsgn | decimal | F | [6 empty] | Required
ControlMethod | CtrlMthd | enumerated list | none | ConstantVolume | [5 empty] | Required |  |  |  |  | 2013 NACR ACM 5.7.3.2,
Dampers
InletVanes
TwoSpeed
VariablePitchBlades
VariableSpeedDrive
ControlSystemType | CtrlSysType | enumerated list | none | DDCToZone | [5 empty] | Defaulted |  |  |  | The type of control system for multizone HVAC systems and their related equipment.This input affects the proposed design system specification for zone levelcontrols, supply air temperature reset controls, ventilation controls and fanand pump static pressure part-load curves. | 2013 NR ACM: 5.6.5.1, 5.7.2.1 The type of control system for multizone HVAC systems and their related equipment.This input affects the proposed design system specification for zone levelcontrols, supply air temperature reset controls, ventilation controls and fanand pump static pressure part-load curves.
Other
ControlType | CtrlType | enumerated list | none | DDC | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM
Other
ControlZoneReference | CtrlZnRef | reference | none | [6 empty] | CondRequired | ThrmlZn
CoolingAvailabilityScheduleReference | ClgAvailSchRef | reference | none | [6 empty] | Optional |  | Schedule |  |  | 2013 NR ACM: 5.7.2 System Controls
CoolingAvailabilityScheduleReference | ClgAvailSchRef | reference | none | [6 empty] | Optional |  | Schedule |  |  | 2013 NR ACM: 5.7.2 System Controls
CoolingControl | ClgCtrl | enumerated list | none | Fixed | [5 empty] | Defaulted |  |  |  | Defines the cooling supply air temperature control method used for systems with cooling coils | 2013 NR ACM: 5.7.2.2 Cooling Control
FixedDualSetpoint
NoSATControl
OutsideAirReset
Scheduled
WarmestResetFlowFirst
WarmestResetTemperatureFirst
CoolingDesignFlow | ClgDsgnFlow | decimal | none | [6 empty] | Optional |  |  |  | The design zone cooling air flow rate in cubic meters per second. If a thermal zone has cooling unmet load hours, the first step in addressing this issue is to increase the zone design air flow. | 2013 NR ACM 2.6.2
CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted |  |  |  | The design cooling temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also is cold deck temp | 2013 NR ACM 5.7.2.2 Cooling Control
CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted
CoolingDesignSupplyAirTemperature | ClgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
CoolingDesignSupplyAirTemperatureDifference | ClgDsgnSupAirTempDiff | decimal | F | [6 empty] | Defaulted
CoolingFixedSupplyAirTemperature | ClgFixedSupTemp | decimal | F | [6 empty] | Defaulted
CoolingFlowSizingFactor | ClgFlowSizingFac | decimal | none | [6 empty] | Optional |  |  |  | This input is a zone level cooling sizing ratio. The zone design cooling air flow rates and loads will be multiplied by the number input in this field. | 2013 NR ACM 2.6.2
CoolingLatentEffectiveness100 | ClgLatEff100 | decimal | [7 empty] | Defaulted
CoolingLatentEffectiveness75 | ClgLatEff75 | decimal | [7 empty] | Defaulted
CoolingSensibleEffectiveness100 | ClgSensEff100 | decimal | [7 empty] | Defaulted
CoolingSensibleEffectiveness75 | ClgSensEff75 | decimal | [7 empty] | Defaulted
CoolingSetPointScheduleReference | ClgSetptSchRef | reference | none | [6 empty] | CondRequired |  | Schedule
CoolingSupplyTemperature | ClgSupTemp | decimal | F | [6 empty] | Optional |  |  |  | The design cooling temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also is cold deck temp | 2013 NR ACM 5.7.2.2 Cooling Control
CoolingTotalEffectiveness100 | ClgTotEff100 | decimal | [7 empty] | Defaulted
CoolingTotalEffectiveness75 | ClgTotEff75 | decimal | [7 empty] | Defaulted
CoolResetOutdoorHigh | ClRstOutdrHi | decimal | F | [6 empty] | Defaulted
CoolResetOutdoorLow | ClRstOutdrLow | decimal | F | [6 empty] | Defaulted
CoolResetSupplyHigh | ClRstSupHi | decimal | F | [6 empty] | Defaulted
CoolResetSupplyLow | ClRstSupLow | decimal | F | [6 empty] | Defaulted
Coordinate | Coord | decimal | ft | [6 empty] | Required |  |  |  | The x, y or z distance measured from an origin.
COP | COP | decimal | none | [6 empty] | Optional |  |  |  | The efficiency of the refrigeration equipment expressed as the ARI rated coefficient of performance | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment
COP | COP | decimal | none | [6 empty] | CondRequired |  |  |  | The efficiency of the chiller expressed as the ARI rated coefficient of performance | 2013 NR ACM 5.8.2 Chillers Chiller Rated Efficiency
Count | Cnt | integer | none | [6 empty] | Defaulted |  |  |  | The number of WaterHeaters in the water heating system that are identical. Because all the features are the same in each unit, the Count can be used as a multiplier for calculating values like capacity of all the units
Count | Cnt | integer | none | [6 empty] | Optional |  |  |  | The number of identical HVAC equipment in the project. Because all the features are the same in each unit, the Count can be used as a multiplier for calculating values like capacity of all the units | 2013 NR ACM: 5.8.1 Boilers Number of Identical Boiler Units; 5.8.2 Chillers Number of Identical Chiller Units; 5.8.5 Pumps Number of pumps
Count | Cnt | integer | none | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM sections 2.3.1 and 5.3 The number of duplicate HVAC systems represented by the modeled system.
Count | Cnt | integer | none | [6 empty] | Defaulted |  |  |  | The number of duplicate HVAC systems represented by the modeled system. | 2013 NR ACM sections 2.3.1 and 5.3
Count | Cnt | integer | none | [6 empty] | Defaulted
Count | Cnt | integer | none | [6 empty] | Required |  |  |  | The number of RecirculationWaterHeaters
Count | Cnt | integer | none | [6 empty] | Optional |  |  |  |  | 2013 NR ACM sections 2.3.1 and 5.3 The number of duplicate HVAC systems represented by the modeled system.
DaylightingControlLightingFraction1 | DayltgCtrlLtgFrac1 | decimal | none | [6 empty] | Optional |  |  |  | Fraction of total zone lighitng controlled by the first DayltgCtrlRefPt | 2013 NR ACM: 5.4.5 Daylighting Controls
DaylightingControlLightingFraction2 | DayltgCtrlLtgFrac2 | decimal | none | [6 empty] | Optional |  |  |  | Fraction of total zone lighitng controlled by the second DayltgCtrlRefPt | 2013 NR ACM: 5.4.5 Daylighting Controls
DaylightingControlType | DayltgCtrlType | enumerated list | none | Continuous | [5 empty] | Optional |  |  |  | The type of control that is used to control the electric lighting in response to daylight available at the reference point. | 2013 NR ACM: 5.4.5 Daylighting Controls
ContinuousPlusOff
None
SteppedDimming
SteppedSwitching
DaylightingMinimumDimmingLightFraction | DayltgMinDimLtgFrac | decimal | none | [6 empty] | Optional |  |  |  | Minimum light output of controlled lighting when fully dimmed. Minimum light fraction = (Minimum light output) / (Rated light output). | 2013 NR ACM: 5.4.5 Daylighting Controls
DaylightingMinimumDimmingPowerFraction | DayltgMinDimPwrFrac | decimal | none | [6 empty] | Optional |  |  |  | The minimum power fraction when controlled lighting is fully dimmed. Minimum power fraction = (Minimum power) / (Full rated power). | 2013 NR ACM: 5.4.5 Daylighting Controls
DaylightingNumberOfControlSteps | DayltgNumCtrlSteps | integer | none | [6 empty] | Optional |  |  |  | For ZnDayltgCtrlType = SteppedDimming or SteppedDimmingPlusOff, the number of equally spaced control steps | 2013 NR ACM: 5.4.5 Daylighting Controls
DefrostControl | DefrostCtrl | enumerated list | none | ExhaustAirRecirculation | [5 empty] | Defaulted
ExhaustOnly
MinimumExhaustTemperature
None
DefrostControlTemperature | DefrostCtrlTemp | decimal | F | [6 empty] | Defaulted
Description | Desc | string | none | [6 empty] | Optional |  |  |  | This is a brief description of the object that summarizes its essential characteristics
DesignGeneratorFluidDeltaTemperature | DsgnGenFluidDelT | decimal | F | [6 empty] | Defaulted
DesignSupplyWaterTemperature | DsgnSupWtrTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
DesignSupplyWaterTemperatureDeltaT | DsgnSupWtrTempDelT | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
DesignWBTemperature | DsgnWBTemp | decimal | F | [6 empty] | Optional
DischargeFluidSegmentInReference | DischrgFluidSegInRef | reference |  |  | No |  |  |  |  | Required | FluidSeg
DischargeFluidSegmentOutReference | DischrgFluidSegOutRef | reference |  |  | No |  |  |  |  | Required | FluidSeg
DischargePriority | DischargePriority | enumerated list | none | Chiller | No |  |  |  |  | Required
Storage
DistributionType | DistType | enumerated list | none | DemandControl | [5 empty] | CondRequired |  |  |  |  | NRCV-PLB22
NoControlContinuousPumping
NoLoopsNoCentralPump
TemperatureModulation
TemperatureModulationMonitoring
DraftFanHorsePower | DraftFanHp | decimal | hp | [6 empty] | CondRequired |  |  |  | Nameplate horsepower of the draft fan motor (HP), | 2013 NR ACM 5.8.3
DraftFanPower | DraftFanPwr | decimal | W | [6 empty] | CondRequired
DraftType | DraftType | enumerated list | none | Condensing | [5 empty] | CondRequired |  |  |  | How combustion airflow is drawn through the boiler | 2013 NR ACM 5.8.1 Boilers equation 59
MechanicalNoncondensing
Natural
DriveEfficiency | DrvEff | decimal | none | [6 empty] | Optional |  |  |  | A measure of how much power transferred through the drive to the fan is lost as heat. DriveEff is one of the parameters used in calculating FanPowerIndex for performance compliance. | 2013 NR ACM 5.7.3.2 Supply Fans Supply Fan Brake Horsepower
DuctConductionLoss | DuctCndctLoss | decimal | Btu per h F | [6 empty] | NotInput |  |  |  | The heat loss rate of ducts which varies depending on duct length and surrounding environment. | ???
DuctInsulation | DuctIns | enumerated list | h ft2 F per Btu | [6 empty] | Optional |  |  | dtyp:EnumerationConstantPermissive | This is the required R Value for ducts in lowrise residential buildings | Required for the residential prescriptive certificate of compliance.
DuctLeakageAllowed | DuctLkgeAllow | decimal | ft3 per min | [6 empty] | Optional |  |  |  | This is the allowable duct leakage rate for residential or nonresidential buildings. For residential low-rise buildings it is calculated using different inputs depending on AHU airflow determination method. | 2013 NR ACM CoolingSystems: 5.7.5 Cooling Systems - Distribution System 2013 residential compliance reports e.g. CF2R-Mech20a
DuctLeakageFactor | DuctLkgeFac | decimal | none | [6 empty] | Optional |  |  |  | A constant used to calculate distribution efficiency | 2013 NR ACM CoolingSystems: 5.7.5 Cooling Systems - Distribution System Efficiency includes duct leakage factor, Residential compliance documents e.g. CF2R-Mech20a
DuctLocation | DuctLctn | enumerated list | none | Conditioned | [5 empty] | Required |  |  |  |  | CF2R-MCH01a, old CF1RPerNAA
None
Other
Unconditioned
DuctLocation | DuctLctn | enumerated list | none | Conditioned | [5 empty] | Required |  |  |  |  | CF2R-MCH01a, old CF1RPerNAA
None
Other
Unconditioned
DuctStatus | DuctStatus | integer | none |  | No |  |  |  |  | Defaulted
DuctSurfaceArea | DuctSurfArea | decimal | ft2 | [6 empty] | Optional |  |  |  | Required in order to calculate the efficiency of the distribution system. It is also used in applying duct leakage requirements. | 2013 NR ACM 5.7.5 Cooling Systems - Distribution System Efficiency requires SurfaceArea for calculating efficiency
DuctSurfaceAreaCoefficient | DuctSurfAreaCoef | decimal | none | [6 empty] | Optional |  |  |  | Used in the default equations for calculating duct SurfaceArea. SurfaceAreaCoefficient are unique depending on if the DistributionSystem.Function is supply or return. | 2008 Appendix NA2.3.3.1 Default Duct Surface Area
DuctSurfaceAreaOutdoors | DuctSurfAreaOutdr | decimal | ft2 | [6 empty] | Optional |  |  |  |  | 2013 NR ACM 5.7.5.2
DuctThermalResistance | DuctThrmlR | decimal | h ft2 F per Btu | [6 empty] | NotInput |  |  |  | The R-value of ducts used in calculating distribution efficiency. The requirement is different for new and existing ducts in a project. | 2013 NR ACM 5.7.5 Cooling Systems - Distribution System Efficiency includes R-values for the supply duct and the return duct. 2008 NA2.3.5 Duct Wall Thermal Resistance
DXCrankcaseControlTemperature | DXCrankcaseCtrlTemp | decimal | F | [6 empty] | Optional
DXCrankcaseHeatCapacity | DXCrankcaseHtCap | decimal | Btu per h | [6 empty] | Optional |  |  |  | The capacity of the electric resistance heater in the crank case of a direct expansion (DX) compressor. The crank case heater operates only when the compressor is off. | 2013 NR ACM 5.7.6.5
DXEER | DXEER | decimal | Btu per h W | [6 empty] | CondRequired |  |  |  | The energy efficiency ratio (EER) of net cooling capacity (in Btu/hr) to total rate of electrical energy input (in watts), of cooling equipment under designated operating conditions. | 2013 NR ACM 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency, equations 21 and 22
DXIEER | DXIEER | decimal | Btu per h W | [6 empty] | CondRequired
DXSEER | DXSEER | decimal | Btu per h W | [6 empty] | CondRequired |  |  |  | The Seasonal Energy Efficiency Ratio (SEER) of the coil in a DX cooling system | 5.7.5.2 Direct Expansion Direct Expansion Cooling Efficiency
EconomizerControlMethod | EconoCtrlMthd | enumerated list | none | DifferentialDryBulb | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.4.2 Air Side Economizers
DifferentialDryBulbAndEnthalpy
DifferentialEnthalpy
FixedDryBulb
NoEconomizer
EconomizerHighTemperatureLockout | EconoHiTempLockout | decimal | F | [6 empty] | Optional |  |  |  | The outside air temperature above which the economizer will return to minimum position. This applies if ControlType is FixedDB | 2013 NR ACM 5.7.4.2 Air Side Economizers; Economizer High Temperature Lockout
EconomizerIntegration | EconoIntegration | enumerated list | none | Integrated | [5 empty] | Defaulted
NonIntegrated
EconomizerIntegration | EconoIntegration | enumerated list | none | Integrated | [5 empty] | Defaulted
NonIntegrated
EconomizerLockout | EconoLockout | boolean | none | [6 empty] | Defaulted
EconomizerLowTemperatureLockout | EconoLowTempLockout | decimal | F | [6 empty] | Defaulted |  |  |  | The outside air temperature below which the economizer will return to the minimum position. This appears to apply to all types of air-side economizers. | 2013 NR ACM 5.7.4.2 Air Side Economizers; Economizer Economizer Low Temperature Lockout
EER | EER | decimal | none | [6 empty] | CondRequired
Effectiveness | Eff | decimal | none | [6 empty] | Required |  |  |  | A ratio that represents the effectiveness of an EvaporativeCooler | 2013 NR ACM 5.7.5.3 Evaporative Cooler equations 37 and 38
EIR | EIR | decimal | none | [6 empty] | CondRequired |  |  |  | The ratio of energy used by the system to the heating capacity in the same units. EIR is used in calculating a performance curve for heating equipment. It is the reciprocal of the coefficient of performance (COP) Represented as EIR | 2013 NR ACM: 5.8.1 Boilers Boiler Part-Load Performance Curve;
ElectricalIgnition | ElecIgnit | boolean | none | [6 empty] | Optional
ElectricMiniTank | ElecMiniTank | boolean | none | [6 empty] | Optional
ElectricMiniTankPower | ElecMiniTankPwr | decimal | W | [6 empty] | Optional
ElementType | ElementType | enumerated list | none | ElectricResistance | [5 empty] | Required
Gas
HeatPump
EnableOnThermalEnergyStorageDischarge | EnableOnThrmlEngyStorDischrg | boolean | none |  | No |  |  |  |  | Defaulted
EnergyFactor | EF | decimal | none | [6 empty] | CondRequired |  |  |  | The ratio of the energy delivered by the water heater divided by the energy used, in the same units.This property is used for Energy Factor values and the new Uniform Energy Factor values which has a more sophisticated approach to establishing efficiency as Energy Factor. | 2013 NR ACM 5.9.1.2 Water Heaters Energy Factor; CF1R-PRF
EnergyFactor | EngyFac | decimal | none | [6 empty] | CondRequired
EnergyLoad | EngyLd | decimal | Btu per h | [6 empty] | Optional
EnteringGeneratorTemperatureDesign | EntGenTempDsgn | decimal | F | [6 empty] | Defaulted
EnteringTemperatureDesign | EntTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
EnteringTemperatureDesign | EntTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
EnteringTemperatureDesign | EntTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Return Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
EnteringTemperatureRated | EntTempRtd | decimal | F | [6 empty] | Optional
EquipmentList1Name | EquipList1Name | reference | none |  | Yes | 0 | 10 |  |  | Optional | Blr
Chlr
EquipmentList2Name | EquipList2Name | reference | none |  | Yes | 0 | 10 |  |  | Optional | Blr
Chlr
EquipmentList3Name | EquipList3Name | reference | none |  | Yes | 0 | 10 |  |  | Optional | Blr
Chlr
EquipmentList4Name | EquipList4Name | reference | none |  | Yes | 0 | 10 |  |  | Optional | Blr
Chlr
EvaporatorFluidSegmentInReference | EvapInRef | reference | none | [6 empty] | Required | FluidSeg
EvaporatorFluidSegmentOutReference | EvapOutRef | reference | none | [6 empty] | Required | FluidSeg
EvaporatorHasBypass | EvapHasBypass | boolean | none | [6 empty] | Optional
ExhaustControlMethod | ExhCtrlMthd | enumerated list | none | COControl | [5 empty] | Defaulted
ConstantFlowConstantSpeedFan
NoCOControl
VariableFlowConstantSpeedFan
VariableFlowVariableSpeedFan
ExhaustOperationMode | ExhOperMode | enumerated list | none | CoupledToSystem | [5 empty] | Defaulted
DecoupledFromSystem
ExhaustSystemReference | ExhSysRef | reference | none | [6 empty] | Optional | AirSys
ZnSys
ExhaustSystemType | ExhSysType | enumerated list | none | CommercialKitchen | [5 empty] | Defaulted
General
Laboratory
ParkingGarage
ExteriorTankInsulation | ExtTankIns | decimal | h ft2 F per Btu | [6 empty] | Required |  |  |  | The R-Value of the insulation on the exterior of the water heater tank. | CF1R-PRF, CF3R-EXC-20-H
FanControl | FanCtrl | enumerated list | none | Continuous | [5 empty] | Defaulted
Cycling
FanControl | FanCtrl | enumerated list | none | Continuous | [5 empty] | Defaulted
Cycling
FanPosition | FanPos | enumerated list | none | BlowThrough | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM
FanReference | FanRef | reference | none | [7 empty] | Fan
FanType | FanType | enumerated list | none | Axial | [5 empty] | Defaulted
Centrifugal
FirstHourRating | FirstHrRating | decimal | gal |  | No |  |  |  |  | CondRequired
FixedSupplyTemperature | FixedSupTemp | decimal | F | [6 empty] | Defaulted
FixedSupplyTemperature | FixedSupTemp | decimal | F | [6 empty] | Defaulted
Flow | Flow | decimal | gal per min | [6 empty] | Optional |  |  |  | Process load flow in gallons per minute
FlowCapacity | FlowCap | decimal | ft3 per min | [6 empty] | Required |  |  |  | Defines the volumetric capacity of the fan measured in cubic ft per minute (cfm). The fan's peak airflow is what it is rated at when running at full capacity. | 2013 Title 24: Section 140.4 (c) Power Consumption of Fans; Used in Residential compliance document CF2R-MCH-27.for exhause fan; 2013 NR ACM 5.6.5.3 Zone Exhaust Exhaust Air Flow Rate; 5.7.3.4 Exhaust Fan Systems Exhaust Fan Rated Capacity; 5.7.3.2 Supply Fans Supply Fan Design Air Rated Capacity
FlowCapacity | FlowCap | decimal | gal per min | [6 empty] | Required |  |  |  | The flow rate of fluid through the Pump in gallons per minute. | 2013 NR ACM 5.8.5 Pumps
FlowEfficiency | FlowEff | decimal | none | [6 empty] | Defaulted |  |  |  | The efficiency of the Fan as a whole at design conditions | 2013 NR ACM: 5.7.3 Fan Systems Supply Fan Efficiency, Return/Relief Fan Efficiency
FlowMinimum | FlowMin | decimal | gal per min | [6 empty] | CondRequired |  |  |  | The lowest flow rate rated for a pump | 2008 NR ACM: Table N2-21 2013 ?
FlowMinimum | FlowMin | decimal | ft3 per min | [6 empty] | CondRequired |  |  |  | The lowest flow rate rated for a fan | 2013 NR ACM 5.7.5.2
FlowRate | FlowRt | decimal | gal per min |  | No |  |  |  |  | CondRequired
Fluid | Fluid | string | none |  | No | [7 empty] | dtyp:String50Char
FluidFlowRateDesign | FluidFlowRtDsgn | decimal | gal per min | [6 empty] | CondRequired |  |  |  | The maximum possible water volume flow rate through a hydronic coil. Used to define capacity for coils not explicilty defined by capacity in terms of Btu/h.
FluidSegmentInReference | FluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSeg |  |  | The name of the fluid segment that brings fluid into HVAC equipment
FluidSegmentInReference | FluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSeg |  |  | For coil, this is defined for Coil type = HotWater, ChilledWater, WaterEconomizer only
FluidSegmentMakeupReference | FluidSegMakeupRef | reference | none | [6 empty] | Required | FluidSeg
FluidSegmentOutReference | FluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSeg |  |  | The name of the fluid segment that takes fluid out of HVAC equipment
FluidSegmentOutReference | FluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSeg |  |  | Defined for Coil type = HotWater, ChilledWater, WaterEconomizer only
FluidSegmentOutReference | FluidSegOutRef | reference | none |  | No |  |  |  |  | Required | FluidSeg |  |  | The name of the fluid segment that takes fluid out of HVAC equipment
FluidSystemCount | FluidSysCnt | integer | none | [6 empty] | Optional |  |  |  |  | 2013 NR ACM sections 2.3.1 and 5.3 The number of duplicate HVAC systems represented by the modeled system.
FuelFullLoad | FuelFullLd | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The fuel consumption at design conditions | 2013 NR ACM 5.7.6.4 Furnace, equation 42 5.8.1 Boilers equation 60; 5.9.1.2 Water Heaters equation 76
FuelRated | FuelRtd | decimal | Btu per h | [6 empty] | Required |  |  |  | The ARI rated fuel consumption of fuel-fired or steamChiller | 2013 NR ACM 5.8.2 Chillers Fuel and Steam Chiller Cooling Efficiency Adjustment Curves equation 65,66
FuelSource | FuelSrc | enumerated list | none | Electric | [5 empty] | Required |  |  |  | Defines the type of energy used to run the equipment or provide heat. Values: electricity, natural gas, propane, fuel oil, hot water, steam, solar thermal. | 2013 NR ACM: 5.8.1 Boiler fuel
Gas
FuelSource | FuelSrc | enumerated list | none | Electric | [5 empty] | Required |  |  |  | Defines the type of energy used to run the Chiller. | 2013 NR ACM: 5.8.2 Chiller Fuel
Indirect
FuelSource | FuelSrc | enumerated list | none | Electric | [5 empty] | Defaulted |  |  |  | This lists all sources of heat for a heating coil | 2013 NR ACM 5.7.6 Heating Systems 5.7.6.1 General Heating Source
Gas
OilNoLongerValid
FuelSource | FuelSrc | enumerated list | none | [6 empty] | Required |  |  |  |  | CF1R-NCB/ALT/ADD-01
FuelSource | FuelSrc | enumerated list | none | Gas | [5 empty] | Required |  |  |  |  | CF1R-NCB/ALT/ADD-01
FurnaceAFUE | FurnAFUE | decimal | none | [6 empty] | CondRequired |  |  |  | The Annual Fuel Utilization Efficiency (AFUE) season-long, average efficiency of that piece of equipment | 2013 NR ACM 5.7.6.4
FurnaceIgnitionType | FurnIgnType | enumerated list | none | IntermittentIgnitionDevice | [5 empty] | Defaulted |  |  |  | Either pilot or an intermittent ignition device (IID) in furnaces. An IID is mandatory for furnaces with capacities of 225,000 Btu/h and greater. | 2008 Title 24: Section 112 Mandatory Requirements For Space-Conditioning Equipment (d) Gas- and Oil-Fired Furnace Standby Loss Controls
PilotLight
FurnacePilotFuelInput | FurnPilotFuelInp | decimal | Btu per h | [6 empty] | Defaulted |  |  |  | The measure of energy required by the Furnace pilot light. | 2013 NR ACM: 5.7.6.4 Furnace Furnace Fuel Heating Pilot
FurnaceThermalEfficiency | FurnThrmlEff | decimal | none | [6 empty] | CondRequired |  |  |  | The full load of a water heater or heating coil efficiency calculated as the ratio of heat transferred to the water divided by the heat input of the fuel. | 2013 NR ACM 5.7.6.4 Furnace equation 41
FurnaceType | FurnaceType | enumerated list | none | Fan | No |  |  |  |  | Defaulted
Gravity
GeneratorFluidFlowCapacity | GenFluidFlowCap | decimal | gal per min | [6 empty] | Optional
GeneratorFluidSegmentInReference | GenFluidSegInRef | reference | none | [6 empty] | CondRequired | FluidSeg
GeneratorFluidSegmentOutReference | GenFluidSegOutRef | reference | none | [6 empty] | CondRequired | FluidSeg
GlassDoorCount | GlsDrCnt | integer | none | [6 empty] | Optional |  |  |  | The number of glass display doors in the RefrigerationEquipment | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Equation 6
GlassDoorPower | GlsDrPwr | decimal | W | [6 empty] | Optional |  |  |  | The power associated with a glass display door for a walk-in refrigerator or freezer
HasBypass | HasBypass | boolean | none | [6 empty] | Optional
HasHeatExchangerBypass | HasHXBypass | boolean | none | [6 empty] | Defaulted
HeatingAirFlowMaximum | HtgAirFlowMax | decimal | ft3 per min | [6 empty] | CondRequired
HeatingAvailabilityScheduleReference | HtgAvailSchRef | reference | none | [6 empty] | Optional |  | Schedule |  |  | 2013 NR ACM: 5.7.2 System Controls
HeatingAvailabilityScheduleReference | HtgAvailSchRef | reference | none | [6 empty] | Optional |  | Schedule |  |  | 2013 NR ACM: 5.7.2 System Controls
HeatingDesignFlow | HtgDsgnFlow | decimal | none | [6 empty] | Optional |  |  |  | The design zone Heating air flow rate in cubic meters per second. If a thermal zone has heating unmet load hours, the first step in addressing this issue is to increase the zone design air flow. | 2013 NR ACM 2.6.2
HeatingDesignMaximumFlowFraction | HtgDsgnMaxFlowFrac | decimal | none | [6 empty] | Defaulted
HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted |  |  |  | The design heating temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also hot deck temp | 2013 NR ACM 5.7.2.3 Heating Control;
HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted
HeatingDesignSupplyAirTemperature | HtgDsgnSupAirTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
HeatingDesignSupplyAirTemperatureDifference | HtgDsgnSupAirTempDiff | decimal | F | [6 empty] | Defaulted
HeatingDesignSupplyWaterTemperature | HtgDsgnSupWtrTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM
HeatingFixedSupplyTemperature | HtgFixedSupTemp | decimal | F | [6 empty] | Defaulted
HeatingFixedSupplyTemperature | HtgFixedSupTemp | decimal | F | [6 empty] | Optional
HeatingFlowSizingFactor | HtgFlowSizingFac | decimal | none | [6 empty] | Optional |  |  |  | This input is a zone level heating sizing ratio. The zone design heating air flow rates and loads will be multiplied by the number input in this field. | 2013 NR ACM 2.6.2
HeatingLatentEffectiveness100 | HtgLatEff100 | decimal | [7 empty] | Defaulted
HeatingLatentEffectiveness75 | HtgLatEff75 | decimal | [7 empty] | Defaulted
HeatingSensibleEffectiveness100 | HtgSensEff100 | decimal | [7 empty] | Defaulted
HeatingSensibleEffectiveness75 | HtgSensEff75 | decimal | [7 empty] | Defaulted
HeatingSetPointScheduleReference | HtgSetPtSchRef | reference | none | [6 empty] | Optional |  | Schedule
HeatingSupplyTemperature | HtgSupTemp | decimal | F | [6 empty] | Optional |  |  |  | The design heating temperature of leaving air ( LAT) at rated coil capacity. If no other control is specified, this is also hot deck temp | 2013 NR ACM 5.7.2.3 Heating Control;
HeatingSystemReference | HtgSysRef | reference | none | [6 empty] | Required | AirSys
HeatingTemperatureSetPointScheduleReference | HtgTempSetptSchRef | reference | none | [6 empty] | CondRequired |  | Schedule
HeatingTotalEffectiveness100 | HtgTotEff100 | decimal | [7 empty] | Defaulted
HeatingTotalEffectiveness75 | HtgTotEff75 | decimal | [7 empty] | Defaulted
HeatLoss | HtLoss | decimal | Btu per h | [6 empty] | Optional |  |  |  | The heat lost when the Boiler is firing and is expressed as a fraction of full load output capacity. The default is .02 for electric boilers and heat-exchangers and 0 for fuel-fired boilers | 2013 NR ACM: 5.8.1 Boilers Boiler Heat Loss
HeatPumpCompressorLockoutTemperature | HtPumpCprsrLockoutTemp | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.5.6.5
HeatPumpCOP | HtPumpCOP | decimal | none | [6 empty] | CondRequired |  |  |  | The ARI rated coefficient of performance for the heating equipment such as a heat pump | 2013 NR ACM 5.7.6.5 Electric Heat Pump Electric Heat Pump Heating Efficiency
HeatPumpCrankcaseControlTemperature | HtPumpCrankcaseCtrlTemp | decimal | F | [6 empty] | Defaulted |  |  |  | The dry bulb temperature at which the crank case in an electric heat pump is shut off. | 2013 NR ACM: 5.7.6.5 Electric Heat Pump Heat Pumps Crank Case Heater Shutoff Temperature
HeatPumpCrankcaseHeatCapacity | HtPumpCrankcaseHtCap | decimal | Btu per h | [6 empty] | Optional |  |  |  | The capacity of the electric resistance heater in the crank case of a direct expansion (DX) compressor. The crank case heater operates only when the compressor is off. | 2013 NR ACM 5.7.6.5
HeatPumpDefrostControl | HtPumpDefCtrl | enumerated list | none | OnDemand | [5 empty] | Defaulted |  |  |  | Defines how the defrosting is activated, either on demand or on a timed cycle which is by default 3.5 minutes in length | 2013 NR ACM: 5.7.6.5 Heat Pumps Coil Defrost
TimedCycle
HeatPumpDefrostHeatCapacity | HtPumpDefHtCap | decimal | Btu per h | [6 empty] | CondRequired |  |  |  | The capacity of the electric resistance defrost heater. | 2013 NR ACM: 5.7.6.5
HeatPumpDefrostHeatSource | HtPumpDefHtSrc | enumerated list | none | Electric | [5 empty] | Defaulted |  |  |  | Defines the source of the defrosting heat which is usually hot gas or electric resisitance | 2013 NR ACM: 5.7.6.5 Heat Pumps Coil Defrost
HotGas
HeatPumpEIR_fPLRCurveReference | HtPumpEIR_fPLRCrvRef | reference | none | [6 empty] | Optional |  |  |  | The electric heat pump heating efficiency PLR adjustment curve | 2013 NR ACM 5.7.6.5 Electric Heat Pump equation 50 Table 61
HeatPumpHSPF | HtPumpHSPF | decimal | Btu per W h | [6 empty] | CondRequired |  |  |  | A measure of efficiency of heating equipment using Heating Season Performance Factor (HSPF) | 2013 NR ACM 5.7.6.5 Electric Heat Pump Electric Heat Pump Heating Efficiency
HeatPumpSupplementalCoilHeatingReference | HtPumpSuppCoilHtgRef | reference | none | [6 empty] | Optional | CoilHtg |  |  | Reference to the coil object that provides supplemental heating when the heat pump compressor is cannot meet load or is disabled. | 2013 NR ACM: 5.7.6.5
HeatPumpSupplementalTemperature | HtPumpSuppTemp | decimal | F | [6 empty] | Defaulted |  |  |  | The dry bulb temperature at which supplemental heating equipment is allowed to be turned on | 2013 NR ACM 5.7.6.5 Heat Pumps Electric Heat Pump Electric Supplemental Heating Control Temp
HeatPumpWaterHeaterBrand | HPWHBrand | enumerated list | none | A. O. Smith | No |  |  |  |  | CondRequired
American
Bradford White
EcoSense
GE
Kenmore
Lochinvar
Reliance
Rheem
Richmond
Ruud
Sanden
State
Stiebel Eltron
US Craftmaster
Whirlpool
HeatPumpWaterHeaterModel | HPWHModel | enumerated list | none | 10 50 DHPHT 120 (50 gal) | [5 empty] | CondRequired
10 50 DHPHTNE 120 (50 gal)
10 60 DHPT 120 (60 gal)
10 66 DHPHT 120 (66 gal)
10 66 DHPHTN 120 (66 gal)
10 80 DHPHT 120 (80 gal)
10 80 DHPHTNE 120 (80 gal)
10 80 DHPT 120 (80 gal)
10E50-HP4D (50 gal)
10E65-HP4D (65 gal)
10E80-HP4D (80 gal)
12E50-HP (50 gal)
12E80-HP (80 gal)
153.32116 (60 gal)
153.32118 (80 gal)
153.5925 (50 gal)
153.5926 (60 gal)
153.5928 (80 gal)
6 50 DHPHT 120 (50 gal)
6 66 DHPHT 120 (66 gal)
6 80 DHPHT 120 (80 gal)
6 80 DHPT 102 (80 gal)
Accelera 220 E (58 gal)
Accelera 300/WHP 300 (80 gal)
BEH50DCEJSB (50 gal)
BEH80DCEJSB (80 gal)
EP6 80 DHPT 102 (80 gal)
EPX 60 DHPT (60 gal)
EPX 80 DHPT (80 gal)
FPTU 50 120 (50 gal)
FPTU 66 120 (66 gal)
FPTU 80 120 (80 gal)
GEH50DEEJSC (50 gal)
GEH50DEEJXXX (50 gal)
GEH50DFEJSR (50 gal)
GEH50DHEKSC (50 gal)
GEH80DEEJSC (80 gal)
GEH80DFEJSR (80 gal)
GEH80DHEKSC (80 gal)
GS3-45HPA-US & GAUS-1315EQTD (83 gal)
GS3-45HPA-US & GAUS-160QTA (43 gal)
GS3-45HPA-US & SAN-43SSAQA (43 gal)
GS3-45HPA-US & SAN-83SSAQA (83 gal)
GUS-45HPA-US & GAUS-1315EQTD (83 gal)
GUS-45HPA-US & SAN-83SSAQA (83 gal)
HB50ES (50 gal)
HB50RH (50 gal)
HB50RM (50 gal)
HB50RU (50 gal)
HHPT 80 120 (80 gal)
HP10-50H45DV (50 gal)
HP10-80H45DV (80 gal)
HP6 50 DHPT 120 (50 gal)
HP6 66 DHPT 120 (66 gal)
HP6 80 DHPT 120 (80 gal)
HPA051KD 120 (50 gal)
HPA052KD 120 (50 gal)
HPA067KD 120 (66 gal)
HPA068KD 120 (66 gal)
HPA081KD 120 (80 gal)
HPA082KD 120 (80 gal)
HPE10260H045DV (60 gal)
HPE10280H045DV (80 gal)
HPE2F80HD045VU 102 (80 gal)
HPE2K60HD045V (60 gal)
HPE2K60HD045V (60 gal)
HPE2K80HD045V (80 gal)
HPE2K80HD045V (80 gal)
HPE6280H045DV 102 (80 gal)
HPHE10250H045DV 102 (50 gal)
HPHE10250H045DVN 102 (50 gal)
HPHE10266H045DV 102 (66 gal)
HPHE10266H045DVN 102 (66 gal)
HPHE10280H045DV 102 (80 gal)
HPHE10280H045DVN 102 (80 gal)
HPHE2F50HD045VU 120 (50 gal)
HPHE2F66HD045VU 120 (66 gal)
HPHE2F80HD045VU 120 (80 gal)
HPHE2K50HD045V 120 (50 gal)
HPHE2K50HD045VC 120 (50 gal)
HPHE2K50HD045VN 120 (50 gal)
HPHE2K50HD045VUN 120 (50 gal)
HPHE2K66HD045V 120 (66 gal)
HPHE2K66HD045VC 120 (66 gal)
HPHE2K66HD045VUN 120 (66 gal)
HPHE2K80HD045V 120 (80 gal)
HPHE2K80HD045VC 120 (80 gal)
HPHE2K80HD045VUN 120 (80 gal)
HPHE6250H045DV (50 gal)
HPHE6266H045DV (66 gal)
HPHE6280H045DV (80 gal)
HPHE650H045DV (50 gal)
HPSE2K50HD045V 100 (WP) (50 gal)
HPSE2K50HD045VC 100 (WP) (50 gal)
HPSE2K80HD045V (80 gal)
HPSE2K80HD045VC (80 gal)
HPTU 50 120 (50 gal)
HPTU 50N 120 (50 gal)
HPTU 66 120 (66 gal)
HPTU 66N 120 (66 gal)
HPTU 80 120 (80 gal)
HPTU 80N 120 (80 gal)
HPX 50 DHPT 120 (50 gal)
HPX 50 DHPTNE 120 (50 gal)
HPX 66 DHPT 120 (66 gal)
HPX 66 DHPTNE 120 (66 gal)
HPX 80 DHPT 120 (80 gal)
HPX 80 DHPTNE 120 (80 gal)
PHPT 60 (60 gal)
PHPT 80 (80 gal)
PROPH50 T2 RH245 (50 gal)
PROPH50 T2 RH350 D (50 gal)
PROPH80 T2 RH245 (80 gal)
PROPH80 T2 RH350 D (80 gal)
PROUH50 T2 RU245 (50 gal)
PROUH50 T2 RU350 D (50 gal)
PROUH65 T2 RU350 D (65 gal)
PROUH80 T2 RU245 (80 gal)
PROUH80 T2 RU350 D (80 gal)
RE2H50R10B-1NCWT (50 gal)
RE2H80R10B-1NCWT (80 gal)
XE50T10HD50U0 (50 gal)
XE50T12EH45U0 (50 gal)
XE50T12EH45U0W (50 gal)
XE65T10HD50U0 (65 gal)
XE80T10HD50U0 (80 gal)
XE80T12EH45U0 (80 gal)
XE80T12EH45U0W (80 gal)
HeatPumpWaterHeaterNEEARated | HtPumpWtrHtrNEEARtd | boolean | none | [6 empty] | Optional
HeatRecoveryReference | HtRcvryRef | reference | none | [6 empty] | Optional | HtRcvry
HIR_fPLRCurveReference | HIR_fPLRCrvRef | reference | none | [6 empty] | Defaulted |  |  |  | The heating input ratio part load ratio performance curve is normally a quadratic curve. | 2013 NR ACM 5.7.6.4 Furnace, Table 59, equation 43 5.8.1 Boilers equation 60; 5.9.1.2 Water Heaters Fuel Water Heater Part Load Efficiency Curve equation 76
HotWaterSupplyTemperature | HotWtrSupTemp | decimal | F | [6 empty] | Defaulted
HVACAutoSizing | HVACAutoSizing | boolean | none | [6 empty] | Optional
HvacSystemAreaServed | HvacSystemAreaServed | string | [10 empty] | dtyp:String50Char
HVACZoneCount | HVACZnCnt | integer | none | [6 empty] | Defaulted
ImpellerEfficiency | ImpellerEff | decimal | none | [6 empty] | Required
IndirectDewPointEffectiveness | IndirectDewPtEff | decimal | none | [6 empty] | Defaulted |  |  |  | Effectiveness applied to the dewpoint depression. The cooler uses the warmer of the temperatures determined from the wetbulb depression and dewpoint depression | 2013 NR ACM 5.7.5.3
InducedAirZoneReference | InducedAirZnRef | reference | none | [6 empty] | CondRequired | ThrmlZn |  |  | The Name of ThermalZone that air is induced from
InductionRatio | InductionRat | decimal | none | [6 empty] | Defaulted |  |  |  | The fraction of induced air, divided by AirFlowPrimary
InputPower | InpPwr | decimal | kW |  | No |  |  |  |  | CondRequired
InputRating | InpRating | integer | Btu per h | [6 empty] | Required
InputRatingElectric | InpRatingElec | integer | W | [6 empty] | CondRequired
InteriorTankInsulation | IntTankIns | decimal | h ft2 F per Btu | [6 empty] | Required |  |  |  | The R-Value of the insulation on the interior of the water heater tank.
IPLVCOP | IPLVCOP | decimal | none | [6 empty] | CondRequired |  |  |  | IPLV is a metric of part load performance, but the units change based on the efficiency descriptor. This makes it three different properties in SDD terms. | 2013 NR ACM 5.8.2
IPLVEER | IPLVEER | decimal | Btu per W h | [6 empty] | CondRequired |  |  |  | IPLV is a metric of part load performance, but the units change based on the efficiency descriptor. This makes it three different properties in SDD terms. | 2013 NR ACM 5.8.2
IPLVKwPerTon | IPLVKwPerTon | decimal | kW per ton | [6 empty] | CondRequired |  |  |  | IPLV is a metric of part load performance, but the units change based on the efficiency descriptor. This makes it three different properties in SDD terms. | 2013 NR ACM 5.8.2
IPLVRated | IPLVRtd | decimal | none | [10 empty] | The integrated part load efficiency of the chiller | 2013 NR ACM 5.8.2 Chillers Chiller Rated Efficiency
IsAllOutsideAir | IsAllOA | boolean | none |  | No |  |  |  |  | Defaulted
IsComplexSystem | IsComplexSystem | boolean | none | [6 empty] | Defaulted
IsUniformEnergyFactorRated | IsUEFRtd | boolean | none |  | No |  |  |  |  | Required |  |  |  |  | CBECC-Com 2016 Input data model
KwPerTon | KwPerTon | decimal | kW per ton | [6 empty] | CondRequired
LeavingTemperatureDesign | LvgTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
LeavingTemperatureDesign | LvgTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
LeavingTemperatureDesign | LvgTempDsgn | decimal | F | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 13-16; 5.8.1 Boilers Hot Water Supply Temperature; 5.8.2 Chiller Cooling Capacity Adjustment Curves equations 62 and 63
LeavingTemperatureRated | LvgTempRtd | decimal | F | [6 empty] | Optional
LoadRangeLimit | LdRngLim | integer | Btu per h |  | Yes | 0 | 4 |  |  | Optional |  |  | dtyp:IntegerNonnegative
LoopCount | LpCnt | integer | none | [6 empty] | CondRequired
LoopPipeInsulationThickness | LpPipeInsThkns | decimal | in |  | Yes | 6 | 6 |  |  | Required
LowSpeedAirFlowRatio | LowSpdAirFlowRat | decimal | none | [6 empty] | Defaulted |  |  |  | The percentage of full load airflow at low speed which is equivalent to the percentage of full load capacity at low speed. | 2013 NR ACM 5.8.3 Cooling Towers
MakeupAirSystemReference | MakeupAirSysRef | reference | none | [6 empty] | Optional | AirSys |  |  | The Name of AirSystem from which makeup air is supplied | 2013 NR ACM: 5.6.5 Zone Level Air Flow
MakeupThermalZoneReference | MakeupThrmlZnRef | reference | none | [6 empty] | Optional | ThrmlZn |  |  | The Name of ThermalZone from which makeup air is drawn | 2013 NR ACM: 5.6.5 Zone Level Air Flow
Manufacturer | Manufacturer | string | none | [6 empty] | Optional |  |  | xsd:string
Manufacturer | Manufacturer | string | none |  | No | [7 empty] | dtyp:String50Char
MinimumCapacity | MinCap | decimal | Btu per h | [6 empty] | Defaulted
MinimumHotGasRatio | MinHotGasRat | decimal | none | [6 empty] | Optional |  |  |  |  | 2013 NR ACM 5.7.5.2
MinimumSpeedRatio | MinSpdRat | decimal | none | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.8.3 Cooling Towers Fan minimum speed ratio
MinimumSpeedRatio | MinSpdRat | decimal | none | [6 empty] | Optional |  |  |  | The ratio of the lowest speed to the full load speed | 2013 NR ACM 5.8.3 Cooling Towers Fan minimum speed ratio; 5.8.5 Pumps Pump Minimum Speed
ModelingMethod | ModelingMthd | enumerated list | none | Detailed | [5 empty] | Defaulted |  |  |  | Defines how the Pump is modeled. | 2013 NR ACM 5.8.5 Pumps Pump Motor Modeling Method
PowerPerUnitFlow
ModelingMethod | ModelingMthd | enumerated list | none | BrakeHorsePower | [5 empty] | Required |  |  |  | Defines how the FanSystem is modeled. | 2013 NR ACM 5.7.3.2 Supply Fans; 5.7.3.4 Exhaust Fan Systems
PowerPerUnitFlow
StaticPressure
ModelNumber | ModelNum | string | none |  | No | [7 empty] | dtyp:String50Char
ModeScheduleReference | ModeSchRef | reference |  |  | No |  |  |  |  | Required |  | ThermalEnergyStorageModeScheduleDay
ModulationControl | ModCtrl | enumerated list | none | Bypass | [5 empty] | Defaulted |  |  |  | Defines how the CoolingTower modulates capacity to respond to changing loads. Assignment of value depends on FanSystem and Fan attributes e.g. operation mode and Fan speed and pony motor attributes. | 2013 NR ACM: 5.8.3 Cooling Towers Cooling Tower Capacity Control
Cycling
TwoSpeed
VariableSpeedDrive
MotorBHP | MtrBHP | decimal | hp | [6 empty] | Optional |  |  |  | The brake horsepower of the motor before the loss in power caused by the gearbox, alternator, differential, and other auxiliary components. | 2013 NR ACM 5.7.3 Fan systems, 5.7.5 Cooling Systems Total Cooling Capacity equation 11;
MotorEfficiency | MtrEff | decimal | none | [6 empty] | Required |  |  |  | Indicates how well the motor converts electrical power into mechanical power and is defined as output power divided by input power expressed as a percentage . | 2013 NR ACM 5.8.5 Pumps Motor Efficiency
MotorEfficiency | MtrEff | decimal | none | [6 empty] | Required |  |  |  | Indicates how well the motor converts electrical power into mechanical power and is defined as output power divided by input power expressed as a percentage . | 2013 NR ACM 5.7.3.2 Supply Fans Supply Motor Efficiency; 5.8.5 Pumps Motor Efficiency
MotorHP | MtrHP | decimal | hp | [6 empty] | Required |  |  |  | The rated horsepower of the pump motor. | 2013 NR ACM 5.8.5 Pumps Motor Efficiency Table N2-20 Minimum Nominal Efficiency for Electric Motors (from 2008 NR ACM)
MotorHP | MtrHP | decimal | hp | [6 empty] | Required |  |  |  | The nameplate (rated) horsepower of the motor. | 2013 NR ACM Supply Motor Efficiency Table N2-20 Minimum Nominal Efficiency for Electric Motors (from 2008 NR ACM); 5.8.5 Pumps Motor Efficiency
MotorPoleCount | MtrPoleCnt | integer | none | [6 empty] | Defaulted |  |  |  | The number of pole electromagnetic windings in the motor's stator and used to assign MotorEfficiency. Poles is always paired, so PoleCount is always a multiple of 2. | 2013 NR ACM 5.7.3 Fan systems, References 2008 NR ACM Table N2-20 which requires PoleCount of the motor
MotorPosition | MtrPos | enumerated list | none | InAirStream | [5 empty] | Defaulted |  |  |  | Defines where the Fan motor is located relative to the cooling air stream. Values: InAirStream, NotInAirStream | 2013 NR ACM 5.7.3 Fan systems, Motor position
NotInAirStream
MotorRPM | MtrRPM | integer | rpm | [6 empty] | Required |  |  |  | The number of full revolutions in a unit of time and is used to assign MotorEfficiency. 2008 NR ACM table N2-20 has four speeds: 3600 rpm, 1800 rpm, 1200 rpm, 900 rpm. | 2013 NR ACM 5.7.3 Fan systems, References 2008 NR ACM Table N2-20 which requires RotationalSpeed of the motor
MotorType | MtrType | enumerated list | none | Enclosed | [5 empty] | Defaulted |  |  |  | Defines if the motor is Open or Enclosed | 2013 NR ACM 5.7.3 Fan systems, References 2008 NR ACM Table N2-20 which requires EnclosedType of the motor
Open
Multiplier | Mult | integer | none | [6 empty] | Optional
Name | Name | string | none | [6 empty] | Required |  |  |  | A text string that uniquely defines the HVAC object, and is returned when the object is referenced.
Name | Name | name | none | [6 empty] | Required
NameOfProgramUsed | NameOfProgramUsed | string | none |  | No
NightCycleFanControl | NightCycleFanCtrl | enumerated list | none | CycleOnCallAnyZone | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM: 5.7.2 System Controls
CycleOnCallPrimaryZone
CycleZoneFansOnly
StaysOff
NumberCoolingStages | NumClgStages | integer | none | [6 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.5.2
NumberOfIdenticalDwellingUnits | NumOfIdenticalDwellingUnits | integer | none |  | No
OperableWindowInterlock | OperableWinInterlock | boolean | none | [6 empty] | CondRequired
OperableWindowsHaveInterlock | OperableWinHaveInterlock | boolean | none | [6 empty] | CondRequired
OperationControl | OperCtrl | enumerated list | none | OnDemand | [5 empty] | Defaulted |  |  |  | Defines how pump operation is controlled. Values: OnDemand, StandBy, Schedule | 2013 NR ACM 5.8.5 Pumps Pump Operation
Scheduled
StandBy
OptimumStart | OptStart | boolean | none | [6 empty] | Defaulted
ParallelBoxFanFlowFraction | ParallelBoxFanFlowFrac | decimal | none | [6 empty] | Defaulted
ParallelBoxThermostatScheduleReference | ParallelBoxTtatSchRef | reference | none | [6 empty] | Required |  | Schedule |  |  | 2013 NR ACM 5.6.2
ParasiticLoad | ParasiticLd | decimal | W | [6 empty] | CondRequired |  |  |  | Electricity consumption of mechanical draft equipment (W) | 2013 NR ACM 5.8.3
PartLoadRatioMinimum | PLRMin | decimal | none | [6 empty] | Defaulted |  |  |  | The minimum chiller load which can be met with continuous operation. Below this load, the chiller cycles. The UnldRatMin is the lowest load which the chiller can meet with unloading. Between UnldRatMin and PartLdRatMin, the chiller is false loaded as with hot gas bypass. | 2013 NR ACM 5.8.2
Path | Path | enumerated list | none | Direct | [5 empty] | Defaulted
Ducted
PlenumZones
PerformanceCurveName | Name | name | none
PipeLocation | PipeLctn | enumerated list | none | Conditioned |  | 0 | 6 |  |  | CondRequired
SemiConditioned
Unconditioned
Underground
PlantCoolingCapacity | PlantClgCap | decimal | cooling ton (12,000 Btu per h) | [6 empty] | Defaulted |  |  |  | Nominal heating capacity of an HVAC system | 2013 CF1R perf
PlantHeatingCapacity | PlantHtgCap | decimal | Btu per h | [6 empty] | Defaulted |  |  | dtyp:Decimal1Place | Nominal heating capacity of an HVAC system | 2013 CF1R perf
Power | Pwr | decimal | kW | [6 empty] | Optional |  |  |  | The power of the fan system at AirFlowCap | 2013 NR ACM 5.7.3.2 Supply Fan kW
Power_fPLRCurveReference | Pwr_fPLRCrvRef | reference | none | [6 empty] | Optional |  |  |  | The PLR power curve is normally a quadratic curve. | 2013 NR ACM: 5.7.3 Fan Systems equation 9 Table 46; 5.8.3 Cooling Towers; 5.8.5 Pumps Part Load Power Curve equation 74 Table 80;
PowerMinimumRatio | PwrMinRat | decimal | none | [6 empty] | Required |  |  |  | The minimum power draw of the fan, expressed as a ratio of the full load fan power. | 2013 NR ACM 5.7.3 Fan Systems
PowerPerFlow | PwrPerFlow | decimal | W per ft3 per min | [6 empty] | Optional |  |  |  | Measures the full load power of the Fan per unit of air flow. | NR ACM: 2.5.3.5 Fan Power has fan power index which is power per cfm Residential CF1R reports this value and it's used on CF2R-MCH01a
PowerPerUnitArea | PwrPerUnitArea | decimal | W per ft2 | [6 empty] | Optional |  |  |  | The measure of power per square foot of space in a walk-in cooler or freezer | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Table 24 Default Power for Walk-in Refirgerators and Freezers
PrimaryAirConditioningSystemPriority | PriAirCondgSysPriority | integer | none |  |  | 2 | 2 |  |  | Defaulted
PrimaryAirConditioningSystemReference | PrimAirCondgSysRef | reference | none |  |  |  | 2 |  |  | CondRequired | AirSys |  |  | Defines the primary HVAC system that provides heating or cooling to the space. The same system might also provide ventilation air to the space. In this case, the VentSysRef property should reference the same system name. Both AirSystem and ZoneSystem are valid object assignments for this property. However, if the ventilation and primary air conditioning systems are different, the ventilation system must be defined as an AirSystem, and the primary air conditioning system defined as a ZoneSystem/
ZnSys
PrimaryAirFlowMaximum | PriAirFlowMax | decimal | ft3 per min | [6 empty] | Required
PrimaryAirFlowMinimum | PriAirFlowMin | decimal | ft3 per min | [6 empty] | CondRequired
PrimaryAirSegmentReference | PriAirSegRef | reference | none | [6 empty] | Required | AirSeg |  |  | Name of primary AirFlowSegment, or cooling AirFlowSegment for DualDuct systems
PrimarySegmentReference | PriSegRef | reference | none | [6 empty] | CondRequired | FluidSeg
PumpBreakHorsepower | PumpBHP | decimal | hp
PumpEfficiency | PumpEff | decimal | none | [6 empty] | Optional
PumpPower | PumpPwr | decimal | kW | [6 empty] | Optional
PumpPower | PumpPwr | decimal | W | [6 empty] | Required |  |  |  |  | 2013 NR ACM 5.7.5.3 Evaporative Cooler
RatedEfficiencyCurveIntercept | RatedEffCurveIntercept | decimal | none |  | No | [7 empty] | dtyp:Decimal3Places
RatedEfficiencyCurveSlope | RatedEffCurveSlope | decimal | none |  | No | [7 empty] | dtyp:Decimal3Places
RecirculationLoopCount | RecircLoopCnt | integer | none | [6 empty] | Required |  |  |  | The total number of hot water recirculation loops coming from and returning to a specific water heater.
RecoveryEfficiency | RE | decimal | none |  |  |  |  | 0 | 1 | CondRequired
RecoveryType | RcvryType | enumerated list | none | LatentOnly | [5 empty] | Defaulted
SensibleOnly
Total
ReheatControlMethod | ReheatCtrlMthd | enumerated list | none | DualMaximum | [5 empty] | Defaulted |  |  |  | The air/temperature control strategy for VAV systems with reheat boxes during heating mode.
SingleMaximum
ReheatControlMethod | ReheatCtrlMthd | enumerated list | none | DualMaximum_TU | [5 empty] | Defaulted
SingleMaximum_TU
RemoteCondenserFraction | RemCndsrFrac | decimal | none | [6 empty] | Optional |  |  |  | The fraction of condenser heat that is rejected to the outdoors. For self-contained refrigeration casework, this value will be zero. For remote condenser systems, this value is 1.0. For combination systems, the value should be weighted according refrigeration capacity. | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Remote Condenser Fraction
RemoteCondenserHeatRemovalRate | RemCndsrHtRmvlRt | decimal | Btu per h | [6 empty] | Optional |  |  |  | The rate of heat removal from the space due to the continuous operation of the refrigeration system (kBtu/h). A negative number means that heat is being removed from the space; a positive number means that heat is being added. | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment Remote Condenser Fraction
ResetOutdoorHigh | RstOutdrHi | decimal | F | [6 empty] | CondRequired
ResetOutdoorLow | RstOutdrLow | decimal | F | [6 empty] | CondRequired
ResetSupplyHigh | RstSupHi | decimal | F | [6 empty] | CondRequired
ResetSupplyLow | RstSupLow | decimal | F | [6 empty] | CondRequired
ResidentialDHWDwellingUnitDistributionType |  | enumerated list | none | RecirculationNonDemand | [9 empty] | This describes the type of mechanism is used to distribute hot water in a dwelling unit in a low-rise residential buildings | Title 24 Part 6 Section 150.1(c)8. CF1R-NCB-01,
ReturnAirSegmentReference | RetAirSegRef | reference | none | [7 empty] | AirSeg
ReturnPlenumZoneReference | RetPlenumZnRef | reference | none | [6 empty] | Optional | ThrmlZn |  |  |  | 2013 NR ACM: 2.3.2
RValue | RVal | decimal | h ft2 F per Btu | [6 empty] | Required |  |  |  | Performance of unfired storage tank insulation.
SecondaryAirSource | SecAirSrc | enumerated list | none | OutdoorAir | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.5.3
ReturnAir
SecondaryFanFlowCapacity | SecFanFlowCap | decimal | ft3 per min | [6 empty] | CondRequired |  |  |  |  | 2013 NR ACM 5.7.5.3 Evaporative Cooler Evaporative Cooling
SecondaryFanTotalEfficiency | SecFanTotEff | decimal | none | [6 empty] | Defaulted |  |  |  | includes motor eff | 2013 NR ACM 5.7.5.3 Evaporative Cooler
SecondaryFanTotalStaticPressure | SecFanTotStaticPress | decimal | in water column | [6 empty] | CondRequired |  |  |  |  | 2013 NR ACM 5.7.5.3 Evaporative Cooler
SecondaryTankVolume | SecondaryTankVol | decimal | gal | [6 empty] | Optional
SecondaryTankVolume | SecondaryTankVol | decimal | gal | [6 empty] | Optional
ServiceReference | ServiceRef | reference | none | [7 empty] | AirSeg
AirSys
Blr
Chlr
FluidSeg
FluidSys
HtRej
TrmlUnit
SlopeFromHorizontal | SlopeFromHorizontal | decimal | deg arc | [6 empty] | Optional
SolarCollectorCount | SolCollectorCnt | integer | none |  | No | [9 empty] | CF1RSTH02E, CBECC Com NR SDD
SolarFractionFluidSystemName | SolFracFluidSysName | string | none | [6 empty] | Optional |  |  | xsd:string
Source | Src | enumerated list | none | MunicipalWater | [5 empty] | Required
NoExternalSource
SpeedControl | SpdCtrl | enumerated list | none | ConstantSpeed | [5 empty] | Defaulted
VariableSpeed
SpeedMinimumRatio | SpdMinRat | decimal | none | [6 empty] | Required |  |  |  |  | 2013 NR ACM 5.7.5.2
SRRCCertificationNumber | SRRCCertNum | string | none |  | No
StandbyLossFraction | StdbyLossFrac | decimal | none | [11 empty] | The tank standby loss fraction for storage tanks.
StandbyLossFraction | StdbyLossFrac | decimal | none | [6 empty] | Optional
Status | Status | enumerated list | none | Altered | [5 empty] | Required |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply.
Existing
New
Status | Status | enumerated list | none | Existing | [5 empty] | Required |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
Status | Status | enumerated list | none | Altered | [5 empty] | Required |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for AirSystem and ZoneSystem; Required for FluidSystem and RecirculationDHWSystem
Existing
New
Status | Status | enumerated list | none | Existing | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for TerminalUnit; Required for Chiller, Boiler, HeatRejection, WaterHeater, Pump, and RecirculationWaterHeater
New
Status | Status | enumerated list | none | Altered | [5 empty] | Defaulted |  |  |  | Defines if equipment is new, existing or modified. Existing equipment may be moved and reinstalled in the project. If so, mandatory efficiency ratings may not apply. |  | Compliance Use is Defaulted for AirSystem and ZoneSystem; Required for FluidSystem and RecirculationDHWSystem
Existing
New
StorageCapacity | StorCap | decimal | gal | [6 empty] | Required
StorageCapacity | StorCap | decimal | gal |  | No |  |  |  |  | Required
StorageCapacitySimulated | StorCapSim | decimal | gal |  | No |  |  |  |  | Optional
StorageLocation | StorLoc | integer | none |  | No |  |  |  |  | CondRequired
StorageLocation | StorLctn | enumerated list | none | Indoor | No |  |  |  |  | Required
Outdoor
Underground
StorageLocationSimulated | StorLctnSim | enumerated list | none | Outdoor | No |  |  |  |  | Required
Zone
StorageZoneReference | StorZnRef | reference | none |  | No |  |  |  |  | CondRequired | ThrmlZn
StorageZoneReference | StorageZoneReference | reference |  |  | No |  |  |  |  | CondRequired | ThrmlZn
SubType | SubType | enumerated list | none | CRAC | [5 empty] | Defaulted |  |  |  | Air System equipment subtype | 2013 NR ACM
CRAH
SinglePackaged1Phase
SinglePackaged3Phase
Split1Phase
Split3Phase
SubType | SubType | enumerated list | none | Floor | [5 empty] | Defaulted |  |  |  | Air System equipment subtype | 2013 NR ACM
Other
Room
SinglePackaged1Phase
SinglePackaged3Phase
Split1Phase
Split3Phase
Wall
SupplementalStorageTankVolume | SuppStorTankVol | decimal | gal | [6 empty] | Optional
SupplyAirSegmentReference | SupAirSegRef | reference | none | [7 empty] | AirSeg
SupplyFlowRated | SupFlowRtd | decimal | ft3 per min | [6 empty] | Defaulted
SupplyPlenumZoneReference | SupPlenumZnRef | reference | none | [6 empty] | Optional | ThrmlZn |  |  |  | 2013 NR ACM: 2.3.2
SystemStoryCount | SysStoryCnt | integer | none | [6 empty] | CondRequired
T24DHWType | T24DHWType | integer | none | [6 empty] | Required |  |  |  | This term was created to combine SDD term Size and Type into a numerical value for the T24SDD.DLL
TankCategory | TankCat | enumerated list | none | Boiler | [5 empty] | Optional
Commercial Instantaneous (TE)
Commercial Storage (TE & SBL)
Indirect
Instantaneous
Storage
TankExteriorInsulationRValue | TankExtInsR | decimal | h ft2 F per Btu | [6 empty] | Optional
TankHeight | TankHgt | decimal | ft |  | No |  |  |  |  | Required
TankHeightSimulated | TankHgtSim | decimal | ft |  | No |  |  |  |  | CondRequired
TankInteriorInsulationRValue | TankIntInsR | decimal | h ft2 F per Btu | [6 empty] | Optional
TankLengthToWidthRatio | TankLenToWdRat | decimal |  |  | No |  |  |  |  | CondRequired
TankNodeCount | TankNodeCnt | enumerated list | none | 10 | No |  |  |  |  | Required
5
6
7
8
9
TankRValue | TankR | decimal | h ft2 F per Btu |  | No |  |  |  |  | Required
TankShape | TankShape | enumerated list | none | HorizontalCylinder | No |  |  |  |  | Required
Rectangular
VerticalCylinder
TankVolume | TankVol | decimal | gal | [6 empty] | CondRequired
TankZone | TankZn | enumerated list | none | Conditioned | [5 empty] | Optional
Outside or in Exterior Closet
Unconditioned
TemperatureControl | TempCtrl | enumerated list | none | Fixed | [5 empty] | Defaulted |  |  |  |  | 2013 NR ACM 5.7.2.2 Cooling Control
FixedDualSetpoint
OutsideAirReset
Scheduled
WetBulbReset
TemperatureControl | TempCtrl | enumerated list | none | Fixed | [5 empty] | Defaulted
None
Scheduled
TemperatureSetPointScheduleReference | TempSetptSchRef | reference | none | [6 empty] | CondRequired |  | Schedule
TemperatureSetpointScheduleReference | TempSetptSchRef | reference | [7 empty] | CondRequired |  | Schedule
ThermalEfficiency | ThrmlEff | decimal | none | [6 empty] | CondRequired |  |  |  | The full load of a boiler or water heater or heating coil efficiency calculated as the ratio of heat transferred to the water divided by the heat input of the fuel. | 2013 NR ACM 5.8.1 Boilers equation 59 Used in residential CF1R-PRF
ThermalEfficiency | ThrmlEff | decimal | none | [6 empty] | CondRequired
TotalAirFlow | TotAirFlow | decimal | ft3 per min |  | No |  |  |  |  | Defaulted
TotalFanHP | TotFanHP | decimal | hp | [6 empty] | Required |  |  |  | The sum of the nameplate rated horsepower (hp) of all fan motors on the cooling tower | 2013 NR ACM: 5.8.3 Cooling Towers CoolingTower Total Fan Power
TotalHead | TotHd | decimal | ft | [6 empty] | Required
TotalInputRating | TotInpRating | decimal | none | [6 empty] | Optional
TotalStaticPressure | TotStaticPress | decimal | in water column | [6 empty] | CondRequired |  |  |  | The design static pressure for the Fan | 2013 NR ACM 5.7.3 Fan Systems Supply Fan Static Pressure Return/Relief Design Static Pressure
TotalTankVolume | TotTankVol | decimal | gal | [6 empty] | Optional
Type | Type | enumerated list | none | Connector | [5 empty] | Compulsory |  |  |  |  | AirSegmentType
ExhaustSegment
OutsideAir
Relief
Return
Supply
Type | Type | enumerated list | none | ChilledWater | [5 empty] | Compulsory |  |  |  | FluidSystemType
CondenserWater
HotWater
ServiceHotWater
Type | Type | enumerated list | none | MakeupFluid | [5 empty] | Compulsory |  |  |  | FluidSegmentType
PrimaryReturn
PrimarySupply
SecondaryReturn
SecondarySupply
Type | Type | enumerated list | none | AbsorptionSingleEffect | [5 empty] | Required |  |  |  | ChillerType
Centrifugal
Reciprocating
Screw
Scroll
Type | Type | enumerated list | none | ClosedTower | [5 empty] | Defaulted |  |  |  | HeatRejectionType
OpenTower
Type | Type | enumerated list | none | Conventional | [5 empty] | Defaulted
HeatPumpPackaged
HeatPumpSplit
Type | Type | enumerated list | none | HotWater | [5 empty] | Required |  |  |  |  | 2013 NR ACM: 5.8.1 Boilers Boiler Type;
Steam
Type | Type | enumerated list | none | ParallelFanBox | [5 empty] | Compulsory |  |  |  | TerminalUnitType | 2013 NR ACM 5.6.2 Terminal Device Data
SeriesFanBox
Uncontrolled
VAVNoReheatBox
VAVReheatBox
Type | Type | enumerated list | none | Energy | [5 empty] | Required |  |  |  | ProcessLoadType
Flow
Type | Type | enumerated list | none | Direct | [5 empty] | Required |  |  |  | Defines the type of EvaporativeCooler operation | 2013 NR ACM 5.7.5.3 Evaporative Cooler Evaporative Cooling Type
Indirect
Type | Type | enumerated list | none | Casework | [5 empty] | Optional |  |  |  | RefrigerationEquipmentType | 2013 NR ACM 5.4.6 Commerical Refrigeration Equipment
WalkInCooler
WalkInFreezer
Type | Type | enumerated list | none | ChilledWater | [5 empty] | Compulsory |  |  |  | CoilCoolingType | 2013 NR ACM 5.7.5.1 Cooling Systems General
DirectExpansion
Type | Type | enumerated list | none | Furnace | [5 empty] | Compulsory |  |  |  | CoilHeatingType
HeatPump
HotWater
Resistance
Type | Type | enumerated list | none | CounterFlow | [5 empty] | Defaulted |  |  |  | HeatExchangerType
Type | Type | enumerated list | none | Conditioned | [5 empty] | Defaulted |  |  |  | Defines the type of conditioning in the thermal zone | 2013 NR ACM 5.3 Thermal Zones Thermal Zone type values are: directly conditioned, indirectly conditioned, unconditioned or plenum
Plenum
Unconditioned
Type | Type | enumerated list | none | CompactHotWaterDistributionSystemHERS | [5 empty] | Required |  |  |  | RecirculationDHWSystemType
DemandRecirculationSensorControlsHERS
DemandRecirculationSensorControlsNR
RecirculatingDemandControlPushButtonHERS
RecirculatingDemandControlledPushButton
RecirculationNonDemandHERS_NR
RecirculationNonDemandNR
StandardDistributionCentralParallelPipingHERS
StandardDistributionCentralParallelPipingNR
StandardDistributionInsulatedPipesBelowGradeNR
StandardDistributionInsulatedPipesHERS
StandardDistributionInsulatedPipesNR
StandardDistributionNR
Type | Type | enumerated list | none | DOASCV | [5 empty] | Compulsory |  |  |  |  | 2013 NR ACM: 5.7 HVAC Secondary Systems; Tables 15 and N2-16 to N2-23
DOASVAV
Exhaust
PVAV
SPVAC
SPVHP
SZAC
SZHP
SZVAVAC
SZVAVHP
VAV
Type | Type | enumerated list | none | Baseboard | [5 empty] | Compulsory |  |  |  | ZoneSystemType | 2013 NR ACM: 5.7 HVAC Secondary Systems; Tables 15 and N2-16 to N2-23
Exhaust
FPFC
Furnace
MiniSplitAC
MiniSplitHP
PTAC
PTHP
PassiveBeam
SPVAC
SPVHP
SZAC
SZHP
WSHP
Type | Type | enumerated list | none | Plate | [5 empty] | Defaulted
Wheel
Type | Type | enumerated list | none | ChilledWater | No |  |  |  |  | Required
UniformEnergyFactor | UEF | decimal | none |  | No |  |  |  |  | CondRequired
UnloadRatioMinimum | UnldRatMin | decimal | none | [6 empty] | Defaulted |  |  |  | The minimum unloading capacity of the Chiller, expressed as a fraction of the rated capacity. Below this level the equipment must cycle to meet the load. | 2013 NR ACM: 5.8.2 Chillers Table 85 Default Minimum Unloading Ratios;
UnloadRatioMinimum | UnldRatMin | decimal | none | [6 empty] | Defaulted |  |  |  | The minimum unloading capacity of the Boiler,expressed as a fraction of the rated capacity. Below this level the equipment must cycle to meet the load. | 2013 NR ACM: 5.8.1 Boilers Boiler Minimum Unloading Ratio, Table 64,
UnmetCoolingLoadHours | UnmetClgLdHrs | decimal | h | [6 empty] | NotInput |  |  |  | The number of hours during the year when the space temperature is below the heating set point temperature or greater than the cooling set point temperature. UnmetLoadHours are used to determine if resizing is required. If greater than 300 there are rules for adjusting the baseline model to decrease the UnmetLoadHours | 2013 NR ACM 2.5 HVAC Capacity Requirements and Sizing;
UnmetHeatingLoadHours | UnmetHtgLdHrs | decimal | h | [6 empty] | NotInput |  |  |  | The number of hours during the year when the space temperature is below the heating set point temperature or greater than the cooling set point temperature. UnmetLoadHours are used to determine if resizing is required. If greater than 300 there are rules for adjusting the baseline model to decrease the UnmetLoadHours | 2013 NR ACM 2.5 HVAC Capacity Requirements and Sizing;
VentilationControlMethod | VentCtrlMthd | enumerated list | none | CO2Sensors | [5 empty] | Defaulted |  |  |  | The method used to determine outside air ventilation needed for each hour in the simulation | 2013 NR ACM 5.6.5.4 Outdoor Air Ventilation Ventilation Control Method
Fixed
VentilationSource | VentSrc | enumerated list | none | Forced | [5 empty] | Required
Natural
None
VentilationSpecificationMethod | VentSpecMthd | enumerated list | none | AirChangesPerHour | [5 empty] | Defaulted
FlowPerArea
FlowPerPerson
FlowPerZone
Maximum
NoVentilation
Sum
VentilationStandard | VentStd | enumerated list | none | T24_2013 | [5 empty] | Defaulted
VentilationStandardDescription | VentStdDesc | string | none |  | No |  |  |  |  | CondRequired
VentilationSystemPriority | VentSysPriority | integer | none | [6 empty] | Defaulted
VentilationSystemReference | VentSysRef | reference | none | [6 empty] | CondRequired | AirSys |  |  | Defines the HVAC system that provides ventlation air to the space. The same system might also be the primary source of space heating/cooling. In this case, the PrimAirCondgSysRef property should reference the same system name. Both AirSystem and ZoneSystem are valid object assignments for this property. However, if the ventilation and primary air conditioning systems are different, the ventilation system must be defined as the only AirSystem serving the zone.
ZnSys
Version | Version | string | none |  | No
WaterEconomizerCWSTemperatureMaximum | WtrEconoCWSTempMax | decimal | F | [6 empty] | Required |  |  |  | The control temperature of the condenser water supply temperature above which the water-side economizer is disabled. | 2013 NR ACM 5.8.4 Water-side Economizers Water-Side Economizer Maximum CWS
WaterEconomizerCWSTemperatureSetpoint | WtrEconoCWSTempSetpt | decimal | F | [6 empty] | Required |  |  |  | The design condenser water supply temperature for the cooling tower in economizer mode. | 2013 NR ACM 5.8.4 Water-side Economizers Water-Side Economizer CWS Setpoint
WaterEconomizerDBTemperatureMaximum | WtrEconoDBTempMax | decimal | F | [6 empty] | Required |  |  |  | The control temperature (outside air dry-bulb temperature) above which the water-side economizer is disabled. | 2013 NR ACM 5.8.4 Water-side Economizers Water-Side Economizer Maximum Tdb
WaterEconomizerHXEffectiveness | WtrEconoHXEff | decimal | none | [6 empty] | Required |  |  |  | Ratio expressing the effectiveness of a water-side heat exchanger at design conditions,dependent on entering and leaving temperatures | 2013 NR ACM 5.8.4 Water-side Economizers Water-Side Economizer HX Effectiveness
WaterEconomizerType | WtrEconoType | enumerated list | none | None | [5 empty] | Required |  |  |  | The type of water-side economizer used in cooling. | 2013 NR ACM 5.8.4 Water-side Economizers Water Economizer Type
ParallelHeatExchanger
SeriesHeatExchanger
StrainerCycle
ThermoCycle
WaterFlowCapacity | WtrFlowCap | decimal | gal per min | [6 empty] | Defaulted
WaterHeaterPipeLocation | PipeLocation | enumerated list | none | ConditionedSpace_WHPL | [5 empty] | Required |  |  |  | Location of 50% or more of the piping.
SemiConditionedSpace
UnconditionedSpace
UndergroundOrBurriedInSlabOrUnderSlab
WaterHeaterTankVolume | WtrHtrTankVol | decimal | gal | [6 empty] | Optional
WBEnteringTemperature | WBEntTemp | decimal | F | [10 empty] | The wet bulb temperature of the air as it enters cooling equipment. | 2013 NR ACM: 5.7.5 Cooling Systems Cooling Capacity Adjustment Curves Equations 14-16;
WesternCoolingChallengeSensibleCreditedCapacity | WCCSensCreditedCap | decimal | Btu per h | [6 empty] | Optional |  |  |  | The Credited Sensible Capacity of WCC certified systems at the WCEC test design conditionsThe ruleset will overwrite the simulated Sensible Capacity with this value for WCC certified systems
WesternCoolingChallengeTotalCreditedCapacity | WCCTotCreditedCap | decimal | Btu per h | [6 empty] | Optional |  |  |  | The Credited Total Capacity of WCC certified systems at the WCEC test design conditionsThe ruleset will overwrite the Simulated Total Capacity with this value for WCC certified systems
WesternCoolingChallengeTotalCreditedEER | WCCTotCreditedEER | decimal | Btu per W h | [6 empty] | Optional |  |  |  | The Credited EER of WCC certified systems at the WCEC test design conditionsThe ruleset will overwrite the Simulated EER with this value for WCC certified systems
WetBulbApproach | WetBulbApproach | decimal | F | [6 empty] | CondRequired
ZoneServedReference | ZnServedRef | reference | none | [6 empty] | Compulsory | ThrmlZn

## HvacEnumerations
| CBECC NR Term | CBECC NR Term Short Form | Property | Definition | CBECC NR XML Term
AmbientCondition
| Conditioned |  | AmbientCondition
| Unconditioned |  | AmbientCondition
CentrifugalType
| AirFoil |  | CentrifugalType
| BackwardInclined |  | CentrifugalType
| ForwardCurved |  | CentrifugalType
Classification
| Axial |  | Classification
| Centrifugal |  | Classification
CompressorZone
| Conditioned |  | CompressorZone
| Outside or in Exterior Closet |  | CompressorZone
| Unconditioned |  | CompressorZone
CondenserType
| Air |  | CondenserType
| Air_Chiller |  | CondenserType
| Fluid |  | CondenserType
| WaterSource |  | CondenserType
ControlMethod
| ConstantVolume |  | ControlMethod
| Dampers |  | ControlMethod
| InletVanes |  | ControlMethod
| TwoSpeed |  | ControlMethod
| VariablePitchBlades |  | ControlMethod
| VariableSpeedDrive |  | ControlMethod
ControlSystemType
| DDCToZone |  | ControlSystemType
| Other |  | ControlSystemType
ControlType
| DDC |  | ControlType
| Other |  | ControlType
CoolingControl
| ColdestReset |  | CoolingControl
| Fixed |  | CoolingControl
| FixedDualSetpoint |  | CoolingControl
| NoSATControl |  | CoolingControl
| OutsideAirReset |  | CoolingControl
| Scheduled |  | CoolingControl
| ScheduledDualSetpoint |  | CoolingControl
| WarmestResetFlowFirst |  | CoolingControl
| WarmestResetTemperatureFirst |  | CoolingControl
DaylightingControlType
| Continuous |  | DaylightingControlType
| ContinuousPlusOff |  | DaylightingControlType
| None |  | DaylightingControlType
| SteppedDimming |  | DaylightingControlType
| SteppedDimmingPlusOff |  | DaylightingControlType
| SteppedSwitching |  | DaylightingControlType
DefrostControl
| ExhaustAirRecirculation |  | DefrostControl
| ExhaustOnly |  | DefrostControl
| MinimumExhaustTemperature |  | DefrostControl
| None |  | DefrostControl
DischargePriority
| Chiller |  | DischargePriority
| Storage |  | DischargePriority
DistributionType
| DemandControl |  | DistributionType |  | Demand Control (Standard Design for new construction)
| NoControlContinuousPumping |  | DistributionType |  | No Control (continuous pumping)
| NoLoopsNoCentralPump |  | DistributionType |  | No loops or central system pump
| TemperatureModulation |  | DistributionType |  | Temperature modulation
| TemperatureModulationMonitoring |  | DistributionType |  | Temperature modulation and monitoring
DraftType
| Condensing |  | DraftType
| MechanicalNoncondensing |  | DraftType
| Natural |  | DraftType
DuctLocation
| Conditioned |  | DuctLocation
| None_ZSDL |  | DuctLocation
| Other_ZSDL |  | DuctLocation
| Unconditioned |  | DuctLocation
EconomizerControlMethod
| DifferentialDryBulb |  | EconomizerControlMethod
| DifferentialDryBulbAndEnthalpy |  | EconomizerControlMethod
| DifferentialEnthalpy |  | EconomizerControlMethod
| FixedDryBulb |  | EconomizerControlMethod
| NoEconomizer |  | EconomizerControlMethod
EconomizerIntegration
| Integrated |  | EconomizerIntegration
| IntegratedEconomizer_HE |  | EconomizerIntegration
| NonIntegrated |  | EconomizerIntegration
| NonIntegratedEconomizer_HE |  | EconomizerIntegration
ElementType
| ElectricResistance |  | ElementType |  | Electric Resistance
| Gas |  | ElementType
| HeatPump |  | ElementType |  | Heat Pump
ExhaustControlMethod
| COControl |  | ExhaustControlMethod
| ConstantFlowConstantSpeedFan |  | ExhaustControlMethod
| NoCOControl |  | ExhaustControlMethod
| VariableFlowConstantSpeedFan |  | ExhaustControlMethod
| VariableFlowVariableSpeedFan |  | ExhaustControlMethod
ExhaustOperationMode
| CoupledToSystem |  | ExhaustOperationMode
| DecoupledFromSystem |  | ExhaustOperationMode
ExhaustSystemType
| CommercialKitchen |  | ExhaustSystemType
| General |  | ExhaustSystemType
| Laboratory |  | ExhaustSystemType
| ParkingGarage |  | ExhaustSystemType
FanControl
| Continuous |  | FanControl
| ContinuousFanControlAS |  | FanControl
| Cycling |  | FanControl
| CyclingFanControlAS |  | FanControl
FanPosition
| BlowThrough |  | FanPosition
| Coincident |  | FanPosition
FanType
| Axial |  | FanType
| Centrifugal |  | FanType
FuelSource
| Electric |  | FuelSource
| Electric |  | FuelSource
| Electric |  | FuelSource
| Electricity_PerfNR |  | FuelSource
| Gas |  | FuelSource
| Gas |  | FuelSource
| Gas |  | FuelSource
| GasWaterHeater_PerfNR |  | FuelSource
| Indirect |  | FuelSource
| OilNoLongerValid |  | FuelSource
| OilNoLongerValid |  | FuelSource |  | Oil (no longer valid)
FurnaceIgnitionType
| IntermittentIgnitionDevice |  | FurnaceIgnitionType
| PilotLight |  | FurnaceIgnitionType
FurnaceType
| Fan |  | FurnaceType
| Gravity |  | FurnaceType
HeatPumpDefrostControl
| OnDemand |  | HeatPumpDefrostControl
| TimedCycle |  | HeatPumpDefrostControl
HeatPumpDefrostHeatSource
| Electric |  | HeatPumpDefrostHeatSource
| HotGas |  | HeatPumpDefrostHeatSource
HeatPumpWaterHeaterBrand
| A. O. Smith |  | HeatPumpWaterHeaterBrand
| American |  | HeatPumpWaterHeaterBrand
| Bradford White |  | HeatPumpWaterHeaterBrand
| EcoSense |  | HeatPumpWaterHeaterBrand
| GE |  | HeatPumpWaterHeaterBrand
| Kenmore |  | HeatPumpWaterHeaterBrand
| Lochinvar |  | HeatPumpWaterHeaterBrand
| Reliance |  | HeatPumpWaterHeaterBrand
| Rheem |  | HeatPumpWaterHeaterBrand
| Richmond |  | HeatPumpWaterHeaterBrand
| Ruud |  | HeatPumpWaterHeaterBrand
| Sanden |  | HeatPumpWaterHeaterBrand
| State |  | HeatPumpWaterHeaterBrand
| Stiebel Eltron |  | HeatPumpWaterHeaterBrand
| US Craftmaster |  | HeatPumpWaterHeaterBrand
| Whirlpool |  | HeatPumpWaterHeaterBrand
HeatPumpWaterHeaterModel
| 10 50 DHPHT 120 (50 gal) |  | HeatPumpWaterHeaterModel
| 10 50 DHPHTNE 120 (50 gal) |  | HeatPumpWaterHeaterModel
| 10 60 DHPT 120 (60 gal) |  | HeatPumpWaterHeaterModel
| 10 66 DHPHT 120 (66 gal) |  | HeatPumpWaterHeaterModel
| 10 66 DHPHTN 120 (66 gal) |  | HeatPumpWaterHeaterModel
| 10 80 DHPHT 120 (80 gal) |  | HeatPumpWaterHeaterModel
| 10 80 DHPHTNE 120 (80 gal) |  | HeatPumpWaterHeaterModel
| 10 80 DHPT 120 (80 gal) |  | HeatPumpWaterHeaterModel
| 10E50-HP4D (50 gal) |  | HeatPumpWaterHeaterModel
| 10E65-HP4D (65 gal) |  | HeatPumpWaterHeaterModel
| 10E80-HP4D (80 gal) |  | HeatPumpWaterHeaterModel
| 12E50-HP (50 gal) |  | HeatPumpWaterHeaterModel
| 12E80-HP (80 gal) |  | HeatPumpWaterHeaterModel
| 153.32116 (60 gal) |  | HeatPumpWaterHeaterModel
| 153.32118 (80 gal) |  | HeatPumpWaterHeaterModel
| 153.5925 (50 gal) |  | HeatPumpWaterHeaterModel
| 153.5926 (60 gal) |  | HeatPumpWaterHeaterModel
| 153.5928 (80 gal) |  | HeatPumpWaterHeaterModel
| 6 50 DHPHT 120 (50 gal) |  | HeatPumpWaterHeaterModel
| 6 66 DHPHT 120 (66 gal) |  | HeatPumpWaterHeaterModel
| 6 80 DHPHT 120 (80 gal) |  | HeatPumpWaterHeaterModel
| 6 80 DHPT 102 (80 gal) |  | HeatPumpWaterHeaterModel
| Accelera 220 E (58 gal) |  | HeatPumpWaterHeaterModel
| Accelera 300/WHP 300 (80 gal) |  | HeatPumpWaterHeaterModel
| BEH50DCEJSB (50 gal) |  | HeatPumpWaterHeaterModel
| BEH80DCEJSB (80 gal) |  | HeatPumpWaterHeaterModel
| EP6 80 DHPT 102 (80 gal) |  | HeatPumpWaterHeaterModel
| EPX 60 DHPT (60 gal) |  | HeatPumpWaterHeaterModel
| EPX 80 DHPT (80 gal) |  | HeatPumpWaterHeaterModel
| FPTU 50 120 (50 gal) |  | HeatPumpWaterHeaterModel
| FPTU 66 120 (66 gal) |  | HeatPumpWaterHeaterModel
| FPTU 80 120 (80 gal) |  | HeatPumpWaterHeaterModel
| GEH50DEEJSC (50 gal) |  | HeatPumpWaterHeaterModel
| GEH50DEEJXXX (50 gal) |  | HeatPumpWaterHeaterModel
| GEH50DFEJSR (50 gal) |  | HeatPumpWaterHeaterModel
| GEH50DHEKSC (50 gal) |  | HeatPumpWaterHeaterModel
| GEH80DEEJSC (80 gal) |  | HeatPumpWaterHeaterModel
| GEH80DFEJSR (80 gal) |  | HeatPumpWaterHeaterModel
| GEH80DHEKSC (80 gal) |  | HeatPumpWaterHeaterModel
| GS3-45HPA-US & GAUS-1315EQTD (83 gal) |  | HeatPumpWaterHeaterModel
| GS3-45HPA-US & GAUS-160QTA (43 gal) |  | HeatPumpWaterHeaterModel
| GS3-45HPA-US & SAN-43SSAQA (43 gal) |  | HeatPumpWaterHeaterModel
| GS3-45HPA-US & SAN-83SSAQA (83 gal) |  | HeatPumpWaterHeaterModel
| GUS-45HPA-US & GAUS-1315EQTD (83 gal) |  | HeatPumpWaterHeaterModel
| GUS-45HPA-US & SAN-83SSAQA (83 gal) |  | HeatPumpWaterHeaterModel
| HB50ES (50 gal) |  | HeatPumpWaterHeaterModel
| HB50RH (50 gal) |  | HeatPumpWaterHeaterModel
| HB50RM (50 gal) |  | HeatPumpWaterHeaterModel
| HB50RU (50 gal) |  | HeatPumpWaterHeaterModel
| HHPT 80 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HP10-50H45DV (50 gal) |  | HeatPumpWaterHeaterModel
| HP10-80H45DV (80 gal) |  | HeatPumpWaterHeaterModel
| HP6 50 DHPT 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HP6 66 DHPT 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HP6 80 DHPT 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPA051KD 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPA052KD 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPA067KD 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPA068KD 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPA081KD 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPA082KD 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPE10260H045DV (60 gal) |  | HeatPumpWaterHeaterModel
| HPE10280H045DV (80 gal) |  | HeatPumpWaterHeaterModel
| HPE2F80HD045VU 102 (80 gal) |  | HeatPumpWaterHeaterModel
| HPE2K60HD045V (60 gal) |  | HeatPumpWaterHeaterModel
| HPE2K60HD045V (60 gal) |  | HeatPumpWaterHeaterModel
| HPE2K80HD045V (80 gal) |  | HeatPumpWaterHeaterModel
| HPE2K80HD045V (80 gal) |  | HeatPumpWaterHeaterModel
| HPE6280H045DV 102 (80 gal) |  | HeatPumpWaterHeaterModel
| HPHE10250H045DV 102 (50 gal) |  | HeatPumpWaterHeaterModel
| HPHE10250H045DVN 102 (50 gal) |  | HeatPumpWaterHeaterModel
| HPHE10266H045DV 102 (66 gal) |  | HeatPumpWaterHeaterModel
| HPHE10266H045DVN 102 (66 gal) |  | HeatPumpWaterHeaterModel
| HPHE10280H045DV 102 (80 gal) |  | HeatPumpWaterHeaterModel
| HPHE10280H045DVN 102 (80 gal) |  | HeatPumpWaterHeaterModel
| HPHE2F50HD045VU 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPHE2F66HD045VU 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPHE2F80HD045VU 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K50HD045V 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K50HD045VC 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K50HD045VN 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K50HD045VUN 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K66HD045V 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K66HD045VC 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K66HD045VUN 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K80HD045V 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K80HD045VC 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPHE2K80HD045VUN 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPHE6250H045DV (50 gal) |  | HeatPumpWaterHeaterModel
| HPHE6266H045DV (66 gal) |  | HeatPumpWaterHeaterModel
| HPHE6280H045DV (80 gal) |  | HeatPumpWaterHeaterModel
| HPHE650H045DV (50 gal) |  | HeatPumpWaterHeaterModel
| HPSE2K50HD045V 100 (WP) (50 gal) |  | HeatPumpWaterHeaterModel
| HPSE2K50HD045VC 100 (WP) (50 gal) |  | HeatPumpWaterHeaterModel
| HPSE2K80HD045V (80 gal) |  | HeatPumpWaterHeaterModel
| HPSE2K80HD045VC (80 gal) |  | HeatPumpWaterHeaterModel
| HPTU 50 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPTU 50N 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPTU 66 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPTU 66N 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPTU 80 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPTU 80N 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPX 50 DHPT 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPX 50 DHPTNE 120 (50 gal) |  | HeatPumpWaterHeaterModel
| HPX 66 DHPT 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPX 66 DHPTNE 120 (66 gal) |  | HeatPumpWaterHeaterModel
| HPX 80 DHPT 120 (80 gal) |  | HeatPumpWaterHeaterModel
| HPX 80 DHPTNE 120 (80 gal) |  | HeatPumpWaterHeaterModel
| PHPT 60 (60 gal) |  | HeatPumpWaterHeaterModel
| PHPT 80 (80 gal) |  | HeatPumpWaterHeaterModel
| PROPH50 T2 RH245 (50 gal) |  | HeatPumpWaterHeaterModel
| PROPH50 T2 RH350 D (50 gal) |  | HeatPumpWaterHeaterModel
| PROPH80 T2 RH245 (80 gal) |  | HeatPumpWaterHeaterModel
| PROPH80 T2 RH350 D (80 gal) |  | HeatPumpWaterHeaterModel
| PROUH50 T2 RU245 (50 gal) |  | HeatPumpWaterHeaterModel
| PROUH50 T2 RU350 D (50 gal) |  | HeatPumpWaterHeaterModel
| PROUH65 T2 RU350 D (65 gal) |  | HeatPumpWaterHeaterModel
| PROUH80 T2 RU245 (80 gal) |  | HeatPumpWaterHeaterModel
| PROUH80 T2 RU350 D (80 gal) |  | HeatPumpWaterHeaterModel
| RE2H50R10B-1NCWT (50 gal) |  | HeatPumpWaterHeaterModel
| RE2H80R10B-1NCWT (80 gal) |  | HeatPumpWaterHeaterModel
| XE50T10HD50U0 (50 gal) |  | HeatPumpWaterHeaterModel
| XE50T12EH45U0 (50 gal) |  | HeatPumpWaterHeaterModel
| XE50T12EH45U0W (50 gal) |  | HeatPumpWaterHeaterModel
| XE65T10HD50U0 (65 gal) |  | HeatPumpWaterHeaterModel
| XE80T10HD50U0 (80 gal) |  | HeatPumpWaterHeaterModel
| XE80T12EH45U0 (80 gal) |  | HeatPumpWaterHeaterModel
| XE80T12EH45U0W (80 gal) |  | HeatPumpWaterHeaterModel
ModelingMethod
| BrakeHorsePower |  | ModelingMethod
| Detailed |  | ModelingMethod
| PowerPerUnitFlow |  | ModelingMethod
| PowerPerUnitFlow |  | ModelingMethod
| StaticPressure |  | ModelingMethod
ModulationControl
| Bypass |  | ModulationControl
| Cycling |  | ModulationControl
| TwoSpeed |  | ModulationControl
| VariableSpeedDrive |  | ModulationControl
MotorPosition
| InAirStream |  | MotorPosition
| NotInAirStream |  | MotorPosition
MotorType
| Enclosed |  | MotorType
| Open |  | MotorType
NightCycleFanControl
| CycleOnCallAnyZone |  | NightCycleFanControl
| CycleOnCallPrimaryZone |  | NightCycleFanControl
| CycleZoneFansOnly |  | NightCycleFanControl
| StaysOff |  | NightCycleFanControl
OperationControl
| OnDemand |  | OperationControl
| Scheduled |  | OperationControl
| StandBy |  | OperationControl
Path
| Direct |  | Path
| Ducted |  | Path
| PlenumZones |  | Path
PipeLocation
| Conditioned |  | PipeLocation
| SemiConditioned |  | PipeLocation
| Unconditioned |  | PipeLocation
| Underground |  | PipeLocation
RecoveryType
| LatentOnly |  | RecoveryType
| SensibleOnly |  | RecoveryType
| Total |  | RecoveryType
ReheatControlMethod
| DualMaximum |  | ReheatControlMethod
| DualMaximum_TU |  | ReheatControlMethod
| SingleMaximum |  | ReheatControlMethod
| SingleMaximum_TU |  | ReheatControlMethod
ResidentialDHWDwellingUnitDistributionType
| RecirculationNonDemand |  | ResidentialDHWDwellingUnitDistributionType
SecondaryAirSource
| OutdoorAir |  | SecondaryAirSource
| ReturnAir |  | SecondaryAirSource
Source
| MunicipalWater |  | Source
| NoExternalSource |  | Source
SpeedControl
| ConstantSpeed |  | SpeedControl
| VariableSpeed |  | SpeedControl
Status
| Altered |  | Status
| Existing |  | Status
| New |  | Status
StorageLocation
| Indoor |  | StorageLocation
| Outdoor |  | StorageLocation
| Underground |  | StorageLocation
StorageLocationSimulated
| Outdoor |  | StorageLocationSimulated
| Zone |  | StorageLocationSimulated
SubType
| CRAC |  | SubType | Computer Room Air Conditioner
| CRAH |  | SubType | Computer Room Air Handler
| Floor |  | SubType
| NA_ZS |  | SubType
| Other |  | SubType
| Room |  | SubType
| SinglePackaged1Phase |  | SubType | Air System Packaged1 Phase equipment
| SinglePackaged1Phase |  | SubType
| SinglePackaged3Phase |  | SubType | Air System Packaged3 Phase equipment
| SinglePackaged3Phase |  | SubType
| Split1Phase |  | SubType | Air System Split1 Phase equipment
| Split1Phase |  | SubType
| Split3Phase |  | SubType | Air System Split3 Phase equipment
| Split3Phase |  | SubType
| Wall |  | SubType
TankCategory
| Boiler |  | TankCategory |  | Boiler
| Commercial Instantaneous (TE) |  | TankCategory
| Commercial Storage (TE & SBL) |  | TankCategory
| Indirect |  | TankCategory
| Instantaneous |  | TankCategory
| Storage |  | TankCategory
TankNodeCount
| 10 |  | TankNodeCount
| 5 |  | TankNodeCount
| 6 |  | TankNodeCount
| 7 |  | TankNodeCount
| 8 |  | TankNodeCount
| 9 |  | TankNodeCount
TankShape
| HorizontalCylinder |  | TankShape
| Rectangular |  | TankShape
| VerticalCylinder |  | TankShape
TankZone
| Conditioned |  | TankZone
| Outside or in Exterior Closet |  | TankZone
| Unconditioned |  | TankZone
TemperatureControl
| Fixed |  | TemperatureControl
| Fixed |  | TemperatureControl
| FixedDualSetpoint |  | TemperatureControl
| None |  | TemperatureControl
| OutsideAirReset |  | TemperatureControl
| Scheduled |  | TemperatureControl
| Scheduled |  | TemperatureControl
| WetBulbReset |  | TemperatureControl
Type
| AbsorptionSingleEffect |  | Type
| Baseboard |  | Type
| Casework |  | Type
| Centrifugal |  | Type
| ChilledWater |  | Type
| ChilledWater |  | Type
| ChilledWater |  | Type
| ClosedTower |  | Type
| CompactHotWaterDistributionSystemHERS |  | Type |  | (HERS req'd) Compact Distribution System
| CondenserWater |  | Type
| Conditioned |  | Type
| Connector |  | Type
| Conventional |  | Type
| CounterFlow |  | Type
| DemandRecirculationSensorControlsHERS |  | Type |  | (HERS req'd) Recirculation, Demand Control Occupancy/Motion
| DemandRecirculationSensorControlsNR |  | Type |  | Recirculation, Demand Control Occupancy/Motion
| Direct |  | Type
| DirectExpansion |  | Type
| DOASCV |  | Type
| DOASVAV |  | Type
| Energy |  | Type
| Exhaust |  | Type
| Exhaust |  | Type
| ExhaustSegment |  | Type
| Flow |  | Type
| FPFC |  | Type | Four Pipe Fan Coil
| Furnace |  | Type
| Furnace |  | Type
| HeatPump |  | Type
| HeatPumpPackaged |  | Type
| HeatPumpSplit |  | Type
| HotWater |  | Type
| HotWater |  | Type
| HotWater |  | Type
| HV |  | Type | Heating Ventilation
| Indirect |  | Type
| MakeupFluid |  | Type
| MiniSplitAC |  | Type
| MiniSplitHP |  | Type
| OpenTower |  | Type
| OutsideAir |  | Type
| ParallelFanBox |  | Type
| PassiveBeam |  | Type
| Plate |  | Type
| Plenum |  | Type
| PrimaryReturn |  | Type
| PrimarySupply |  | Type
| PTAC |  | Type | Package Terminal Air Conditioner
| PTHP |  | Type | Package Terminal Heat Pump
| PVAV |  | Type | Package Variable Air Volume
| Reciprocating |  | Type
| RecirculatingDemandControlledPushButton |  | Type |  | Recirculation, Demand Control Push Button
| RecirculatingDemandControlPushButtonHERS |  | Type |  | (HERS req'd) Recirculation, Demand Control Push Button
| RecirculationNonDemandHERS_NR |  | Type |  | (HERS req'd) Recirculation, Non-Demand Control
| RecirculationNonDemandNR |  | Type |  | Recirculation, Non-Demand Control
| Relief |  | Type
| Resistance |  | Type
| Return |  | Type
| Screw |  | Type
| Scroll |  | Type
| SecondaryReturn |  | Type
| SecondarySupply |  | Type
| SeriesFanBox |  | Type
| ServiceHotWater |  | Type
| SPVAC |  | Type
| SPVAC |  | Type
| SPVHP |  | Type
| SPVHP |  | Type
| StandardDistributionCentralParallelPipingHERS |  | Type |  | (HERS req'd) Parallel Piping
| StandardDistributionCentralParallelPipingNR |  | Type |  | Parallel Piping
| StandardDistributionInsulatedPipesBelowGradeNR |  | Type |  | Insulated and Protected Pipe Below Grade
| StandardDistributionInsulatedPipesHERS |  | Type |  | (HERS req'd) Pipe Insulation, All Lines
| StandardDistributionInsulatedPipesNR |  | Type |  | Pipe Insulation, All Lines
| StandardDistributionNR |  | Type |  | Standard
| Steam |  | Type
| Supply |  | Type
| SZAC |  | Type | Single Zone Air Conditioner
| SZAC |  | Type | Single Zone Air Conditioner
| SZHP |  | Type | Single Zone Heat Pump
| SZHP |  | Type | Single Zone Heat Pump
| SZVAVAC |  | Type | Single Zone Variable Air Volume Air Condiitioning
| SZVAVHP |  | Type | Single Zone Variable Air Volume Heat Pump
| Unconditioned |  | Type
| Uncontrolled |  | Type
| VAV |  | Type | Variable Air Volume
| VAVNoReheatBox |  | Type
| VAVReheatBox |  | Type
| WalkInCooler |  | Type
| WalkInFreezer |  | Type
| Wheel |  | Type
| WSHP |  | Type
VentilationControlMethod
| CO2Sensors |  | VentilationControlMethod
| Fixed |  | VentilationControlMethod
VentilationSource
| Forced |  | VentilationSource
| None |  | VentilationSource
VentilationSpecificationMethod
| AirChangesPerHour |  | VentilationSpecificationMethod
| FlowPerArea |  | VentilationSpecificationMethod
| FlowPerPerson |  | VentilationSpecificationMethod
| FlowPerZone |  | VentilationSpecificationMethod
| Maximum |  | VentilationSpecificationMethod
| NoVentilation |  | VentilationSpecificationMethod
| Sum |  | VentilationSpecificationMethod
VentilationStandard
| T24_2013 |  | VentilationStandard |  | T24-2013
WaterEconomizerType
| None |  | WaterEconomizerType
| ParallelHeatExchanger |  | WaterEconomizerType
| SeriesHeatExchanger |  | WaterEconomizerType
| StrainerCycle |  | WaterEconomizerType
| ThermoCycle |  | WaterEconomizerType
WaterHeaterPipeLocation
| ConditionedSpace_WHPL |  | WaterHeaterPipeLocation
| SemiConditionedSpace |  | WaterHeaterPipeLocation
| UnconditionedSpace |  | WaterHeaterPipeLocation
| UndergroundOrBurriedInSlabOrUnderSlab |  | WaterHeaterPipeLocation | Correct spelling error
(no property)
Compressor_Cooling
FancoilAHU_Cooling
IndoorCoil_Cooling
OutdoorCondensingUnit_Cooling
RefrigerantLineset_Cooling
TXV_EXV_Cooling

## CompObjects
CBECC NR Term | CBECC NR Term Short Form | Properties | Properties Short Form | CBECC NR Parent | SDD Parent | Building Properties | Reporting Component | SDD XSD Namespace | Components | Definition | Standards Reference | Calculations and Rules | Compliance Use | Collapsed From
CurveCubic | CrvCubic | Coefficient1 | Coef1 | Proj |  |  |  | comp |  | Curves expressed as cubic equations contain a variable raised to the 3rd power and 2nd power as follows: ax3 + bx2 + cx + d = 0 where the numbers represent exponent values |  |  | Optional
|  | Coefficient2 | Coef2
|  | Coefficient3 | Coef3
|  | Coefficient4 | Coef4
|  | MaximumOutput | MaxOut
|  | MaximumVariable1 | MaxVar1
|  | MinimumOutput | MinOut
|  | MinimumVariable1 | MinVar1
|  | Name | Name
CurveDoubleQuadratic | CrvDblQuad | Coefficient1 | Coef1 | Proj |  |  |  | comp |  | These curves consists of two quadratic equations e.g. ax2 + bx + c + dy2 + ey + f = 0 where the numbers represent exponent values |  |  | Optional
|  | Coefficient2 | Coef2
|  | Coefficient3 | Coef3
|  | Coefficient4 | Coef4
|  | Coefficient5 | Coef5
|  | Coefficient6 | Coef6
|  | MaximumOutput | MaxOut
|  | MaximumVariable1 | MaxVar1
|  | MaximumVariable2 | MaxVar2
|  | MinimumOutput | MinOut
|  | MinimumVariable1 | MinVar1
|  | MinimumVariable2 | MinVar2
|  | Name | Name
CurveLinear | CrvLin | Coefficient1 | Coef1 | Proj |  |  |  | comp |  | Curves expressed as linear equations consist of variables and constants all with the power of one. For example: ax + by + c = 0 |  |  | Optional
|  | Coefficient2 | Coef2
|  | MaximumOutput | MaxOut
|  | MaximumVariable1 | MaxVar1
|  | MinimumOutput | MinOut
|  | MinimumVariable1 | MinVar1
|  | Name | Name
CurveMapDoubleVariable | CrvMapDblVar | ArrayOutput | ArrayOut | Proj |  |  |  | comp |  |  |  |  | Optional
|  | ArrayVariable1 | ArrayVar1
|  | ArrayVariable2 | ArrayVar2
|  | InterpolationMethod | InterpMthd
|  | MaximumOutput | MaxOut
|  | MaximumVariable1 | MaxVar1
|  | MaximumVariable2 | MaxVar2
|  | MinimumOutput | MinOut
|  | MinimumVariable1 | MinVar1
|  | MinimumVariable2 | MinVar2
|  | NormalizationPoint | NormalizationPt
|  | Type | Type
|  | UnitTypeOutput | UnitTypeOut
|  | UnitTypeVariable1 | UnitTypeVar1
|  | UnitTypeVariable2 | UnitTypeVar2
CurveMapSingleVariable | CrvMapSglVar | ArrayOutput | ArrayOut | Proj |  |  |  | comp |  |  |  |  | Optional
|  | ArrayVariable1 | ArrayVar1
|  | InterpolationMethod | InterpMthd
|  | MaximumOutput | MaxOut
|  | MaximumVariable1 | MaxVar1
|  | MinimumOutput | MinOut
|  | MinimumVariable1 | MinVar1
|  | NormalizationPoint | NormalizationPt
|  | Type | Type
|  | UnitTypeOutput | UnitTypeOut
|  | UnitTypeVariable1 | UnitTypeVar1
CurveQuadratic | CrvQuad | Coefficient1 | Coef1 | Proj |  |  |  | comp |  | Curves expressed as quadratic equations consist of a variable raised to the 2nd power and all other comonents of the equation are to the 1st power. For example: ax2 + bx + c = 0 where 2 represents an exponent value |  |  | Optional
|  | Coefficient2 | Coef2
|  | Coefficient3 | Coef3
|  | MaximumOutput | MaxOut
|  | MaximumVariable1 | MaxVar1
|  | MinimumOutput | MinOut
|  | MinimumVariable1 | MinVar1
|  | Name | Name
Project | Proj | AnalysisType | AnalysisType |  |  | AvgElecCost |  | comp | Building; DesignDay; ExternalShadingObject; Holiday; ThermalEnergyStorageModeScheduleDay; FluidSystem; ResidentialDHWSystemNR; ConstructAssembly; DoorConstruction; FenestrationConstruction; Luminaire; Material; Schedule; ScheduleDay; ScheduleWeek; SpaceFunctionDefaults |  |  |  |  | ComplianceDocumentsRequiredNonResidential ComplianceParameters T24ProjectTeam
|  | AutomaticDaylightingReport | AutoDayltgRpt |  |  | AvgOtherFuelCost
|  | AutomaticTimeSwitchReport | AutoTimeSwitchRpt |  |  | CliZn
|  | City | City |  |  | CliZnCounty
|  | CommercialKitchenMandatoryCompliance | CommKitchenMandComp |  |  | CliZnNum
|  | CommercialRefrigerationMandatoryCompliance | ComRfrgMandComp |  |  | DefaultDayltgCtrls
|  | ComplexHVACMandatoryCompliance | ComplexHVACMandComp |  |  | DisableDayltgCtrls
|  | ComplianceOptionAddition | CompOptAdd |  |  | GasType
|  | ComplianceOptionAlteration | CompOptAlt |  |  | HVACAutoSizing
|  | ComplianceOptionDomesticHotWater | CompOptDHW |  |  | HolidayReference
|  | ComplianceOptionEnvelope | CompOptEnve |  |  | Name
|  | ComplianceOptionExisting | CompOptExist |  |  | NatGasAvail
|  | ComplianceOptionLighting | CompOptLtg |  |  | OccFrac
|  | ComplianceOptionMechanical | CompOptMech |  |  | ProjectCounty
|  | ComplianceOptionNew | CompOptNew |  |  | WeatherStation
|  | ComplianceOptionPartialLighting | CompOptPartLtg |  |  | WeatherStationNum
|  | ComplianceOptionPartialMechanical | CompOptPartMech
|  | CompliancePathComputerRoom | CompPathComputerRm
|  | CompliancePathDomesticHotWater | CompPathDHW
|  | CompliancePathEnvelope | CompPathEnv
|  | CompliancePathKitchen | CompPathKit
|  | CompliancePathLaboratory | CompPathLab
|  | CompliancePathLighting | CompPathLtg
|  | CompliancePathMechanical | CompPathMech
|  | ComplianceReportPDF | CompReportPDF
|  | ComplianceReportStandard | CompReportStd
|  | ComplianceReportXML | CompReportXML
|  | ComplianceType | CompType
|  | CompressedAirMandatoryCompliance | CompressedAirMandComp
|  | ComputerRoomMandatoryCompliance | ComputerRoomMandComp
|  | DemandResponsiveReport | DemandResponsiveRpt
|  | DocumentAuthorAddress | DocAuthAddress
|  | DocumentAuthorCEAIdentification | DocAuthCEAIdent
|  | DocumentAuthorCity | DocAuthCity
|  | DocumentAuthorCompany | DocAuthCompany
|  | DocumentAuthorName | DocAuthName
|  | DocumentAuthorPhone | DocAuthPhone
|  | DocumentAuthorState | DocAuthState
|  | DocumentAuthorZipcode | DocAuthZipCode
|  | DomesticHotWaterDetailsLocation | DHWDetailsLctn
|  | ElectricalMandatoryCompliance | ElecMandComp
|  | ElevatorLightingVentilationMandatoryCompliance | ElevLtgVentMandComp
|  | EnvelopeDesignerAddress | EnvDsgnrAddress
|  | EnvelopeDesignerCity | EnvDsgnrCity
|  | EnvelopeDesignerCompany | EnvDsgnrCompany
|  | EnvelopeDesignerLicense | EnvDsgnrLicense
|  | EnvelopeDesignerName | EnvDsgnrName
|  | EnvelopeDesignerPhone | EnvDsgnrPhone
|  | EnvelopeDesignerState | EnvDsgnrState
|  | EnvelopeDesignerType | EnvDsgnrType
|  | EnvelopeDesignerZipCode | EnvDsgnrZipCode
|  | EnvelopeDetailsLocation | EnvDetailsLctn
|  | EscalatorSpeedControlMandatoryCompliance | EscalSpdCtrlMandComp
|  | ExceptionalConditionExteriorLighting | ExcptCondExtLtg
|  | ExceptionalConditionNarrative | ExcptCondNarrative
|  | ExceptionalConditionNoCoolingSystem | ExcptCondNoClgSys
|  | ExceptionalConditionRatedCapacity | ExcptCondRtdCap
|  | ExceptionalDesignModelFile | ExcptDsgnModelFile
|  | GeometryInputType | GeometryInpType
|  | InstitutionalTuningPAFReport | InstitutionalTuningPAFRpt
|  | LaboratoryExhaustMandatoryCompliance | LabExhaustMandComp
|  | LightingDesignerAddress | LtgDsgnrAddress
|  | LightingDesignerCity | LtgDsgnrCity
|  | LightingDesignerCompany | LtgDsgnrCompany
|  | LightingDesignerLicense | LtgDsgnrLicense
|  | LightingDesignerName | LtgDsgnrName
|  | LightingDesignerPhone | LtgDsgnrPhone
|  | LightingDesignerState | LtgDsgnrState
|  | LightingDesignerType | LtgDsgnrType
|  | LightingDesignerZipCode | LtgDsgnrZipCode
|  | LightingDetailsLocation | LtgDetailsLctn
|  | LightingOutdoorCompliance | LtgOutdrComp
|  | LightingSignCompliance | LtgSignComp
|  | LightingUnconditionedCompliance | LtgUncondComp
|  | MechanicalDesignerAddress | MechDsgnrAddress
|  | MechanicalDesignerCity | MechDsgnrCity
|  | MechanicalDesignerCompany | MechDsgnrCompany
|  | MechanicalDesignerLicense | MechDsgnrLicense
|  | MechanicalDesignerName | MechDsgnrName
|  | MechanicalDesignerPhone | MechDsgnrPhone
|  | MechanicalDesignerState | MechDsgnrState
|  | MechanicalDesignerType | MechDsgnrType
|  | MechanicalDesignerZipCode | MechDsgnrZipCode
|  | MechanicalDetailsLocation | MechDetailsLctn
|  | NRCAEnv02F | NRCAEnv02F
|  | NRCALti02A | NRCALti02A
|  | NRCALti03A | NRCALti03A
|  | NRCALti04A | NRCALti04A
|  | NRCALti05A | NRCALti05A
|  | NRCALto02A | NRCALto02A
|  | NRCAPrc01E | NRCAPrc01E
|  | NRCAPrc01F | NRCAPrc01F
|  | NRCAPrc02F | NRCAPrc02F
|  | NRCAPrc03F | NRCAPrc03F
|  | NRCAPrc04F | NRCAPrc04F
|  | NRCAPrc05F | NRCAPrc05F
|  | NRCAPrc06F | NRCAPrc06F
|  | NRCAPrc07F | NRCAPrc07F
|  | NRCAPrc08F | NRCAPrc08F
|  | NRCAPrc12F | NRCAPrc12F
|  | NRCAPrc13F | NRCAPrc13F
|  | NRCIElc01E | NRCIElc01E
|  | NRCIEnv01E | NRCIEnv01E
|  | NRCILti01E | NRCILti01E
|  | NRCILti02E | NRCILti02E
|  | NRCILti03E | NRCILti03E
|  | NRCILti04E | NRCILti04E
|  | NRCILti05E | NRCILti05E
|  | NRCILti06E | NRCILti06E
|  | NRCILto01E | NRCILto01E
|  | NRCILto02E | NRCILto02E
|  | NRCILts01E | NRCILts01E
|  | NRCIMch01E | NRCIMch01E
|  | NRCIPlb01E | NRCIPlb01E
|  | NRCIPlb02E | NRCIPlb02E
|  | NRCIPlb03E | NRCIPlb03E
|  | NRCIPlb21E | NRCIPlb21E
|  | NRCIPlb22E | NRCIPlb22E
|  | NRCISpv01E | NRCISpv01E
|  | NRCISth01E | NRCISth01E
|  | NRCVMch04H | NRCVMch04H
|  | NRCVPlb21H | NRCVPlb21H
|  | NRCVPlb22H | NRCVPlb22H
|  | NarrativeDetails | NarrativeDetails
|  | NumberOfDaysPerQuickAnalysisPeriod | NumOfDaysPerQuickAnalysisPeriod
|  | NumberOfQuickAnalysisPeriods | NumOfQuickAnalysisPeriods
|  | NumberTimeStepsPerHour | NumTimeStepsPerHr
|  | OccupancySensorCountReport | OccSensorCntRpt
|  | OutdoorControlsReport | OutdrCtrlsRpt
|  | ParkingGarageMandatoryCompliance | ParkingGarageMandComp
|  | PermitScope | PermitScope
|  | ProcessBoilerMandatoryCompliance | ProcBlrMandComp
|  | RefrigerationWarehouseMandatoryCompliance | RfrgWarehouseMandComp
|  | RuleReportFileAppend | RuleReportFileAppend
|  | RuleReportType | RuleReportType
|  | RunPeriodBeginDay | RunPeriodBeginDay
|  | RunPeriodBeginMonth | RunPeriodBeginMonth
|  | RunPeriodEndDay | RunPeriodEndDay
|  | RunPeriodEndMonth | RunPeriodEndMonth
|  | RunPeriodYear | RunPeriodYear
|  | RunTitle | RunTitle
|  | SimpleHVACMandatoryCompliance | SimpleHVACMandComp
|  | SimulateDesignDays | SimDsgnDays
|  | SimulationVariablesDaylighting | SimVarsDayltg
|  | SimulationVariablesFenestration | SimVarsFen
|  | SimulationVariablesHVACPrimary | SimVarsHVACPri
|  | SimulationVariablesHVACSecondary | SimVarsHVACSec
|  | SimulationVariablesHVACZone | SimVarsHVACZn
|  | SimulationVariablesSite | SimVarsSite
|  | SimulationVariablesThermalZone | SimVarsThrmlZn
|  | SoftwareVersion | SoftwareVersion
|  | SolarReadyMandatoryCompliance | SolReadyMandComp
|  | SolarThermalCompliance | SolThrmlComp
|  | StandardsVersion | StandardsVersion
|  | State | State
|  | StreetAddress | StreetAddress
|  | UseExceptionalDesignModel | UseExcptDsgnModel
|  | VentilationMulitplier | VentMult
|  | VentilationStandard | VentStd
|  | Zipcode | Zipcode

## CompObjProps
Object | CBECC NR Property | CBECC NR Property Short Form | Alias for Property | DataType | Units | CompEnumerations | CBECC NR Array | XSD ELEMATTRIB minOccurs | XSD ELEMATTRIB maxOccurs | CBECC NR Different Data Type | XSD Base Type | Compliance Use | Definition | Standards Reference
CurveCubic
| Coefficient1 | Coef1 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient2 | Coef2 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient3 | Coef3 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient4 | Coef4 |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumOutput | MaxOut |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumVariable1 | MaxVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumOutput | MinOut |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumVariable1 | MinVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| Name | Name |  | string | none |  | No
CurveDoubleQuadratic
| Coefficient1 | Coef1 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient2 | Coef2 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient3 | Coef3 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient4 | Coef4 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient5 | Coef5 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient6 | Coef6 |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumOutput | MaxOut |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumVariable1 | MaxVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumVariable2 | MaxVar2 |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumOutput | MinOut |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumVariable1 | MinVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumVariable2 | MinVar2 |  | decimal | none |  | No |  |  |  |  | Optional
| Name | Name |  | string | none |  | No
CurveLinear
| Coefficient1 | Coef1 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient2 | Coef2 |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumOutput | MaxOut |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumVariable1 | MaxVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumOutput | MinOut |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumVariable1 | MinVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| Name | Name |  | string | none |  | No
CurveMapDoubleVariable
| ArrayOutput | ArrayOut |  | decimal | none |  | No | 0 | 60 |  |  | Optional
| ArrayVariable1 | ArrayVar1 |  | decimal | none |  | No | 0 | 60 |  |  | Optional
| ArrayVariable2 | ArrayVar2 |  | decimal | none |  | No | 0 | 60 |  |  | Optional
| InterpolationMethod | InterpMthd |  | enumerated list | none | EvaluateCurveToLimits; LagrangeInterpolationLinearExtrapolation; LinearInterpolationOfTable | No |  |  |  |  | Defaulted
| MaximumOutput | MaxOut |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumVariable1 | MaxVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumVariable2 | MaxVar2 |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumOutput | MinOut |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumVariable1 | MinVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumVariable2 | MinVar2 |  | decimal | none |  | No |  |  |  |  | Optional
| NormalizationPoint | NormalizationPt |  | decimal | none |  | No |  |  |  |  | Optional
| Type | Type |  | enumerated list | none | BiQuadratic; QuadraticLinear | No |  |  |  |  | Required
| UnitTypeOutput | UnitTypeOut |  | enumerated list | none | Capacity; DimensionlessOutput; PowerOutput | No |  |  |  |  | Defaulted
| UnitTypeVariable1 | UnitTypeVar1 |  | enumerated list | none | Dimensionless; Distance; MassFlow; Power; Temperature; VolumetricFlow | No |  |  |  |  | Defaulted
| UnitTypeVariable2 | UnitTypeVar2 |  | enumerated list | none | Dimensionless_Var2; Distance_Var2; MassFlow_Var2; Power_Var2; Temperature_Var2; VolumetricFlow_Var2 | No |  |  |  |  | Defaulted
CurveMapSingleVariable
| ArrayOutput | ArrayOut |  | decimal | none |  | No | 0 | 30 |  |  | Optional
| ArrayVariable1 | ArrayVar1 |  | decimal | none |  | No | 0 | 30 |  |  | Optional
| InterpolationMethod | InterpMthd |  | enumerated list | none | EvaluateCurveToLimits; LagrangeInterpolationLinearExtrapolation; LinearInterpolationOfTable | No |  |  |  |  | Defaulted
| MaximumOutput | MaxOut |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumVariable1 | MaxVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumOutput | MinOut |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumVariable1 | MinVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| NormalizationPoint | NormalizationPt |  | decimal | none |  | No |  |  |  |  | Optional
| Type | Type |  | enumerated list | none | Cubic; Exponent; Linear; Quadratic; Quartic | No |  |  |  |  | Required
| UnitTypeOutput | UnitTypeOut |  | enumerated list | none | Capacity; DimensionlessOutput; PowerOutput | No |  |  |  |  | Defaulted
| UnitTypeVariable1 | UnitTypeVar1 |  | enumerated list | none | Dimensionless; Distance; MassFlow; Power; Temperature; VolumetricFlow | No |  |  |  |  | Defaulted
CurveQuadratic
| Coefficient1 | Coef1 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient2 | Coef2 |  | decimal | none |  | No |  |  |  |  | Optional
| Coefficient3 | Coef3 |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumOutput | MaxOut |  | decimal | none |  | No |  |  |  |  | Optional
| MaximumVariable1 | MaxVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumOutput | MinOut |  | decimal | none |  | No |  |  |  |  | Optional
| MinimumVariable1 | MinVar1 |  | decimal | none |  | No |  |  |  |  | Optional
| Name | Name |  | string | none |  | No
Project
| AnalysisType |  |  | enumerated list | none | Title24Compliance; Title24ProposedOnly | [5 empty] | Required |  | NR CBECC XML output
| AutomaticDaylightingReport | AutoDayltgRpt |  | boolean | none | [6 empty] | Defaulted
| AutomaticTimeSwitchReport | AutoTimeSwitchRpt |  | boolean | none | [6 empty] | Defaulted
| City |  |  | string | none | [5 empty] | dtyp:City | Optional | This is a string representing a city in an address.
| CommercialKitchenMandatoryCompliance | CommKitchenMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| CommercialRefrigerationMandatoryCompliance | ComRfrgMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| ComplexHVACMandatoryCompliance | ComplexHVACMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| ComplianceOptionAddition | CompOptAdd |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionAlteration | CompOptAlt |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionDomesticHotWater | CompOptDHW |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionEnvelope | CompOptEnve |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionExisting | CompOptExist |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionLighting | CompOptLtg |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionMechanical | CompOptMech |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionNew | CompOptNew |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionPartialLighting | CompOptPartLtg |  | boolean | none |  | No |  |  |  |  | Required
| ComplianceOptionPartialMechanical | CompOptPartMech |  | boolean | none |  | No |  |  |  |  | Required
| CompliancePathComputerRoom | CompPathComputerRm | CompliancePath |  | none | [6 empty] | Defaulted
| CompliancePathDomesticHotWater | CompPathDHW | CompliancePath |  | none | [6 empty] | Defaulted
| CompliancePathEnvelope | CompPathEnv | CompliancePath |  | none | [6 empty] | Defaulted
| CompliancePathKitchen | CompPathKit | CompliancePath |  | none | [6 empty] | Defaulted
| CompliancePathLaboratory | CompPathLab | CompliancePath |  | none | [6 empty] | Defaulted
| CompliancePathLighting | CompPathLtg | CompliancePath |  | none | [6 empty] | Defaulted
| CompliancePathMechanical | CompPathMech | CompliancePath |  | none | [6 empty] | Defaulted
| ComplianceReportPDF | CompReportPDF |  | boolean | none | [6 empty] | Optional
| ComplianceReportStandard | CompReportStd |  | boolean | none | [6 empty] | Optional
| ComplianceReportXML | CompReportXML |  | boolean | none | [6 empty] | Optional
| ComplianceType | CompType |  | enumerated list | none | AdditionComplete; AdditionEnvelope; AdditionEnvelopeAndLighting; AdditionEnvelopeAndLightingAndPartialMechanical; AdditionEnvelopeAndMechanical; AdditionEnvelopeAndPartialLighting; AdditionEnvelopeAndPartialLightingAndPartialMechanical; AdditionMechanical; AdditionMechanicalAndLighting; AdditionMechanicalAndPartialLighting; ExistingAdditionAndAlteration; ExistingAlteration; NewComplete; NewEnvelope; NewEnvelopeAndLighting; NewEnvelopeAndLightingAndPartialMechanical; NewEnvelopeAndMechanical; NewEnvelopeAndPartialLighting; NewEnvelopeAndPartialLightingAndPartialMechanical; NewMechanical; NewMechanicalAndLighting; NewMechanicalAndPartialLighting | [5 empty] | Compulsory
| CompressedAirMandatoryCompliance | CompressedAirMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| ComputerRoomMandatoryCompliance | ComputerRoomMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| DemandResponsiveReport | DemandResponsiveRpt |  | boolean | none | [6 empty] | Defaulted
| DocumentAuthorAddress | DocAuthAddress | StreetAddress |  | none |  |  | 0
| DocumentAuthorCEAIdentification | DocAuthCEAIdent | ProfessionalCertificationNumber |  | none |  |  | 0
| DocumentAuthorCity | DocAuthCity | City |  | none |  |  | 0
| DocumentAuthorCompany | DocAuthCompany | Company |  | none |  |  | 0
| DocumentAuthorName | DocAuthName | PersonFullName |  | none |  |  | 0
| DocumentAuthorPhone | DocAuthPhone | PhoneNumber |  | none |  |  | 0
| DocumentAuthorState | DocAuthState | State |  | none |  |  | 0
| DocumentAuthorZipcode | DocAuthZipCode |  |  | none |  |  | 0
| DomesticHotWaterDetailsLocation | DHWDetailsLctn |  | string | none | [6 empty] | Optional
| ElectricalMandatoryCompliance | ElecMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| ElevatorLightingVentilationMandatoryCompliance | ElevLtgVentMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| EnvelopeDesignerAddress | EnvDsgnrAddress | StreetAddress |  | none | [6 empty] | Optional
| EnvelopeDesignerCity | EnvDsgnrCity | City |  | none | [6 empty] | Optional
| EnvelopeDesignerCompany | EnvDsgnrCompany | Company |  | none |  |  | 0 |  |  |  | Optional
| EnvelopeDesignerLicense | EnvDsgnrLicense | LicenseNumber |  | none |  |  | 0 |  |  |  | Optional
| EnvelopeDesignerName | EnvDsgnrName | PersonFullName |  | none |  |  | 0 |  |  |  | Optional
| EnvelopeDesignerPhone | EnvDsgnrPhone | PhoneNumber |  | none | [6 empty] | Optional
| EnvelopeDesignerState | EnvDsgnrState | State |  | none | [6 empty] | Optional
| EnvelopeDesignerType | EnvDsgnrType | DesignerType |  | none
| EnvelopeDesignerZipCode | EnvDsgnrZipCode |  |  | none | [6 empty] | Optional
| EnvelopeDetailsLocation | EnvDetailsLctn |  | string | none | [6 empty] | Optional
| EscalatorSpeedControlMandatoryCompliance | EscalSpdCtrlMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| ExceptionalConditionExteriorLighting | ExcptCondExtLtg |  | enumerated list | none | No | [5 empty] | Required |  | 2013 NR ACM
| ExceptionalConditionNarrative | ExcptCondNarrative |  | enumerated list | none | No | [5 empty] | Required |  | 2013 NR ACM
| ExceptionalConditionNoCoolingSystem | ExcptCondNoClgSys |  | enumerated list | none | No | [5 empty] | Required |  | 2013 NR ACM
| ExceptionalConditionRatedCapacity | ExcptCondRtdCap |  | enumerated list | none | No | [5 empty] | Required |  | 2013 NR ACM
| ExceptionalDesignModelFile | ExcptDsgnModelFile |  | string | none | [6 empty] | Optional
| GeometryInputType | GeometryInpType |  | enumerated list | none | Detailed; Simplified | No
| InstitutionalTuningPAFReport | InstitutionalTuningPAFRpt |  | boolean | none | [6 empty] | Defaulted
| LaboratoryExhaustMandatoryCompliance | LabExhaustMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| LightingDesignerAddress | LtgDsgnrAddress | StreetAddress |  | none | [6 empty] | Optional
| LightingDesignerCity | LtgDsgnrCity | City |  | none | [6 empty] | Optional
| LightingDesignerCompany | LtgDsgnrCompany | Company |  | none |  |  | 0 |  |  |  | Optional
| LightingDesignerLicense | LtgDsgnrLicense | LicenseNumber |  | none |  |  | 0 |  |  |  | Optional
| LightingDesignerName | LtgDsgnrName | PersonFullName |  | none |  |  | 0 |  |  |  | Optional
| LightingDesignerPhone | LtgDsgnrPhone | PhoneNumber |  | none | [6 empty] | Optional
| LightingDesignerState | LtgDsgnrState | State |  | none | [6 empty] | Optional
| LightingDesignerType | LtgDsgnrType | DesignerType |  | none
| LightingDesignerZipCode | LtgDsgnrZipCode |  |  | none | [6 empty] | Optional
| LightingDetailsLocation | LtgDetailsLctn |  | string | none | [6 empty] | Optional
| LightingOutdoorCompliance | LtgOutdrComp | LightingCompliance |  | none | [6 empty] | Defaulted
| LightingSignCompliance | LtgSignComp | LightingCompliance |  | none | [6 empty] | Defaulted
| LightingUnconditionedCompliance | LtgUncondComp | LightingCompliance |  | none | [6 empty] | Defaulted
| MechanicalDesignerAddress | MechDsgnrAddress | StreetAddress |  | none | [6 empty] | Optional
| MechanicalDesignerCity | MechDsgnrCity | City |  | none | [6 empty] | Optional
| MechanicalDesignerCompany | MechDsgnrCompany | Company |  | none |  |  | 0 |  |  |  | Optional
| MechanicalDesignerLicense | MechDsgnrLicense | LicenseNumber |  | none |  |  | 0 |  |  |  | Optional
| MechanicalDesignerName | MechDsgnrName | PersonFullName |  | none |  |  | 0 |  |  |  | Optional
| MechanicalDesignerPhone | MechDsgnrPhone | PhoneNumber |  | none | [6 empty] | Optional
| MechanicalDesignerState | MechDsgnrState | State |  | none | [6 empty] | Optional
| MechanicalDesignerType | MechDsgnrType | DesignerType |  | none
| MechanicalDesignerZipCode | MechDsgnrZipCode |  |  | none | [6 empty] | Optional
| MechanicalDetailsLocation | MechDetailsLctn |  | string | none | [6 empty] | Optional
| NarrativeDetails | NarrativeDetails |  | string | none | [6 empty] | Optional
| NRCAEnv02F | NRCAEnv02F |  | boolean | none | [6 empty] | Defaulted
| NRCALti02A | NRCALti02A |  | boolean | none | [6 empty] | Defaulted
| NRCALti03A | NRCALti03A |  | boolean | none | [6 empty] | Defaulted
| NRCALti04A | NRCALti04A |  | boolean | none | [6 empty] | Defaulted
| NRCALti05A | NRCALti05A |  | boolean | none | [6 empty] | Defaulted
| NRCALto02A | NRCALto02A |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc01E | NRCAPrc01E |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc01F | NRCAPrc01F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc02F | NRCAPrc02F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc03F | NRCAPrc03F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc04F | NRCAPrc04F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc05F | NRCAPrc05F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc06F | NRCAPrc06F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc07F | NRCAPrc07F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc08F | NRCAPrc08F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc12F | NRCAPrc12F |  | boolean | none | [6 empty] | Defaulted
| NRCAPrc13F | NRCAPrc13F |  | boolean | none | [6 empty] | Defaulted
| NRCIElc01E | NRCIElc01E |  | boolean | none | [6 empty] | Defaulted
| NRCIEnv01E | NRCIEnv01E |  | boolean | none | [6 empty] | Defaulted
| NRCILti01E | NRCILti01E |  | boolean | none | [6 empty] | Defaulted
| NRCILti02E | NRCILti02E |  | boolean | none | [6 empty] | Defaulted
| NRCILti03E | NRCILti03E |  | boolean | none | [6 empty] | Defaulted
| NRCILti04E | NRCILti04E |  | boolean | none | [6 empty] | Defaulted
| NRCILti05E | NRCILti05E |  | boolean | none | [6 empty] | Defaulted
| NRCILti06E | NRCILti06E |  | boolean | none | [6 empty] | Defaulted
| NRCILto01E | NRCILto01E |  | boolean | none | [6 empty] | Defaulted
| NRCILto02E | NRCILto02E |  | boolean | none | [6 empty] | Defaulted
| NRCILts01E | NRCILts01E |  | boolean | none | [6 empty] | Defaulted
| NRCIMch01E | NRCIMch01E |  | boolean | none | [6 empty] | Defaulted
| NRCIPlb01E | NRCIPlb01E |  | boolean | none | [6 empty] | Defaulted
| NRCIPlb02E | NRCIPlb02E |  | boolean | none | [6 empty] | Defaulted
| NRCIPlb03E | NRCIPlb03E |  | boolean | none | [6 empty] | Defaulted
| NRCIPlb21E | NRCIPlb21E |  | boolean | none | [6 empty] | Defaulted
| NRCIPlb22E | NRCIPlb22E |  | boolean | none | [6 empty] | Defaulted
| NRCISpv01E | NRCISpv01E |  | boolean | none | [6 empty] | Defaulted
| NRCISth01E | NRCISth01E |  | boolean | none | [6 empty] | Defaulted
| NRCVMch04H | NRCVMch04H |  | boolean | none | [6 empty] | Defaulted
| NRCVPlb21H | NRCVPlb21H |  | boolean | none | [6 empty] | Defaulted
| NRCVPlb22H | NRCVPlb22H |  | boolean | none | [6 empty] | Defaulted
| NumberOfDaysPerQuickAnalysisPeriod | NumOfDaysPerQuickAnalysisPeriod |  | integer | none |  | No
| NumberOfQuickAnalysisPeriods | NumOfQuickAnalysisPeriods |  | integer | none |  | No |  |  |  | dtyp:IntegerNonnegative
| NumberTimeStepsPerHour | NumTimeStepsPerHr |  | integer | none |  | No |  |  |  | dtyp:IntegerNonnegative
| OccupancySensorCountReport | OccSensorCntRpt |  | boolean | none | [6 empty] | Defaulted
| OutdoorControlsReport | OutdrCtrlsRpt |  | boolean | none | [6 empty] | Defaulted
| ParkingGarageMandatoryCompliance | ParkingGarageMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| PermitScope |  |  | enumerated list | none | [6 empty] | Required | Defines what compliance the project covers and depends on what plans will be submitted for a permit. | 2013 NR ACM 1.6.2 Scope of Compliance Calculations
| ProcessBoilerMandatoryCompliance | ProcBlrMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| RefrigerationWarehouseMandatoryCompliance | RfrgWarehouseMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| RuleReportFileAppend | RuleReportFileAppend |  | enumerated list | none | _Envelope_csv; _HvacPrimary_csv; _HvacSecondary_csv; _HvacSecondarySizing_csv; _SpaceLoadsElectricity_csv; _SpaceLoadsFuel_csv |  |  |  |  | dtyp:EnumerationConstantPermissive | Optional
| RuleReportType | RuleReportType |  | enumerated list | none | ModelReport_Envelope; ModelReport_HvacPrimary; ModelReport_HvacSecondary; ModelReport_HvacSecondarySizing; ModelReport_Space_InteriorLoadsElec; ModelReport_Space_InteriorLoadsFuel; ModelReport_VentilationExhaust; None | [5 empty] | Optional
| RunPeriodBeginDay | RunPeriodBeginDay |  | integer | none |  | No | [5 empty] | 1 in annual runs, 0 when simulating design days only
| RunPeriodBeginMonth | RunPeriodBeginMonth |  | integer | none |  | No | [5 empty] | 1 in annual runs, 0 when simulating design days only
| RunPeriodEndDay | RunPeriodEndDay |  | integer | none |  | No | [5 empty] | 31 in annual runs, 0 when simulating design days only
| RunPeriodEndMonth | RunPeriodEndMonth |  | integer | none |  | No | [5 empty] | 12 in annual runs, 0 when simulating design days only
| RunPeriodYear | RunPeriodYear |  | integer | none |  | No | [5 empty] | 2009 in annual runs, 0 when simulating design days only
| RunTitle | RunTitle |  | string | none | [5 empty] | xsd:string | Optional | This is a longer descriptive phrase than the project name and describes the compliance run.
| SimpleHVACMandatoryCompliance | SimpleHVACMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| SimulateDesignDays | SimDsgnDays |  | boolean | none |  | No | [5 empty] | Part of determination of whether DDY-defined design days are to be simulated. DDY-based design days should be simulated if EITHER Proj:HVACAutoSizing OR Proj:SimDsgnDays flags are set.
| SimulationVariablesDaylighting | SimVarsDayltg |  | boolean | none |  | No
| SimulationVariablesFenestration | SimVarsFen |  | boolean | none |  | No
| SimulationVariablesHVACPrimary | SimVarsHVACPri |  | boolean | none |  | No
| SimulationVariablesHVACSecondary | SimVarsHVACSec |  | boolean | none |  | No
| SimulationVariablesHVACZone | SimVarsHVACZn |  | boolean | none |  | No
| SimulationVariablesSite | SimVarsSite |  | boolean | none |  | No
| SimulationVariablesThermalZone | SimVarsThrmlZn |  | boolean | none |  | No
| SoftwareVersion | SoftwareVersion |  | string | none | [6 empty] | Required
| SolarReadyMandatoryCompliance | SolReadyMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
| SolarThermalCompliance | SolThrmlComp |  | enumerated list | none | NA | [5 empty] | Defaulted
| StandardsVersion | StandardsVersion |  | enumerated list | none | Compliance2014; Compliance2015; Compliance2016; Compliance2017 | [5 empty] | Defaulted
| State |  |  | string | none | [5 empty] | dtyp:StateAbbreviation | Optional | Two capital letters representing a state in an address associated with the project or a person on the project.
| StreetAddress |  |  | string | none | [5 empty] | dtyp:StreetAddress | Optional | This value is a string to hold street information in an address associated with a project or a person on the project.
| UseExceptionalDesignModel | UseExcptDsgnModel |  | boolean | none | [6 empty] | Optional
| VentilationMulitplier | VentMult |  | decimal | none | [6 empty] | Defaulted
| VentilationStandard | VentStd |  | enumerated list | none | T24_2013; T24_2016; VentilationStandardOther | [5 empty] | Defaulted
| Zipcode |  |  | integer | none |  | No |  |  |  |  | Optional

## CompProperties
CBECC NR Term | CBECC NR Term Short Form | Alias for Property | DataType | Units | CompEnumerations | CBECC NR Array | XSD ELEMATTRIB minOccurs | XSD ELEMATTRIB maxOccurs | CBECC NR Different Data Type | XSD Base Type | Compliance Use | Definition | Standards Reference
_DocumentationOnly |  |  | string | none | [5 empty] | xsd:string
AHU_ModelNumberAHRI |  |  | string | none | [5 empty] | dtyp:String50Char
AirflowMeasuringDeviceManufacturer |  |  | string | none | [5 empty] | dtyp:String50Char |  |  | CF2R-MCH-23
AirflowMeasuringDeviceModelNumber |  |  | string | none | [5 empty] | dtyp:String50Char |  |  | CF2R-MCH-23
AirflowMethod |  |  | enumerated list | none | CoolingSystemMethod
DefaultAirFlowMethod
HeatingSystemMethod
MeasuredAirFlowMethod
AnalysisType |  |  | enumerated list | none | Title24Compliance | [5 empty] | Required |  | NR CBECC XML output
Title24ProposedOnly
BuildingBoardAndSiding |  |  | enumerated list |  |  | No
BuildingClassificationMethod |  |  | enumerated list | none |  | No
BuildingEnergyModelVersion | BuildingEnergyModelVersion |  | integer | none | [6 empty] | Optional
BuildingInputFileName |  |  | string | none | [5 empty] | xsd:string |  | The name of the building file used in the compliance performance analysis
BuildingLightingPowerAllowedConditioned |  |  | decimal | W |  | No
BuildingLightingPowerAllowedUnconditioned |  |  | decimal | W |  | No
BuildingPlanReference |  |  | string | none | [5 empty] | dtyp:String50Char |  |  | CF1R-SRA-01-E, NRCCLTI01E
CalculationsAndRules |  |  | string | none | [7 empty] | This is a documentation tag for instructions on how to calculate a property or the rules for applying it.
CF1RAdd_DisplayTag |  |  | enumerated list | none |  | No |  |  |  | dtyp:EnumerationConstantPermissive
CF1RCC_DisplayTag |  |  | enumerated list | none |  | No |  |  |  | dtyp:EnumerationConstantPermissive
CF2R_DisplayTag |  |  | enumerated list | none |  | No |  |  |  | dtyp:EnumerationConstantPermissive
CF3R_DisplayTag |  |  | enumerated list | none |  | No |  |  |  | dtyp:EnumerationConstantPermissive
City |  |  | string | none | [5 empty] | dtyp:City | Optional | This is a string representing a city in an address.
CommercialRefrigerationEPD | CommRfrgEPD |  | decimal | W per ft2 |  | No
Company |  |  | name | none | [8 empty] | NA
ComplianceApplicationDate |  |  | datetime | none | [5 empty] | xsd:dateTime
ComplianceCertificateType |  |  | enumerated list | none |  | No
ComplianceDocumentTagNR |  |  | enumerated list | none | NRCVPLB21H |  |  |  |  | dtyp:EnumerationConstantPermissive
NRCVPLB22H
ComplianceMethod |  |  | enumerated list | none | Performance |  |  |  |  | dtyp:EnumerationConstant
PrescriptiveAdditions
PrescriptiveAlterations
PrescriptiveNewConstruction
ComplianceOptionAddition | CompOptAdd |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionAlteration | CompOptAlt |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionDomesticHotWater | CompOptDHW |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionEnvelope | CompOptEnve |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionExisting | CompOptExist |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionLighting | CompOptLtg |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionMechanical | CompOptMech |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionNew | CompOptNew |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionPartialLighting | CompOptPartLtg |  | boolean | none |  | No |  |  |  |  | Required
ComplianceOptionPartialMechanical | CompOptPartMech |  | boolean | none |  | No |  |  |  |  | Required
CompliancePath | CompPath |  | enumerated list | none | NA
Performance
Prescriptive
CompliancePathComputerRoom | CompPathComputerRm | CompliancePath |  | none | [6 empty] | Defaulted
CompliancePathDomesticHotWater | CompPathDHW | CompliancePath |  | none | [6 empty] | Defaulted
CompliancePathEnvelope | CompPathEnv | CompliancePath |  | none | [6 empty] | Defaulted
CompliancePathKitchen | CompPathKit | CompliancePath |  | none | [6 empty] | Defaulted
CompliancePathLaboratory | CompPathLab | CompliancePath |  | none | [6 empty] | Defaulted
CompliancePathLighting | CompPathLtg | CompliancePath |  | none | [6 empty] | Defaulted
CompliancePathMechanical | CompPathMech | CompliancePath |  | none | [6 empty] | Defaulted
ComplianceReportPDF | CompReportPDF |  | boolean | none | [6 empty] | Optional
ComplianceReportStandard | CompReportStd |  | boolean | none | [6 empty] | Optional
ComplianceReportXML | CompReportXML |  | boolean | none | [6 empty] | Optional
ComplianceResult |  |  | enumerated list | none | Building Complies with Computer Performance |  |  |  |  | dtyp:EnumerationConstantPhrase
Building Does Not Comply with Computer Performance
ComplianceRunFilename |  |  | string | none | [5 empty] | xsd:token |  | In performance compliance, this is name of the file that was generated as a result of the compliance analysis.
ComplianceSoftwareName |  |  | name | none | [5 empty] | dtyp:ObjectNamePermissive
ComplianceSpecialFeatures |  |  | enumerated list | none | [5 empty] | dtyp:EnumerationConstantPhrase
Coefficient1 | Coef1 |  | decimal | none |  | No |  |  |  |  | Optional
Coefficient2 | Coef2 |  | decimal | none |  | No |  |  |  |  | Optional
Coefficient3 | Coef3 |  | decimal | none |  | No |  |  |  |  | Optional
Coefficient4 | Coef4 |  | decimal | none |  | No |  |  |  |  | Optional
Coefficient5 | Coef5 |  | decimal | none |  | No |  |  |  |  | Optional
Coefficient6 | Coef6 |  | decimal | none |  | No |  |  |  |  | Optional
ArrayOutput | ArrayOut |  | decimal | none |  | No | 0 | 60 |  |  | Optional
ArrayVariable1 | ArrayVar1 |  | decimal | none |  | No | 0 | 60 |  |  | Optional
ArrayVariable2 | ArrayVar2 |  | decimal | none |  | No | 0 | 60 |  |  | Optional
Type | Type |  | enumerated list | none | BiQuadratic | No |  |  |  |  | Required
QuadraticLinear
InterpolationMethod | InterpMthd |  | enumerated list | none | EvaluateCurveToLimits | No |  |  |  |  | Defaulted
LagrangeInterpolationLinearExtrapolation
LinearInterpolationOfTable
NormalizationPoint | NormalizationPt |  | decimal | none |  | No |  |  |  |  | Optional
Type | Type |  | enumerated list | none | Cubic | No |  |  |  |  | Required
Exponent
Linear
Quadratic
Quartic
UnitTypeOutput | UnitTypeOut |  | enumerated list | none | Capacity | No |  |  |  |  | Defaulted
DimensionlessOutput
PowerOutput
UnitTypeVariable1 | UnitTypeVar1 |  | enumerated list | none | Dimensionless | No |  |  |  |  | Defaulted
Distance
MassFlow
Power
Temperature
VolumetricFlow
UnitTypeVariable2 | UnitTypeVar2 |  | enumerated list | none | Dimensionless_Var2 | No |  |  |  |  | Defaulted
Distance_Var2
MassFlow_Var2
Power_Var2
Temperature_Var2
VolumetricFlow_Var2
MaximumOutput | MaxOut |  | decimal | none |  | No |  |  |  |  | Optional
MaximumVariable1 | MaxVar1 |  | decimal | none |  | No |  |  |  |  | Optional
MaximumVariable2 | MaxVar2 |  | decimal | none |  | No |  |  |  |  | Optional
MinimumOutput | MinOut |  | decimal | none |  | No |  |  |  |  | Optional
MinimumVariable1 | MinVar1 |  | decimal | none |  | No |  |  |  |  | Optional
MinimumVariable2 | MinVar2 |  | decimal | none |  | No |  |  |  |  | Optional
ArrayOutput | ArrayOut |  | decimal | none |  | No | 0 | 30 |  |  | Optional
ArrayVariable1 | ArrayVar1 |  | decimal | none |  | No | 0 | 30 |  |  | Optional
DataRegistryProvider |  |  | name | none
DesignerType | DsgnrType |  | enumerated list | none | Architect | [5 empty] | Optional
BuilderOwner
Contractor
Engineer
DigitalSignatureLabel |  |  | string | none | [5 empty] | xsd:string |  |  | The digital signature of the data registry provider is required on all registered compliance documents and is used to secure the data and verfiy the authority for the data
DisplayTagNR |  |  | enumerated list | none
DocumentAuthorName | DocAuthName | PersonFullName |  | none |  |  | 0
DocumentAuthorCompany | DocAuthCompany | Company |  | none |  |  | 0
DocumentAuthorAddress | DocAuthAddress | StreetAddress |  | none |  |  | 0
DocumentAuthorCEAIdentification | DocAuthCEAIdent | ProfessionalCertificationNumber |  | none |  |  | 0
DocumentAuthorCity | DocAuthCity | City |  | none |  |  | 0
DocumentAuthorState | DocAuthState | State |  | none |  |  | 0
DocumentAuthorZipcode | DocAuthZipCode |  |  | none |  |  | 0
DocumentAuthorPhone | DocAuthPhone | PhoneNumber |  | none |  |  | 0
DomesticHotWaterDetailsLocation | DHWDetailsLctn |  | string | none | [6 empty] | Optional
DoorConstructionCertificationMethod |  |  | enumerated list | none |  | No
EnergyUseTypeNonResidential |  |  | enumerated list | none | HeatRejection |  |  |  |  | dtyp:EnumerationConstantPhrase
Lighting
Process
PumpsAndMisc
Receptacle
Ventilation
EnvelopeDesignerAddress | EnvDsgnrAddress | StreetAddress |  | none | [6 empty] | Optional
EnvelopeDesignerCity | EnvDsgnrCity | City |  | none | [6 empty] | Optional
EnvelopeDesignerCompany | EnvDsgnrCompany | Company |  | none |  |  | 0 |  |  |  | Optional
EnvelopeDesignerLicense | EnvDsgnrLicense | LicenseNumber |  | none |  |  | 0 |  |  |  | Optional
EnvelopeDesignerName | EnvDsgnrName | PersonFullName |  | none |  |  | 0 |  |  |  | Optional
EnvelopeDesignerPhone | EnvDsgnrPhone | PhoneNumber |  | none | [6 empty] | Optional
EnvelopeDesignerState | EnvDsgnrState | State |  | none | [6 empty] | Optional
EnvelopeDesignerType | EnvDsgnrType | DesignerType |  | none
EnvelopeDesignerZipCode | EnvDsgnrZipCode |  |  | none | [6 empty] | Optional
EnvelopeDetailsLocation | EnvDetailsLctn |  | string | none | [6 empty] | Optional
ExceptionalConditionExteriorLighting | ExcptCondExtLtg |  | enumerated list | none | No | [5 empty] | Required |  | 2013 NR ACM
ExceptionalConditionNarrative | ExcptCondNarrative |  | enumerated list | none | No | [5 empty] | Required |  | 2013 NR ACM
ExceptionalConditionNoCoolingSystem | ExcptCondNoClgSys |  | enumerated list | none | No | [5 empty] | Required |  | 2013 NR ACM
ExceptionalConditionRatedCapacity | ExcptCondRtdCap |  | enumerated list | none | No | [5 empty] | Required |  | 2013 NR ACM
ExceptionalDesignModelFile | ExcptDsgnModelFile |  | string | none | [6 empty] | Optional
FenestrationConstructionCertificationMethod |  |  | enumerated list | none |  | No
Revision |  |  |  | none
FramingConfiguration |  |  | enumerated list | none |  | No
FullAddress |  |  | string | none | [7 empty] | This is a string that contains the street, city, state and zipcode for a full mailing address
GeometryInputType | GeometryInpType |  | enumerated list | none | Detailed | No
Simplified
Header07_DatePreparedNrPres |  |  |  | none |  | No
HERS_MeasuresCompletionStatus |  |  | enumerated list | none |  | No
HolidaySpecificationMethod |  |  | enumerated list | none |  | No
ICF_Wall |  |  | enumerated list |  |  | No
InsulationBatt |  |  | enumerated list |  |  | No |  |  |  | dtyp:EnumerationConstantPermissive
InsulationBoard |  |  | enumerated list |  |  | No |  |  |  | dtyp:EnumerationConstantPermissive
InsulationLooseFill |  |  | enumerated list | none |  | No
InsulationSprayApplied |  |  | enumerated list | none |  | No
InteriorLightingPowerDensityNonregulated | IntLPDNonReg |  | decimal | W per ft2 |  | No
InteriorLightingPowerDensityRegulated | IntLPDReg |  | decimal | W per ft2 |  | No
InteriorLightingSystemAllowanceType |  |  | enumerated list | none |  | No
InteriorLightingSystemNonRegulatedExclusion |  |  | enumerated list | none |  | No
AcceptanceTestRequired | AcceptanceTestReq |  | boolean | none | [6 empty] | Defaulted
HERSDuctTested | HERSDuctTested |  | boolean | none | [6 empty] | Defaulted
HERSDuctRequired | HERSDuctReq |  | boolean | none | [6 empty] | Defaulted
JobTitle |  |  | string | none | [5 empty] | dtyp:ObjectNamePermissive |  | This value is a string and should be populated with the job title for the responsible person on the project.
LicenseNumber |  |  | string | none | [5 empty] | xsd:token |  | This value is a string and should be populated with the professional license number of the responsible person on a project.
LightingCompliance | LtgComp |  | enumerated list | none | NA | [5 empty] | Defaulted
LightingOutdoorCompliance | LtgOutdrComp | LightingCompliance |  | none | [6 empty] | Defaulted
LightingSignCompliance | LtgSignComp | LightingCompliance |  | none | [6 empty] | Defaulted
LightingUnconditionedCompliance | LtgUncondComp | LightingCompliance |  | none | [6 empty] | Defaulted
LightingDesignerAddress | LtgDsgnrAddress | StreetAddress |  | none | [6 empty] | Optional
LightingDesignerCity | LtgDsgnrCity | City |  | none | [6 empty] | Optional
LightingDesignerCompany | LtgDsgnrCompany | Company |  | none |  |  | 0 |  |  |  | Optional
LightingDesignerLicense | LtgDsgnrLicense | LicenseNumber |  | none |  |  | 0 |  |  |  | Optional
LightingDesignerName | LtgDsgnrName | PersonFullName |  | none |  |  | 0 |  |  |  | Optional
LightingDesignerPhone | LtgDsgnrPhone | PhoneNumber |  | none | [6 empty] | Optional
LightingDesignerState | LtgDsgnrState | State |  | none | [6 empty] | Optional
LightingDesignerType | LtgDsgnrType | DesignerType |  | none
LightingDesignerZipCode | LtgDsgnrZipCode |  |  | none | [6 empty] | Optional
LightingDetailsLocation | LtgDetailsLctn |  | string | none | [6 empty] | Optional
LightingPowerAdjustmentFactorCreditType |  |  | enumerated list | none | DaylightDimmingPlusOff | No | [6 empty] | NRCCLTI01E, CBECC-Com
DemandResponsiveControl
InstitutionalTuning
OccupantSensingControls_126To250SF
OccupantSensingControls_1To125SF
OccupantSensingControls_251To500SF
MandatoryCompliance | MandComp |  | enumerated list | none | NA | [5 empty] | Defaulted
CommercialKitchenMandatoryCompliance | CommKitchenMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
CommercialRefrigerationMandatoryCompliance | ComRfrgMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
ComplexHVACMandatoryCompliance | ComplexHVACMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
CompressedAirMandatoryCompliance | CompressedAirMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
ComputerRoomMandatoryCompliance | ComputerRoomMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
ElectricalMandatoryCompliance | ElecMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
ElevatorLightingVentilationMandatoryCompliance | ElevLtgVentMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
EscalatorSpeedControlMandatoryCompliance | EscalSpdCtrlMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
LaboratoryExhaustMandatoryCompliance | LabExhaustMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
ParkingGarageMandatoryCompliance | ParkingGarageMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
ProcessBoilerMandatoryCompliance | ProcBlrMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
RefrigerationWarehouseMandatoryCompliance | RfrgWarehouseMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
SimpleHVACMandatoryCompliance | SimpleHVACMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
SolarReadyMandatoryCompliance | SolReadyMandComp | MandatoryCompliance |  | none | [6 empty] | Defaulted
MandatoryLightingControlCountReport | MandatoryLtgCtrlCntRpt |  | integer | none |  | Yes | 0 | 5 |  |  | Defaulted
MandatoryLightingControlDescriptionReport | MandatoryLtgCtrlDescRpt |  | string | none |  | Yes | 0 | 5 |  |  | Optional
MandatoryLightingControlIsAcceptanceTestRequiredReport | MandatoryLtgCtrlIsAcceptanceTestReqdRpt |  | enumerated list | none | No |  | 0 | 5 |  |  | Defaulted
MandatoryLightingControlIsAutoShutOffControlReport | MandatoryLtgCtrlIsAutoShutOffCtrlRpt | MandatoryLightingControlIsReportRequired |  | none |  | Yes | 0 | 5 |  |  | Defaulted
MandatoryLightingControlIsDaylightingControlReport | MandatoryLtgCtrlIsDayltgCtrlRpt | MandatoryLightingControlIsReportRequired |  | none |  | Yes | 0 | 5 |  |  | Defaulted
MandatoryLightingControlIsDemandResponseControlReport | MandatoryLtgCtrlIsDemandResponseCtrlRpt | MandatoryLightingControlIsReportRequired |  | none |  | Yes | 0 | 5 |  |  | Defaulted
MandatoryLightingControlIsManualAreaControlReport | MandatoryLtgCtrlIsManAreaCtrlRpt | MandatoryLightingControlIsReportRequired |  | none |  | Yes | 0 | 5 |  |  | Defaulted
MandatoryLightingControlIsMultiLevelControlReport | MandatoryLtgCtrlIsMultiLvlCtrlRpt | MandatoryLightingControlIsReportRequired |  | none |  | Yes | 0 | 5 |  |  | Defaulted
MandatoryLightingControlIsReportRequired |  |  | enumerated list | none | Exempt | Yes | 0 | 5 |  |  | Defaulted | This property is the basic definition for a number of different mandatory lighting control report properties that are defined as aliases of this property
NA
Required
MechanicalDesignerAddress | MechDsgnrAddress | StreetAddress |  | none | [6 empty] | Optional
MechanicalDesignerCity | MechDsgnrCity | City |  | none | [6 empty] | Optional
MechanicalDesignerCompany | MechDsgnrCompany | Company |  | none |  |  | 0 |  |  |  | Optional
MechanicalDesignerLicense | MechDsgnrLicense | LicenseNumber |  | none |  |  | 0 |  |  |  | Optional
MechanicalDesignerName | MechDsgnrName | PersonFullName |  | none |  |  | 0 |  |  |  | Optional
MechanicalDesignerPhone | MechDsgnrPhone | PhoneNumber |  | none | [6 empty] | Optional
MechanicalDesignerState | MechDsgnrState | State |  | none | [6 empty] | Optional
MechanicalDesignerType | MechDsgnrType | DesignerType |  | none
MechanicalDesignerZipCode | MechDsgnrZipCode |  |  | none | [6 empty] | Optional
MechanicalDetailsLocation | MechDetailsLctn |  | string | none | [6 empty] | Optional
Name | Name |  | string | none |  | No
NonresidentialACM_Section |  |  | string | none | [5 empty] | xsd:token |  | The reference in the Nonresidential Alternative Calculation Manual for the applied rule
NotApplicableMessage |  |  | enumerated list | none | N/A |  |  |  |  | dtyp:EnumerationConstantPermissive
Not Applicable
NotKnownMessage |  |  | enumerated list | none | [5 empty] | dtyp:EnumerationConstantPermissive
NumberOfDaysPerQuickAnalysisPeriod | NumOfDaysPerQuickAnalysisPeriod |  | integer | none |  | No
NumberOfQuickAnalysisPeriods | NumOfQuickAnalysisPeriods |  | integer | none |  | No |  |  |  | dtyp:IntegerNonnegative
NumberTimeStepsPerHour | NumTimeStepsPerHr |  | integer | none |  | No |  |  |  | dtyp:IntegerNonnegative
PayloadDocument | PayloadDocument |  | enumerated list | none
PercentImprovement |  |  | decimal | percent | [7 empty] | The percentage of improvement is the compliance margin represented as a percentage of the total energy use of the Standard Design which may be negative indicating a lack of improvement between the standard and proposed design. | CF1R-PRF-01
PermitDay |  |  | integer | none | [6 empty] | Required | The day that the permit application is submitted to the building department. Used to determine applicability of Standards requirements that become effective at future dates.
PermitMonth |  |  | integer | none | [6 empty] | Required | The month that the permit application is submitted to the building department. Used to determine applicability of Standards requirements that become effective at future dates.
PermitNumber |  |  | string | none | [5 empty] | xsd:token |  | The permit number is assigned by the enforcement agency and is required on installation and field verification compliance reports
PermitScope |  |  | enumerated list | none | [6 empty] | Required | Defines what compliance the project covers and depends on what plans will be submitted for a permit. | 2013 NR ACM 1.6.2 Scope of Compliance Calculations
PermitYear |  |  | integer | none | [6 empty] | Required | The year that the permit application is submitted to the building department. Used to determine applicability of Standards requirements that become effective at future dates.
PersonFullName |  |  | name | none | [7 empty] | This value is a string representing the full name of a person associated with the project such as a documentation author or responsible person.
PersonFullNameExtra |  |  | name | none
PhoneNumber |  |  | string | none | [5 empty] | xsd:token |  | This value is a string representing the telephone number of a person on the project such as a documentation author or responsible person.
PhotovoltaicEnergyOffset |  |  | decimal | kTDV per ft2 per yr | [7 empty] | The photovoltaic energy use offset is the amount of energy generated and it is subtracted from the energy use of the proposed design
ProcessedDate |  | ComplianceApplicationDate |  | none | [7 empty] | This value is am xsd:date data type with the format yyyy-mm-dd recording when the compliance document was processed. For example 2013-12-17
ProcessElectricalPowerDensity | ProcElecPwrDens |  | decimal | W per ft2 |  | No |  |  |  | dtyp:DecimalNonnegative
ProfessionalCertificationNumber |  |  | string | none | [5 empty] | xsd:token |  | This value is a string representing the certification for a person on the project such as a documentation author or responsible person.
NarrativeDetails | NarrativeDetails |  | string | none | [6 empty] | Optional
ComplianceType | CompType |  | enumerated list | none | AdditionComplete | [5 empty] | Compulsory
AdditionEnvelope
AdditionEnvelopeAndLighting
AdditionEnvelopeAndLightingAndPartialMechanical
AdditionEnvelopeAndMechanical
AdditionEnvelopeAndPartialLighting
AdditionEnvelopeAndPartialLightingAndPartialMechanical
AdditionMechanical
AdditionMechanicalAndLighting
AdditionMechanicalAndPartialLighting
ExistingAdditionAndAlteration
ExistingAlteration
NewComplete
NewEnvelope
NewEnvelopeAndLighting
NewEnvelopeAndLightingAndPartialMechanical
NewEnvelopeAndMechanical
NewEnvelopeAndPartialLighting
NewEnvelopeAndPartialLightingAndPartialMechanical
NewMechanical
NewMechanicalAndLighting
NewMechanicalAndPartialLighting
PublicationDate |  |  | datetime | none | [5 empty] | xsd:dateTime
QuickAnalysis | QuickAnalysis |  | boolean | none |  | No
QuickAnalysisWeekNumbers | QuickAnalysisWeekNumbers |  | integer | none |  | No | 0 | 12
ReceptaclePowerDensity | RecptPwrDens |  | decimal | W per ft2 |  | No
RegistrationDateTime |  |  | datetime | none | [5 empty] | xsd:dateTime |  | This value is an xsd:dateTime data type recording when a compliance document was registered. The format is yyyy-mm-ddThh:mm:ss.sss The T indicates that beginning of the time part of the value and all parts are required except the second decimals which are optional. For example 2013-12-17T15:03:00 is valid
RegistrationNumber |  |  | string | none | [5 empty] | xsd:token |  | This value is a string that must conform to the formatting convention defined in the JA7.5.4.2 Residential Registration Numbering Convention for registration numbers.
AutomaticDaylightingReport | AutoDayltgRpt |  | boolean | none | [6 empty] | Defaulted
AutomaticTimeSwitchReport | AutoTimeSwitchRpt |  | boolean | none | [6 empty] | Defaulted
DemandResponsiveReport | DemandResponsiveRpt |  | boolean | none | [6 empty] | Defaulted
InstitutionalTuningPAFReport | InstitutionalTuningPAFRpt |  | boolean | none | [6 empty] | Defaulted
OccupancySensorCountReport | OccSensorCntRpt |  | boolean | none | [6 empty] | Defaulted
OutdoorControlsReport | OutdrCtrlsRpt |  | boolean | none | [6 empty] | Defaulted
ReportRequestor |  |  | string | none
ReportRequestorIP_Address |  |  | token | none
NRCAEnv02F | NRCAEnv02F |  | boolean | none | [6 empty] | Defaulted
NRCALti02A | NRCALti02A |  | boolean | none | [6 empty] | Defaulted
NRCALti03A | NRCALti03A |  | boolean | none | [6 empty] | Defaulted
NRCALti04A | NRCALti04A |  | boolean | none | [6 empty] | Defaulted
NRCALti05A | NRCALti05A |  | boolean | none | [6 empty] | Defaulted
NRCALto02A | NRCALto02A |  | boolean | none | [6 empty] | Defaulted
NRCAMch02A | NRCAMch02A |  | boolean | none | [6 empty] | Defaulted
NRCAMch03A | NRCAMch03A |  | boolean | none | [6 empty] | Defaulted
NRCAMch04H | NRCAMch04H |  | boolean | none | [6 empty] | Defaulted
NRCAMch05A | NRCAMch05A |  | boolean | none | [6 empty] | Defaulted
NRCAMch06A | NRCAMch06A |  | boolean | none | [6 empty] | Defaulted
NRCAMch07A | NRCAMch07A |  | boolean | none | [6 empty] | Defaulted
NRCAMch08A | NRCAMch08A |  | boolean | none | [6 empty] | Defaulted
NRCAMch09A | NRCAMch09A |  | boolean | none | [6 empty] | Defaulted
NRCAMch10A | NRCAMch10A |  | boolean | none | [6 empty] | Defaulted
NRCAMch11A | NRCAMch11A |  | boolean | none | [6 empty] | Defaulted
NRCAMch12A | NRCAMch12A |  | boolean | none | [6 empty] | Defaulted
NRCAMch13A | NRCAMch13A |  | boolean | none | [6 empty] | Defaulted
NRCAMch14A | NRCAMch14A |  | boolean | none | [6 empty] | Defaulted
NRCAMch15A | NRCAMch15A |  | boolean | none | [6 empty] | Defaulted
NRCAMch16A | NRCAMch16A |  | boolean | none | [6 empty] | Defaulted
NRCAMch17A | NRCAMch17A |  | boolean | none | [6 empty] | Defaulted
NRCAMch18A | NRCAMch18A |  | boolean | none | [6 empty] | Defaulted
NRCAPrc01E | NRCAPrc01E |  | boolean | none | [6 empty] | Defaulted
NRCAPrc01F | NRCAPrc01F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc02F | NRCAPrc02F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc03F | NRCAPrc03F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc04F | NRCAPrc04F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc05F | NRCAPrc05F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc06F | NRCAPrc06F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc07F | NRCAPrc07F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc08F | NRCAPrc08F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc12F | NRCAPrc12F |  | boolean | none | [6 empty] | Defaulted
NRCAPrc13F | NRCAPrc13F |  | boolean | none | [6 empty] | Defaulted
NRCIElc01E | NRCIElc01E |  | boolean | none | [6 empty] | Defaulted
NRCIEnv01E | NRCIEnv01E |  | boolean | none | [6 empty] | Defaulted
NRCILti01E | NRCILti01E |  | boolean | none | [6 empty] | Defaulted
NRCILti02E | NRCILti02E |  | boolean | none | [6 empty] | Defaulted
NRCILti03E | NRCILti03E |  | boolean | none | [6 empty] | Defaulted
NRCILti04E | NRCILti04E |  | boolean | none | [6 empty] | Defaulted
NRCILti05E | NRCILti05E |  | boolean | none | [6 empty] | Defaulted
NRCILti06E | NRCILti06E |  | boolean | none | [6 empty] | Defaulted
NRCILto01E | NRCILto01E |  | boolean | none | [6 empty] | Defaulted
NRCILto02E | NRCILto02E |  | boolean | none | [6 empty] | Defaulted
NRCILts01E | NRCILts01E |  | boolean | none | [6 empty] | Defaulted
NRCIMch01E | NRCIMch01E |  | boolean | none | [6 empty] | Defaulted
NRCIPlb01E | NRCIPlb01E |  | boolean | none | [6 empty] | Defaulted
NRCIPlb02E | NRCIPlb02E |  | boolean | none | [6 empty] | Defaulted
NRCIPlb03E | NRCIPlb03E |  | boolean | none | [6 empty] | Defaulted
NRCIPlb21E | NRCIPlb21E |  | boolean | none | [6 empty] | Defaulted
NRCIPlb22E | NRCIPlb22E |  | boolean | none | [6 empty] | Defaulted
NRCISpv01E | NRCISpv01E |  | boolean | none | [6 empty] | Defaulted
NRCISth01E | NRCISth01E |  | boolean | none | [6 empty] | Defaulted
NRCVMch04H | NRCVMch04H |  | boolean | none | [6 empty] | Defaulted
NRCVPlb21H | NRCVPlb21H |  | boolean | none | [6 empty] | Defaulted
NRCVPlb22H | NRCVPlb22H |  | boolean | none | [6 empty] | Defaulted
BuriedReport | BuriedReport |  | decimal | none | [6 empty] | Optional |  | CBECC-NR SDD
OutsideReport | OutsideReport |  | decimal | none | [6 empty] | Optional |  | CBECC-NR SDD
PlenumReport | PlenumReport |  | decimal | none | [6 empty] | Optional |  | CBECC-NR SDD
SolarFractionReport | SolFracRpt |  | decimal | none | [6 empty] | Optional |  | CBECC-NR SDD
ResidentialProjectCompletionStatus |  |  | enumerated list | none | Complete_Project | No | [6 empty] | PSR01
NotComplete_Project
ResidentialProjectType |  |  | enumerated list | none |  | No
Role |  |  | enumerated list | none | Builder |  |  |  |  | dtyp:EnumerationConstant
RuleReportFileAppend | RuleReportFileAppend |  | enumerated list | none | _Envelope_csv |  |  |  |  | dtyp:EnumerationConstantPermissive | Optional
_HVACPrimary_csv
_HVACPrimary_csv
_HVACSecondarySizing_csv
_SpcLoadsElec_csv
_SpcLoadsFuel_csv
RuleReportType | RuleReportType |  | enumerated list | none | ModelReport_Envelope | [5 empty] | Optional
ModelReport_HvacPrimary
ModelRpt_HVACSecondary
ModelRpt_HVACSecondarySizing
ModelRpt_Space_InteriorLoadsElec
ModelRpt_Space_InteriorLoadsFuel
ModelRpt_VentilationExhaust
None
RuleSetFilename |  |  | string | none | [5 empty] | xsd:token |  |  | Performance certificates
RuleSetVersion |  |  | string | none | [5 empty] | xsd:token |  |  | Performance certificates
RunDateTime |  |  | datetime | none | [5 empty] | xsd:dateTime |  | In performance compliance, this is the date that the compliance analysis was performed
RunTitle | RunTitle |  | string | none | [5 empty] | xsd:string | Optional | This is a longer descriptive phrase than the project name and describes the compliance run.
RunPeriodBeginDay | RunPeriodBeginDay |  | integer | none |  | No | [5 empty] | 1 in annual runs, 0 when simulating design days only
RunPeriodBeginMonth | RunPeriodBeginMonth |  | integer | none |  | No | [5 empty] | 1 in annual runs, 0 when simulating design days only
RunPeriodEndDay | RunPeriodEndDay |  | integer | none |  | No | [5 empty] | 31 in annual runs, 0 when simulating design days only
RunPeriodEndMonth | RunPeriodEndMonth |  | integer | none |  | No | [5 empty] | 12 in annual runs, 0 when simulating design days only
RunPeriodYear | RunPeriodYear |  | integer | none |  | No | [5 empty] | 2009 in annual runs, 0 when simulating design days only
SectionCorrectionNotes |  |  | string | none
SignatureDate |  |  | datetime | none | [5 empty] | xsd:dateTime |  | This value is an xsd:dateTime data type that records when the person electronically signed the document. The format is yyyy-mm-ddThh:mm:ss.sss The T indicates that beginning of the time part of the value and all parts are required except the second decimals which are optional. For example 2013-12-17T15:03:00 is valid
SimulateDesignDays | SimDsgnDays |  | boolean | none |  | No | [5 empty] | Part of determination of whether DDY-defined design days are to be simulated. DDY-based design days should be simulated if EITHER Proj:HVACAutoSizing OR Proj:SimDsgnDays flags are set.
SimulationVariablesDaylighting | SimVarsDayltg |  | boolean | none |  | No
SimulationVariablesDoor | SimVarsDr |  | boolean | none |  | No |  |  |  |  | Optional
SimulationVariablesFenestration | SimVarsFen |  | boolean | none |  | No
SimulationVariablesHVACPrimary | SimVarsHVACPri |  | boolean | none |  | No
SimulationVariablesHVACSecondary | SimVarsHVACSec |  | boolean | none |  | No
SimulationVariablesHVACZone | SimVarsHVACZn |  | boolean | none |  | No
SimulationVariablesSite | SimVarsSite |  | boolean | none |  | No
SimulationVariablesThermalEnergyStorage | SimVarsThrmlEngyStor |  | boolean | none |  | No |  |  |  |  | Optional
SimulationVariablesThermalZone | SimVarsThrmlZn |  | boolean | none |  | No
SimulationVariablesWaterHeater | SimVarsWtrHtr |  | boolean | none |  | No |  |  |  |  | Optional
SoftwareVersion | SoftwareVersion |  | string | none | [6 empty] | Required
SolarThermalCompliance | SolThrmlComp |  | enumerated list | none | NA | [5 empty] | Defaulted
Brand | Brand |  | string | none | [5 empty] | dtyp:String50Char | Optional |  | CBECC Com NR SDD
Manufacturer | Manufacturer |  | string | none | [5 empty] | dtyp:String50Char | Optional |  | CBECC Com NR SDD
ModelNumber | ModelNum |  | string | none | [5 empty] | dtyp:String50Char | Optional |  | CBECC Com NR SDD
State |  |  | string | none | [5 empty] | dtyp:StateAbbreviation | Optional | Two capital letters representing a state in an address associated with the project or a person on the project.
StreetAddress |  |  | string | none | [5 empty] | dtyp:StreetAddress | Optional | This value is a string to hold street information in an address associated with a project or a person on the project.
SystemDescription |  |  | string | none |  | No
AddCoolingSystem | AddClgSys |  | boolean | none |  | No |  |  |  |  | Optional
HasNoCooling | HasNoClg |  | boolean | none |  | No |  |  |  |  | Optional
HasUnknownHVAC | HasUnknownHVAC |  | boolean | none |  | No |  |  |  |  | Defaulted
StandardsVersion | StandardsVersion |  | enumerated list | none | Compliance2014 | [5 empty] | Defaulted
Compliance2015
Compliance2016
Compliance2017
UseExceptionalDesignModel | UseExcptDsgnModel |  | boolean | none | [6 empty] | Optional
Validates |  |  | boolean | none
VentilationMulitplier | VentMult |  | decimal | none | [6 empty] | Defaulted
VentilationStandard | VentStd |  | enumerated list | none | Other | [5 empty] | Defaulted
T24-2013
T24-2016
VerifiedLowLeakageAirHandlingUnit |  |  | boolean | none | [8 empty] | CF2R-MCH-01 and CF2R/3R-MCH-20's; CBECC CF1R-PERF equivalent property LowLkgAH
Zipcode |  |  | integer | none |  | No |  |  |  |  | Optional

## CompEnumerations
CBECC NR Term | CBECC NR Term Short Form | CBECC NR XML Term | Property
_csv |  | .csv | RuleReportFileAppend
_Envelope_csv |  | - Envelope.csv | RuleReportFileAppend
_HVACPrimary_csv |  | - HVACPrimary.csv | RuleReportFileAppend
_HVACPrimary_csv |  | - HVACSecondary.csv | RuleReportFileAppend
_HVACSecondarySizing_csv |  | - HVACSecondarySizing.csv | RuleReportFileAppend
_SpcLoadsElec_csv |  | - SpcLoadsElec.csv | RuleReportFileAppend
_SpcLoadsFuel_csv |  | - SpcLoadsFuel.csv | RuleReportFileAppend
_VentilationExhaust_csv |  | - VentilationExhaust.csv | RuleReportFileAppend
AdditionComplete |  |  | ComplianceType
AdditionEnvelope |  |  | ComplianceType
AdditionEnvelopeAndLighting |  |  | ComplianceType
AdditionEnvelopeAndLightingAndPartialMechanical |  |  | ComplianceType
AdditionEnvelopeAndMechanical |  |  | ComplianceType
AdditionEnvelopeAndPartialLighting |  |  | ComplianceType
AdditionEnvelopeAndPartialLightingAndPartialMechanical |  |  | ComplianceType
AdditionMechanical |  |  | ComplianceType
AdditionMechanicalAndLighting |  |  | ComplianceType
AdditionMechanicalAndPartialLighting |  |  | ComplianceType
Architect |  |  | DesignerType
BiQuadratic |  |  | Type
Builder |  |  | Role
BuilderOwner |  |  | DesignerType
Building Complies with Computer Performance |  |  | ComplianceResult
Building Does Not Comply with Computer Performance |  |  | ComplianceResult
California |  |  | State
Capacity |  |  | UnitTypeOutput
CERTIFICATE OF ACCEPTANCE NR
CERTIFICATE OF COMPLIANCE
CERTIFICATE OF INSTALLATION
CERTIFICATE OF VERIFICATION
Complete_Project |  |  | ResidentialProjectCompletionStatus
Compliance2014 |  |  | StandardsVersion
Compliance2015 |  |  | StandardsVersion
Compliance2016 |  |  | StandardsVersion
Compliance2017 |  |  | StandardsVersion
Contractor |  |  | DesignerType
CoolingSystemMethod |  |  | AirflowMethod
Cubic |  |  | Type
DaylightDimmingPlusOff |  |  | LightingPowerAdjustmentFactorCreditType
DefaultAirFlowMethod |  |  | AirflowMethod
DemandResponsiveControl |  |  | LightingPowerAdjustmentFactorCreditType
Detailed |  |  | GeometryInputType
Dimensionless |  |  | UnitTypeVariable1
Dimensionless_Var2 |  |  | UnitTypeVariable2
DimensionlessOutput |  |  | UnitTypeOutput
Distance |  |  | UnitTypeVariable1
Distance_Var2 |  |  | UnitTypeVariable2
Engineer |  |  | DesignerType
EvaluateCurveToLimits |  |  | InterpolationMethod
Exempt |  |  | MandatoryLightingControlIsReportRequired
ExistingAdditionAndAlteration |  |  | ComplianceType
ExistingAlteration |  |  | ComplianceType
Exponent |  |  | Type
HeatingSystemMethod |  |  | AirflowMethod
HeatRejection |  |  | EnergyUseTypeNonResidential
InstitutionalTuning |  |  | LightingPowerAdjustmentFactorCreditType
LagrangeInterpolationLinearExtrapolation |  |  | InterpolationMethod
Lighting |  |  | EnergyUseTypeNonResidential
Linear |  |  | Type
LinearInterpolationOfTable |  |  | InterpolationMethod
MassFlow |  |  | UnitTypeVariable1
MassFlow_Var2 |  |  | UnitTypeVariable2
MCH04a Completely New Duct System
MCH04c Low Leakage Air-Handling Unit
MCH04d Altered Duct System
MCH04e Altered Duct System using Smoke Test
MeasuredAirFlowMethod |  |  | AirflowMethod
ModelReport_Envelope |  |  | RuleReportType
ModelReport_HvacPrimary |  |  | RuleReportType
ModelRpt_HVACSecondary |  |  | RuleReportType
ModelRpt_HVACSecondarySizing |  |  | RuleReportType
ModelRpt_Space_InteriorLoadsElec |  |  | RuleReportType
ModelRpt_Space_InteriorLoadsFuel |  |  | RuleReportType
ModelRpt_VentilationExhaust |  |  | RuleReportType
N/A |  |  | NotApplicableMessage
N/A_CF3R
NA |  |  | CompliancePath
NewComplete |  |  | ComplianceType
NewEnvelope |  |  | ComplianceType
NewEnvelopeAndLighting |  |  | ComplianceType
NewEnvelopeAndLightingAndPartialMechanical |  |  | ComplianceType
NewEnvelopeAndMechanical |  |  | ComplianceType
NewEnvelopeAndPartialLighting |  |  | ComplianceType
NewEnvelopeAndPartialLightingAndPartialMechanical |  |  | ComplianceType
NewMechanical |  |  | ComplianceType
NewMechanicalAndLighting |  |  | ComplianceType
NewMechanicalAndPartialLighting |  |  | ComplianceType
No
None |  |  | RuleReportType
NonstandardExteriorWall
NoSpecialFeatures
Not Applicable |  |  | NotApplicableMessage
NotApplicable |  |  | NotApplicableMessage
NotApplicable
NotComplete_Project |  |  | ResidentialProjectCompletionStatus
Not Known
NotTested
NRCA-MCH-02-A
NRCVMCH04aH
NRCVMCH04cH
NRCVMCH04dH
NRCVMCH04eH
NRCV-MCH-04-H
NRCVPLB21H
NRCV-PLB-21-H
NRCVPLB22H
NRCV-PLB-22-H
OccupantSensingControls_126To250SF |  |  | LightingPowerAdjustmentFactorCreditType
OccupantSensingControls_1To125SF |  |  | LightingPowerAdjustmentFactorCreditType
OccupantSensingControls_251To500SF |  |  | LightingPowerAdjustmentFactorCreditType
Performance |  |  | ComplianceMethod
Power |  |  | UnitTypeVariable1
Power_Var2 |  |  | UnitTypeVariable2
PowerOutput |  |  | UnitTypeOutput
Prescriptive |  |  | CompliancePath
PrescriptiveAdditions |  |  | ComplianceMethod
PrescriptiveAlterations |  |  | ComplianceMethod
PrescriptiveNewConstruction |  |  | ComplianceMethod
Process |  |  | EnergyUseTypeNonResidential
PumpsAndMisc |  |  | EnergyUseTypeNonResidential
Quadratic |  |  | Type
QuadraticLinear |  |  | Type
Quartic |  |  | Type
Receptacle |  |  | EnergyUseTypeNonResidential
Required |  |  | MandatoryLightingControlIsReportRequired
Research |  |  | AnalysisType
Simplified |  |  | GeometryInputType
T24-2013 |  |  | VentilationStandard
T24-2016 |  |  | VentilationStandard
Temperature |  |  | UnitTypeVariable1
Temperature_Var2 |  |  | UnitTypeVariable2
Tested
Title24Compliance |  |  | AnalysisType
Title24ProposedOnly |  |  | AnalysisType
Ventilation |  |  | EnergyUseTypeNonResidential
Other |  |  | VentilationStandard
VolumetricFlow |  |  | UnitTypeVariable1
VolumetricFlow_Var2 |  |  | UnitTypeVariable2

## Abbreviations
CBECC NR Term | CBECC NR Term Short Form | Subword Group | Acronym | Subword | Abbreviation
|  | ActiveChilledBeam | ACHB | Absorptance | Abs
|  | AirChangesPerHour | ACH | Addition | Add
|  | AirConditioner | AC | Adjusted | Adj
|  | AirHandlingUnit | AHU | Adjustment | Adj
|  | AnnualFuelUtilizationEfficiency | AFUE | Aggregated | Agg
|  | AreaCategoryMethod | ACM | Allowance | Allow
|  | BrakeHorsePower | BHP | Alteration | Alt
|  | BrushlessPermanentMagnet | BPM | Ambient | Amb
|  | BypassFactor | BF | Amount | Amt
|  | CaliforniaBuildingCode | CBC | Angle | Ang
|  | CaliforniaEnergyCommission | CEC | Architectural | Arch
|  | Carbon DioxideEequivalent | CO2e | Assemblies | Assm
|  | CarbonDioxide | CO2 | Assembly | Assm
|  | CenterOfGlazing | COG | Assignment | Assgn
|  | CentralFanIntegrated | CFI | Astronomical | Astro
|  | ChilledWater | CHW | Attenuation | Attn
|  | ChilledWaterTemperature | CHWT | Attribution | Attrib
|  | CoefficientOfPerformance | COP | Author | Auth
|  | Commercial Buildings Energy Consumption Survey | CBECS | Authority | Auth
|  | CompactFluorescentLuminaire | CFL | Automatic | Auto
|  | ComputerRoomAirConditioner | CRAC | Auxiliary | Aux
|  | ComputerRoomAirHandler | CRAH | Available | Avail
|  | ConcreteMasonryUnit | CMU | Average | Avg
|  | CondenserWater | CW | Azimuth | Az
|  | CondenserWaterSupply | CWS | Ballast | Bal
|  | CondenserWaterTemperature | CWT | Baseline | Base
|  | ConstantVolume | CV | Biosafety | Biosaf
|  | ContractorsStateLicenseBoard | CSLB | Boiler | Blr
|  | CoolRoofRatingCouncil | CRRC | Budget | Bud
|  | DedicatedOutdoorAirSystem | DOAS | Building | Bldg
|  | DeltaTemperature | DelT | Capacity | Cap
|  | DemandControlledVentilation | DCV | Category | Cat
|  | DemandResponse | DR | Cavity | Cav
|  | DesignDay | DD | Centrifugal | Cent
|  | DewPointTemperature | DPT | Charge | Chrg
|  | DirectDigitalControls | DDC | Chiller | Chlr
|  | DirectExpansion | DX | Classification | Class
|  | DisplacementVentilation | DV | Climate | Cli
|  | DomesticHotWater | DHW | Coefficient | Coef
|  | DryBulb | DB | Coefficient1 | Coef1
|  | DualFanDualDuct | DFDD | Coefficient2 | Coef2
|  | EmergingTechnologyProgram | ETP | Coefficient3 | Coef3
|  | EnergyEfficiencyMeasure | EEM | Coefficient4 | Coef4
|  | EnergyEfficiencyRatio | EER | Coefficient5 | Coef5
|  | EnergyFactor | EF | Coefficient6 | Coef6
|  | EnergyInputRatio | EIR | Coincident | Coin
|  | EnergyRecoveryVentilator | ERV | Combined | Cmbd
|  | EnergyUseIntensity | EUI | Combustion | Comb
|  | EqualTo | EQ | Commercial | Comm
|  | EquipmentPowerDensity | EPD | Compliance | Comp
|  | ExpandedPolystyrene | ESP | Compressor | Cprsr
|  | ExtrudedPolystyrene | EXP | Concrete | Conc
|  | FaultDetectionDiagnostics | FDD | Condenser | Cndsr
|  | FourPipeFanCoil | FPFC | Condition | Cond
|  | FuelInputRatio | FIR | Conditioned | Cond
|  | GreaterThan | GT | Conditioning | Condg
|  | GreaterThanOrEqualTo | GTE | Conduction | Cndct
|  | Green House Gases | GHG | Conductivity | Cndct
|  | GroundSourceHeatPump | GSHP | Configuration | Config
|  | HeatExchanger | HX | Construct | Cons
|  | HeatingInputRatio | HIR | Construction | Cons
|  | HeatingSeasonalPerformanceFactor | HSPF | Continuous | Cont
|  | HeatingVentilation | HV | Control | Ctrl
|  | HeatingVentilationAirConditioner | HVAC | Controls | Ctrls
|  | HeatPump | HP | Cool | Cl
|  | HighDefinitionTelevision | HDTV | Cooler | Clr
|  | ICCEvaluationServices | ICCES | Cooling | Clg
|  | Identification Number | ID | Coordinate | Coord
|  | IlluminationEngineeringSocietyNorthernAmercia | IESNA | Count | Cnt
|  | IndoorAirQuality | IAQ | Credit | Cred
|  | IntegratedPartLoadValue | IPLV | Curve | Crv
|  | InternationalCodeCouncilEvaluationService | ICCES | Daylight | Daylt
|  | LeadershipInEnergy&EnvironmentalDesign | LEED | Daylighting | Dayltg
|  | LeavingAirTemperature | LAT | Defrost | Def
|  | LeavingWaterTemperature | LWT | Degree | Deg
|  | LessThan | LT | Delta | Del
|  | LessThanOrEqualTo | LTE | Demand | Dem
|  | LightEmittingDiode | LED | Density | Dens
|  | LightingPowerAllowance | LPA | Dependent | Dep
|  | LightingPowerDensity | LPD | Depth | Dp
|  | MinimumEfficiencyReportingValue | MERV | Description | Desc
|  | MixedAirTemperature | MAT | Design | Dsgn
|  | NewSolarHomesPartnership | NSHP | Designer | Dsgnr
|  | NonresidentialAppendix6 | NA6 | Device | Dev
|  | OccupantControlledSmartThermostat | OCST | Diameter | Dia
|  | OnCenter | OC | Difference | Diff
|  | OutsideAir | OA | Dimmable | Dim
|  | PacificGas&Electric | PG&E | Dimming | Dim
|  | PackageSingleZone | PSZ | Display | Disp
|  | PackageSingleZoneAirConditioner | PSZAC | Distribution | Dist
|  | PackageSingleZoneHeatPump | PSZHP | Documentation | Doc
|  | PackageSingleZoneVariableAirVolumeAirCondiitioning | PSZVAVAC | Door | Dr
|  | PackageSingleZoneVariableAirVolumeHeatPump | PSZVAVHP | Double | Dbl
|  | PackageTerminal | PT | Drive | Drv
|  | PackageTerminalAirConditioner | PTAC | Ducted | Duct
|  | PackageTerminalHeatPump | PTHP | East | E
|  | PackageVariableAirVolume | PVAV | Economizer | Econo
|  | PartLoad | PL | Effect | Eft
|  | PartLoadRatio | PLR | Effectiveness | Eff
|  | PassiveChilledBeam | PCHB | Efficiency | Eff
|  | PersonalComputer | PC | Electric | Elec
|  | PowerAdjustmentFactor | PAF | Electrical | Elec
|  | PowerAdjustmentFactor | PAF | Electricity | Elec
|  | PressureDrop | PD | Elevator | Elev
|  | RelativeHumidity | RH | Emittance | Emit
|  | RelativeSystemEfficiency | RSE | Energy | Engy
|  | ReturnAirTemperature | RAT | Engine | Eng
|  | RevolutionsPerMinute | RPM | Entering | Ent
|  | RoomCavityRatio | RCR | Enthalpy | Enth
|  | SanDiegoGas&Electric | SDG&E | Envelope | Env
|  | SeasonalEnergyEfficiencyRatio | SEER | Equipment | Eqp
|  | ServiceHotWater | SHW | Escalator | Escal
|  | ShadingCoefficent | SC | Evaporative | Evap
|  | SingleZone | SZ | Evaporator | Evap
|  | SingleZoneVariableAirVolume | SZVAV | Exception | Excpt
|  | SkylightRoofRatio | SRR | Exceptional | Excpt
|  | SolarHeatGainCoefficient | SHGC | Exchanger | Exchr
|  | SolarReflectiveIndex | SRI | Exhaust | Exh
|  | SouthernCaliforniaEdison | SCE | Exterior | Ext
|  | StructuralInsulatedPanel | SIP | External | Ext
|  | SupplyAirTemperature | SAT | Fabricated | Fab
|  | TailoredMethod | TM | Factor | Fac
|  | Television | TV | Factory | Fctry
|  | ThirdPartyQualityControlProgram | TPQCP | Fenestration | Fen
|  | TimeDependantValuation | TDV | Fixed | Fxd
|  | UnderFloorAirDistribution | UFAD | Fixture | Fxtr
|  | UniformEnergyFactor | UEF | Floor | Flr
|  | VariableAirVolume | VAV | Floors | Flr
|  | VariableFrequencyDrive | VFD | Fluorescent | Fluor
|  | VariableRefrigerantFlow | VRF | Foot | Ft
|  | VerifiedLowLeakageDuctsConditionedSpace | VLLDCS | Fraction | Frac
|  | VisibleTransmittance | VT | Framing | Frm
|  | WaterSourceHeatPump | WSHP | Friday | Fri
|  | Weekday | WD | Fully | Full
|  | Weekend | WE | Function | Func
|  | WesternCoolingChallenge | WCC | Furnace | Furn
|  | WetBulb | WB | Gain | Gn
|  | WindowWallRatio | WWR | General | Genl
|  |  |  | Generated | Gen
|  |  |  | Generator | Gen
|  |  |  | Glass | Gls
|  |  |  | Glazing | Glz
|  |  |  | Grade | Grd
|  |  |  | Group | Grp
|  |  |  | Head | Hd
|  |  |  | Heat | Ht
|  |  |  | Heater | Htr
|  |  |  | Heating | Htg
|  |  |  | Height | Hgt
|  |  |  | High | Hi
|  |  |  | Holiday | Hol
|  |  |  | Hollow | Hlw
|  |  |  | Horizontal | Horz
|  |  |  | Horsepower | HP
|  |  |  | Hour | Hr
|  |  |  | Hourly | Hrly
|  |  |  | Hours | Hrs
|  |  |  | Humidifier | Hum
|  |  |  | Identification | Ident
|  |  |  | Ignition | Ign
|  |  |  | Illuminance | Illum
|  |  |  | Incandescent | Incan
|  |  |  | Inch | In
|  |  |  | Inches | In
|  |  |  | Index | Idx
|  |  |  | Indoor | Indr
|  |  |  | Infiltration | Inf
|  |  |  | Information | Infrm
|  |  |  | Input | Inp
|  |  |  | Installed | Inst
|  |  |  | Insulated | Ins
|  |  |  | Insulation | Ins
|  |  |  | Interior | Int
|  |  |  | Kitchen | Kit
|  |  |  | Laboratory | Lab
|  |  |  | Latent | Lat
|  |  |  | Latitude | Lat
|  |  |  | Layer | Lyr
|  |  |  | Layers | Lyrs
|  |  |  | Leakage | Lkge
|  |  |  | Leaving | Lvg
|  |  |  | Length | Len
|  |  |  | Level | Lvl
|  |  |  | Light | Ltg
|  |  |  | Lighting | Ltg
|  |  |  | Limit | Lim
|  |  |  | Linear | Lin
|  |  |  | Load | Ld
|  |  |  | Loads | Lds
|  |  |  | Location | Lctn
|  |  |  | Longitude | Long
|  |  |  | Loop | Lp
|  |  |  | Lower | Lwr
|  |  |  | Luminaire | Lum
|  |  |  | Mandatory | Mand
|  |  |  | Manual | Man
|  |  |  | Manufactured | Mftr
|  |  |  | Masonry | Msnry
|  |  |  | Material | Mat
|  |  |  | Materials | Mats
|  |  |  | Maximum | Max
|  |  |  | Mechanical | Mech
|  |  |  | Membrane | Memb
|  |  |  | Metal | Mtl
|  |  |  | Method | Mthd
|  |  |  | Minimum | Min
|  |  |  | Modulation | Mod
|  |  |  | Monday | Mon
|  |  |  | Motor | Mtr
|  |  |  | Mounted | Mntd
|  |  |  | Mounting | Mntg
|  |  |  | Multiple | Mult
|  |  |  | Multiplier | Mult
|  |  |  | Natural | Nat
|  |  |  | Nonregulated | NonReg
|  |  |  | Nonresidential | NonRes
|  |  |  | North | N
|  |  |  | Number | Num
|  |  |  | Object | Obj
|  |  |  | Occupancy | Occ
|  |  |  | Occupant | Occ
|  |  |  | Opaque | Opaq
|  |  |  | Operating | Oper
|  |  |  | Operation | Oper
|  |  |  | Optimum | Opt
|  |  |  | Ornamental | Orn
|  |  |  | Outdoor | Outdr
|  |  |  | Outside | Outsd
|  |  |  | Oversizing | Ovrsiz
|  |  |  | Panes | Pns
|  |  |  | Partial | Part
|  |  |  | Partition | Partn
|  |  |  | Peak | Pk
|  |  |  | Percent | Pct
|  |  |  | Percentage | Pct
|  |  |  | Performance | Perf
|  |  |  | Perimeter | Perim
|  |  |  | Person | Pers
|  |  |  | Placement | Plcmt
|  |  |  | Point | Pt
|  |  |  | Portable | Prtbl
|  |  |  | Position | Pos
|  |  |  | Power | Pwr
|  |  |  | Precision | Prec
|  |  |  | Preheat | Preht
|  |  |  | Prescriptive | Prscrp
|  |  |  | Pressure | Press
|  |  |  | Primary | Pri
|  |  |  | Process | Proc
|  |  |  | Product | Prod
|  |  |  | Program | Prog
|  |  |  | Programmable | Prog
|  |  |  | Project | Proj
|  |  |  | Proofing | Proof
|  |  |  | Proposed | Prop
|  |  |  | Public | Pub
|  |  |  | Quadratic | Quad
|  |  |  | Quantity | Qty
|  |  |  | Radiant | Rad
|  |  |  | Radiation | Rad
|  |  |  | Range | Rng
|  |  |  | Rate | Rt
|  |  |  | Rated | Rtd
|  |  |  | Ratio | Rat
|  |  |  | Receptacle | Recpt
|  |  |  | Recessed | Recesd
|  |  |  | Recirculate | Recirc
|  |  |  | Recirculation | Recirc
|  |  |  | Recovery | Rcvry
|  |  |  | Reference | Ref
|  |  |  | Reflectance | Refl
|  |  |  | Refrigerant | Rfrgt
|  |  |  | Refrigeration | Rfrg
|  |  |  | Regulated | Reg
|  |  |  | Rejection | Rej
|  |  |  | Relative | Rel
|  |  |  | Relocatable | Reloc
|  |  |  | Remote | Rem
|  |  |  | Removal | Rmvl
|  |  |  | Report | Rpt
|  |  |  | Required | Reqd
|  |  |  | Requirement | Req
|  |  |  | Reset | Rst
|  |  |  | Residential | Res
|  |  |  | Resistance | R
|  |  |  | Return | Ret
|  |  |  | Roof | Rf
|  |  |  | Room | Rm
|  |  |  | Rotational | Rot
|  |  |  | RValue | R
|  |  |  | Saturday | Sat
|  |  |  | Schedule | Sch
|  |  |  | Schedules | Sch
|  |  |  | Scheme | Schm
|  |  |  | Secondary | Sec
|  |  |  | Segment | Seg
|  |  |  | Sensible | Sens
|  |  |  | Setpoint | Setpt
|  |  |  | Shading | Shdg
|  |  |  | Sidelit | Side
|  |  |  | Simulation | Sim
|  |  |  | Single | Sgl
|  |  |  | Skylight | Skylt
|  |  |  | Solar | Sol
|  |  |  | Sound | Snd
|  |  |  | Source | Src
|  |  |  | South | S
|  |  |  | Space | Spc
|  |  |  | Special | Spcl
|  |  |  | Specific | Spec
|  |  |  | Specification | Spec
|  |  |  | Speed | Spd
|  |  |  | Square | Sq
|  |  |  | Standard | Std
|  |  |  | Standby | Stdby
|  |  |  | Stepped | Stpd
|  |  |  | Storage | Stor
|  |  |  | Suction | Suct
|  |  |  | Sunday | Sun
|  |  |  | Supplemental | Supp
|  |  |  | Supply | Sup
|  |  |  | Surface | Surf
|  |  |  | System | Sys
|  |  |  | Systems | Sys
|  |  |  | Temperature | Temp
|  |  |  | Terminal | Trml
|  |  |  | Thermal | Thrml
|  |  |  | Thermostat | Tstat
|  |  |  | Thickness | Thkns
|  |  |  | Throttling | Thrtlg
|  |  |  | Through | Thru
|  |  |  | Thursday | Thu
|  |  |  | Tolerance | Tol
|  |  |  | Total | Tot
|  |  |  | Transmittance | Trans
|  |  |  | Tuesday | Tues
|  |  |  | Unconditioned | Uncond
|  |  |  | Underground | Undgr
|  |  |  | Unload | Unld
|  |  |  | Valuable | Val
|  |  |  | Value | Val
|  |  |  | Variable | Var
|  |  |  | Velocity | Vel
|  |  |  | Ventilation | Vent
|  |  |  | Vertical | Vert
|  |  |  | Visible | Vis
|  |  |  | Vivarium | Viv
|  |  |  | Volume | Vol
|  |  |  | Volumetric | Vol
|  |  |  | Water | Wtr
|  |  |  | Waterproof | Wtrprf
|  |  |  | Wednesday | Wed
|  |  |  | Weekdays | WD
|  |  |  | Weekends | WE
|  |  |  | Weight | Wt
|  |  |  | Weighted | Wtd
|  |  |  | West | W
|  |  |  | Whole | Whl
|  |  |  | Width | Wd
|  |  |  | Window | Win
|  |  |  | Zone | Zn

## About
Name: | 2013 Title 24 Standards Data Dictionary
Date generated: | 2017-09-11 20:59
DDTools Version: | 142
Source Data: | https://lmonte.sharepointsite.net/T24ComplianceSW/CEC2011Vocab/default.aspx
Description: | This workbook contains the 2013 Nonresidential Compliance Engine Standards Data Dictionary. (SDD) This is a controlled vocabulary collaborately developed by the Building Energy Standards Modeler (BESM) project (CEC contract 500-08-035) team members, 2013 nonresidential compliance software development (CEC contracts 400-09-002 and 400-10-015) team members , CEC Standards staff and subject matter experts and will be used in the 2013 Nonresidential Compliance Engine rules and building descriptions. The SharePoint lists which are the source of this data are maintained by the BESM project staff as part of the BESM Data Manager and shared through their technology transfer activities.